FireWaTER pump specification

Mechanical, Electrical, Control and DCS

Date: 20th November 2025

TABLE OF CONTENTS

A)  Introduction	3

B)  Project Scope	4

C)  Control Specifications	5

D)  New Control Specifications	8

E) Jockey Pump Specifications	12

F) DCS and SCADA Integration	14

G) Contractor Responsibilities - Electrical	15

H) Contractor Responsibilities – Mechanical	18

I) Health and Safety	19

J) Pricing Schedule	23

K) Fire Pump Drawings Collection	24

# A)  Introduction

LondonEnergy Ltd (The Company) own and operate the EcoPark Energy Centre located in Edmonton, London. The Energy Centre has five boilers burning approximately 500,000 tonnes of domestic refuse per year in a continuous 24-hour operation, 7 days per week. The waste is delivered by road via the weighbridges/gate house by various types of transport. The waste is tipped and held in storage bunkers. Waste is fed by three 5m3 grabbing cranes from the storage bunkers to the feed chutes of each boiler. Each of the water tube boilers is operated to achieve an evaporation rate of 40 tonnes per hour, at a steam pressure of 41.5 Bar and temperature of 415 OC. Material which remains after the incineration process is transferred to the residual conveyors for onward transfer for further treatment and recycling.

Within the EcoPark, there is a firewater ring main system consisting of:

- 2 x Firewater Pumps

- 1 x Sprinkler Header with level control (float switch start)

- 1 x Fire Water Ring Main (with pressure-controlled start capability)

- 40 x Isolation Valves

- 18 x Fire Hose Points

- 18 x Fire Hose Connections

- 20 x Fire Hydrants

- 1 x Crossover Pipeline (for pressure compensation — to be decommissioned and replaced with the jockey pump)

The Eco Park Firewater Pump Project aims to install two new diesel firewater pumps and integrate them with the London Energy DCS system. This will enhance the control, monitoring, and visibility of the fire protection system compared to the currently installed setup. Additionally, a new jockey pump will replace the existing crossover system to maintain pressure in the Firewater Ring Main.

In addition to the installation of two new firewater pumps and a jockey pump, this project requires enhanced visual, audible, and control capabilities. All components and alarms must be integrated with the SCADA system, ensuring seamless monitoring and control.

# B)  Project Scope

- Replace the existing firewater pumps with two new diesel driven firewater pumps. Disconnection of the existing cables from the current firewater pumps and re-termination into the new firewater pump panel. Extending the existing cables via a JB or cable joint. Installation of any additional cables (to be specified and installed by the contractor).

- Select, procure and install a new jockey pump to maintain Ring Main pressure. Installation of any additional cables (power and control) for the jockey pump.

- Upgrade repeater panels to communicate all alarms and faults to the SCADA system.

- Implement DCS-based control and monitoring of the firewater pumps and jockey pump through SCADA.

- All technical documentation and drawings are to be provided to LEL by the selected contractor for upload to the London Energy SharePoint, by LEL.

# C)  Control Specifications

This section outlines the existing control and installation configurations, as well as the required upgrades.

Existing Control and DCS Specifications (Electrical):

- Auto Start: Currently initiated via the "Firewater Pump Test Panel" located on the turbine mezzanine level and from the Sprinkler Header Level Switch.

- Manual Start: Operated through local control panels at each pump and at various push buttons throughout site. Manual stop is only available via the engine choke on the diesel engine.

- Indications Available:

  - Pump running

  - Battery circuit healthy

  - Battery charger healthy

  - Pump on demand

  - Fail to start

  - Low oil pressure

  - High water temperature

  - Lamp test

  - Alarm acknowledgement

All above indications are repeated on remote repeater panels located in the Turbine Hall (East end).

- Audio and visual alarms: Present on both local and remote panels.

- No current control or status indication is available in the CCR via SCADA.

Current Layout:

Fault Indication and Alarms (Current Local Control Panel):

  - High water temperature

  - Low oil pressure

  - Battery charger failure

  - Battery circuit failure

  - Fail to start

  - Pump on demand

  - Alarm acknowledgment

  - Repeater panels provide remote visual and audible alarms.

  - The local test panel enables auto start/stop of firewater pumps

  - No current DCS connectivity or SCADA monitoring of pump operation

Fault Indication and Alarms (New Local Control Panel to be installed):

The new firewater pump control panel (provided by SPP Pumps) will use a volt-free contact for a common fault alarm. Individual alarm indications will be shown locally via the HMI.  Features include an integrated PCB board with volt-free contacts and designated inputs, dual 10A battery chargers and 12V DC batteries for ignition coil and motor starter.

Alarm and Status Indications:

  - Not in Auto Mode

  - Pump Running

  - Pump on Demand (via Float, Pressure or Manual Start request)

  - Failed to Start

  - Mains Supply Failure

  - High Water Temperature

  - Low Oil Pressure

  - Low Engine Cooling Water Flow

  - Low Fuel Level

  - Low Engine Temperature

# D)  New Control Specifications

This section outlines the specifications for the new firewater pump control system to be installed by the selected contractor, including all hardwired electrical requirements, the selected contractor is expected to incorporate the existing manual and automatic start functions.

New Control System Specifications:

- Auto/Remote Start
Auto or remote start will be initiated from the Firewater Pump Test Panel. Interconnections required to enable this function are shown in the associated project drawings.

  - All interconnection work will be carried out by the selected contractor.

- Manual Start
Manual start shall be initiated locally via push buttons installed on the new control panel at each firewater pump. These panels include an integrated HMI display.

- Local Indication and Fault Display
The new control system shall provide local indication of the following conditions via LEDs installed on the new repeater panels.

  - Pump Running

  - High Water Temperature

  - Low Engine Temperature

  - Low Cooling Water Flow

  - Remote Start Active

- Repeater Panel Signal Integration
Pre-existing repeater panel cables will be reused. These will be terminated in the new repeater panels, which will display:

  - Pump Running

  - Fault Alarm

  - Not in Auto Mode

  - Pump on Demand

  - Mains Failure

  - Failed to Start

Interconnection between the new firewater pump control panel and repeater panels will be made using an IP67-rated polycarbonate junction box, installed locally at the new firewater pump.

  - All terminations will be completed by the selected contractor.

- Repeater Panel Construction
Repeater panels will be built on-site by a LEL-specified technician.

  - All components must comply with the appropriate SIL (Safety Integrity Level) as defined by selected contractor.

- SWA Cable – Mezzanine Floor
A single 3-core cable, conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), shall be routed between the junction box and the relay/start push-button station on the Mezzanine Floor for each firewater pump shall be installed by the contractor.

- SWA Cable – Firewater Pump Control Panel
A single 19-core SWA cable conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), shall be routed between the junction box and the control panel on each firewater pump.

- Sirens
Existing orange mineral-insulated cables for the sirens on Panel 1 and Panel 2 must be reinstalled on top of the new control panels.

- A LPCB flow meter is to be provided and installed in accordance with LPC rules (technical bulletins) incorporating BSEN12845, with an integral “self-test” return loop for both pumps.

Existing Repeater Panel – Indications and Installation (Turbine Hall):

Current repeater panels provide the following indications:

- High Water Temperature

- Low Oil Pressure

- Battery Charger Failure

- Battery Circuit Failure

- Fail to Start

- Pump on Demand

- Alarm Acknowledgement

- Visual and audio alarms for remote fault indication

- Local Test Panel for auto start/stop control

No DCS or SCADA connectivity for pump status or alarms

New Repeater Panel – Indications and Installation (Turbine Hall):

- Common Fault Alarm – Visual and audible indication

- Not in Auto Mode

- Failed to Start

- Pump on Demand

- Pump Running

- Mains Failure

Full DCS/SCADA Integration – All alarms and remote start/stop functions to be extended to SCADA, existing cabling will be reused for connectivity between new firewater pump control panels and repeater panels, Sirens to be reinstalled on top of new control panels

Cable Schedule:

| Fire pump Allocation | Cab ID old | Cab ID (new) | Description (control/signal/power) | Cable Spec | Gland spec | Location (to and from) |
| --- | --- | --- | --- | --- | --- | --- |
| Fire pump one | FP1-1 | FP1-1 | Alarms and indication | Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), | Hawk M32 | Repeater panel to new junction box |
| Fire pump two | FP2-1 | FP2-1 | Alarms and indication | Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), | Hawk M32 | Repeater panel to new junction box |
| Fire pump one | FP1-3 | FP1-3 | 240Vac power supply | Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), | Hawk M20(S) | From P405 DB to New Control panel via JB |
| Fire Pump two | FP2-3 | FP2-3 | 240Vac power supply | Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), | Hawk M20(S) | Switchroom A distribution board to New control panel via JB |
| Fire pump one |  | FP1-4 | Interconnections from JB to new control panel. | Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), | Hawk M20(L) | From new JB to new fire control panel. |
| Fire pump two |  | FP2-4 | Interconnections from JB to new control panel. | Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), | Hawk M20(L) | From new JB to new fire pump control panel. |
| Fire pump one |  | FP1-5 | Battery connection to fire pump ignition coils/starter motor | Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), | To be specified by contractor | To be specified by contractor |
| Fire pump two |  | FP2-5 | Battery connection to fire pump ignition coils/starter motor | Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), | To be specified by contractor | To be specified by contractor |
| Jockey pump |  | JP1-1 | 415Vac motor supply | Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), | To be specified by contractor | To be specified by contractor |

# E) Jockey Pump Specifications

This section outlines the installation requirements for the jockey pump, including electrical, control, and mechanical specifications

- Decommissioning:

  - Two “Dust Extraction Pump Discharge” pumps are to be disconnected, removed, and associated cables made safe.

- Installation:

  - A Jockey Pump will be installed in place of the “TY192 Dust Extraction Pump Discharge” pump.

  - Jockey pump to replace cross over pipeline for pressure compensation. Installation to be carried out by the selected contractor.

- Electrical Supply:

  - A new 415V 3-phase supply is required.

  - One of:

    - 4-core  Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), , or

    - 3-core  with bare copper earth, Conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236),
from an appropriate designated distribution board. Location to be determined by contractor.

  - A lockable isolator must be installed near the jockey pump on a suitable stand. The appropriate loading and size of the jockey pump motor to be designed, selected, procured, installed and commissioned by the contractor.

- Pump Specification:

  - The motor nameplate details must be provided to the E&I technician.

  - Final pump sizing is to be determined by the selected contractor.

- Starter Panel:

  - Must be redesigned to include:

    - Control voltage protection and Primary voltage protection (a number of appropriately rated fuses for the control voltage and a suitable sized MCCB with thermal or CT overload).

    - Motor protection.

  - Design and component selection to be carried out by the LEL E&I technician in collaboration with the contractor.

  - Design documentation and SIL certification to be provided.

- Test Fire Pump Panel:

  - To be modified by the contractor to incorporate jockey pump activation based on header low pressure.

  - Jockey pump to have its own pressure switch independent of the Test Fire Pump Panel, which will need to include a cable from the Jockey Pump Starter Panel to the position of the new Pressure Switch to be selected, designed and installed by the contractor.

- Pump initiation board:

- A pump initiation board is to supply in accordance with BS EN 12845. Pump initiation boards are designed to allow the initial setting and testing of sprinkler system pump initiation pressure switches in compliance with BS EN 12845. Each main pump has two pressure switches and jockey pumps have a single switch. The pressure switches can be isolated so that its function and cut-in pressure can be verified during system servicing. The special arrangement of ball and check valves means that even if all switches are isolated, a drop in system pressure will still initiate pump operation. As an additional safety measure, lockable ball valves are used to reduce the risk of them being accidentally closed.

- Integration:

  - The jockey pump must be fully integrated into the DCS system by the selected contractor.

  - Signals required from the jockey pump to DCS include “Tripped” signal in line with other alarm terminology.

# F) DCS and SCADA Integration

DCS and SCADA Specifications

The selected contractor is responsible for designing and implementing integration of the fire pump system with the DCS/SCADA system.

- All alarms (visual and audible) must be replicated in the SCADA interface.

- Fire pump status (running, faults, etc.) must be visible in the CCR SCADA graphic interface, which is to be developed by valmet.

- Remote start/stop and fault status for:

- Jockey pump and Fire pumps must be available on SCADA (No requirement for a remote “Start/Stop” signal from DCS for the jockey pumps).

- All SIL-rated instruments must be specified and documented by the contractor.

- Fire pump header pressure is to be displayed in SCADA, integrated via the graphic interface.

- All communication cabling must be specified by the contractor.

- Any I/O racks required must be specified and integrated by the contractor.

- PLC panels and I/O racking:

- Specified and installed by the contractor.

- All terminations to be completed by the contractor.

- PLC Logic and Design:

- Must be reviewed and approved prior to commissioning

- Two new 12-core cables conforming to LPC Technical Bulletins 210 and 236 (TB210 and TB236), are to be routed via existing cable tray from Alarm Panels 1 and 2 to the “Central Gauge Board De-Min Control Panel” in the Turbine Hall.

- Existing spare DCS Valmet I/O slot 8,16 Digital Input Card:

- Wire numbers 720017 to 720032,are to be utilised for SCADA connections.

# G) Contractor Responsibilities - Electrical

1. Decommissioning Work

To be performed by the selected contractor:

- Verifying circuits are de-energised ("prove dead")

- Removal of redundant cabling from existing firewater pumps and panels

- Removal of obsolete or unsuitable cable trays, containment systems, and ancillary fixings as required

2. Installation and Terminations

The selected contractor will be responsible for the installation and termination of cabling and equipment, including:

- Installation of new repeater panels as per specifications

- Installation of junction boxes at the firewater pump locations to accommodate signal interconnections

- Installation of cable tray systems near firewater pump sets for proper containment and support of cables

  - All tray work to be galvanised and painted with galvanised spray at cut ends and properly earth bonded.

  - Metal Cable Ties to be applied in all instances

- Termination of cables between:

  - New repeater panels

  - Battery panels

  - New junction boxes

- All local control panel terminations

- Installation of cable between the jockey pump and the new junction boxes at the fire pumps to accommodate a “Tripped” signal back to the DCS.

- End-to-end testing of all new and existing circuits and cables to ensure compliance and functionality.

- Earthing Design to be submitted as part of the tender submission.

Cable Containment:

This section outlines the cable containment requirements for the project.

- For the two cables running from the alarm panels in the Turbine Hall to the junction boxes at the fire pumps, the selected contractor is to:

  - Calculate the appropriate cable tray sizing.

  - Assess and communicate any requirement for scaffolding for installation.

- For the 240V supply cables from the designated Power Distribution Boards to each fire pump:

  - The cable trays must be installed suspended due to the inaccessibility and hazards associated with the existing ducting (e.g. lifting metal covers and accumulated sediment).

  - All installation work to be carried out by the selected contractor.

- For the cables between the junction boxes and the relay/start push-button stations on the Mezzanine Floor:

  - Suspended cable trays are also required and must be calculated and installed by the contractor.

- Additional ancillary tray work must be measured and installed for:

  - Other control and power cables (e.g., 35mm² tri-rated cables) routed between the control panel frames and fire pumps.

  - This work is to be carried out by the selected contractor(s).

Diesel Day Fuel Tank Control

This section specifies the fuel tank overfill protection system for the diesel day tanks.

- To prevent overfilling, the system shall include:

  - A High-High Level Float Switch installed on the existing new tank, and

  - A Solenoid Isolation Valve on the gravity-fed fuel inlet lines.

- The control philosophy follows a fail-safe design:

  - Upon detection of a high-high fuel level, the float switch signals the solenoid valve to close, preventing overflow.

  - Once the fuel level drops to a predefined safe level, the float resets, re-energising the solenoid valve to reopen, resuming normal operation allowing the operations to manually fill the Day Tanks.

- This automatic level regulation:

  - Prevents spillage,

  - Ensures environmental compliance,

  - Aligns with critical fuel system safety standards.

- The high-high level condition shall be annunciated on the control panel.

  - Additional cables and electrically controlled equipment (solenoids and valves) shall be selected and precured by the contractor.

  - Integration into DCS to be completed by valmet.

Battery Control Panels

This section outlines requirements for the Battery Control Panels associated with each fire pump.

- Two Battery Isolation Control Panels are to be mounted to the frames of the fire pump control panels. Additionally, two junction boxes are to be mounted on each fire pump control panel.

- From each battery pack, two 35mm² tri-rated cables are to be routed:

  - To the battery isolation panels,

  - Then to the fire pump terminals for solenoids (for “Auto” and “Manual” start functions),

  - Including earth connections.

- Two new 240V supplies cables are to be installed:

  - From the designated power distribution boards to each fire pump control panel.

- One cable is to be routed:

  - Between the junction boxes and the battery isolation panels on each fire pump.

# H) Contractor Responsibilities – Mechanical

1. Decommissioning Work

To be performed by the selected contractor:

- Verifying stored energy for any pipework removal has been completed by LEL

- Removal of redundant pipework and fittings from existing firewater pumps & making good

- Removal of existing pumps and diesel drivers and any ancillary fittings as required

2. Installations

The selected contractor will be responsible for the installation of the following equipment, including:

- Installation of two new pumps: : SPP TD15A Horizontal Split Case Pump coupled with Matched Diesel Engines and Combined Diesel Tanks.

- Installation of one new Jockey pump and Electric Motor: Discharge Jockey Pump pressure to maintain fire ring main at max 7 bar. Suction pressure will be Plant Auxiliary Cooling Water Pump Suction pressure. Pipework Tie-In’s will be site run to existing Firewater Pump suction and discharge pipework local to the pump.

- Installation of new jockey pump valves (Zurich will come in to check required valve spec):

  - x1 Inlet valve

  - x1 Outlet valve

  - x1 Drain valve

  - x1 Vent valve

  - x1 NRV

- Existing isolation valves to be used for original fire pump sets.

Timeline for Installations, commissioning and handover (including drawings and training) to be completed by selected contractor.

Firewater Pumps:

This section outlines the mechanical required works for the firewater pumps.

- Diesel - Supply, isolation standard (Additional valves required), protection, control and instrumentation. Use SPP W00-003E installation specification.

  - Use SPP W00-003E installation specification.

- Engine Exhaust - Contractor to determine whether existing exhaust system is suitable for SPP Diesel Engine specification.

- Suction/Discharge Pipework - Field run into existing firewater pump pipework and compliant with [ASME B31.3.]. ASTM A106/B Sch 40 with fittings and Flanges compliant with existing pipework.

- Pipe fittings and supports – Compliant with BS EN 12845

- Painting – Any new pipework to be prepared with x2coats of primer and x2coats of red gloss.

- Civils and structural – Contractor to determine new footprints, ensuring compatibility of existing plinths for gross weights, to accommodate seating of new pumps.

Jockey Pumps:

This section outlines the mechanical required works for the jockey pumps

- Suction/Discharge Pipework - Field run into existing jockey pump pipework and compliant with [ASME B31.3.]. ASTM A106/B Sch 40 with fittings and Flanges compliant with existing pipework.

- Civils and structural – Contractor to determine new footprints, ensuring compatibility of existing plinths for gross weights, to accommodate seating of new pumps.

- Pipe fittings and supports – Compliant with BS EN 12845

- Painting – Any new pipework to be prepared with x2coats of primer and x2coats of red gloss

# I) Health and Safety

Specific Health Hazards:

This section identifies significant residual hazards that remain after all design mitigations and must be considered during execution.

Contractors are required to carry out formal risk assessments before undertaking any work.

This list is not exhaustive and does not absolve either the Company or the Contractors of their responsibilities under the following (and other applicable) legislation:

- Health & Safety at Work etc Act 1974

- Management of Health & Safety at Work Regulations

- The Electricity at Work Regulations 1989

- Dangerous Substances and Explosive Atmospheres Regulations 2002.

- Construction (Design and Management) Regulations

- Any other statutory or industry-specific regulations.

- All portable equipment shall have a valid electrical test & inspections certificate and HAVS assessment where applicable.

- Any work carried out in a potentially hazardous environment shall be carried out by CompEx trained personnel.

| Area | Hazard |
| --- | --- |
| Energy Centre | Chemicals e.g. Sulphuric acid, Hydrochloric acid, Sodium hydroxide, Sodium hypochlorite, etc. Dust e.g. Lime, PAC, Fly ash etc. Flue gases e.g. Hydrogen Chloride, Sulphur Dioxide etc. |
| Throughout site | Site traffic/Segregation of traffic and persons. |
| Throughout site | Working at Height. |
| Waste | Disposal of demolition waste and debris. |
| Throughout site | Working in confined space. |
| Throughout site | Hot Works. |
| Throughout site | Electricity. |
| Throughout site | Pressure systems |
| Throughout site | Machinery |
| Throughout site | Asbestos |
| Throughout site | Noise |
| Throughout site | Leptospirosis (Weils disease). |

Control of Substances Hazardous to Health (COSHH):

The Contractor must provide all documentation required under the Control of Substances Hazardous to Health Regulations (COSHH) prior to bringing any chemical substances onto site.

This includes:

- A current Material Safety Data Sheet (MSDS) for each substance

- A complete COSHH assessment for each substance to be used

No contractor is permitted to bring any chemical product onto site without prior approval from the Company.

Environmental Protection:

The Contractor must comply with all relevant environmental legislation and adhere strictly to site-specific environmental rules throughout the duration of the works.

Contractor obligations include:

- Segregating all waste generated during the course of the works

- Disposing of all waste in the correct skips and containers, as supplied by the Company

Waste management practices must align with site environmental policies and current UK environmental regulations.

HSQE

Firewater Pump performance standards are found within SCR05 (Safety Case Regulation 2005), Chapter 5. This is an “offshore” regulation, so we need clarification from our insurers (Zurich).

This project will fall under CDM regulations as far as worker safety and SSOW are concerned, whether it falls under an F10 will depend on if:

•	The project is expected to last longer than 30 working days

•	The project is expected to exceed 500 workdays between individual workers

•	If more than 20 workers will be working on the project at any point

Any CDM compliance or notification will be the responsibility of the Contractor, Daily CDM meetings will be held on site by, chaired by LEL on behalf of the contractor.

The above will need confirming via a detailed programme of works.

British Standards:

- BS 7671 - 18th Edition-Requirements for electrical installations. IET Wiring Regulation, 18th Edition

- BS 5424 Parts 2 and 3, also IEC 60158 part 3-Specification for low voltage control gear

- BS 7430 1998 - Code of practice for earthing

- BS EN 60529 1992- Specification for degrees of protection provided by enclosures (IP code)

- BS EN 60947 Parts 1-8 2001-2011- Specification for low voltage switch gear and control gear

- BS EN 61439- 2009 -2012- Low-voltage switchgear and control gear assemblies

- BS EN (IEC) 60309, Parts 1, 2, 4 1999-2007- Plugs, socket-outlets and couplers for industrial purposes.

- BS EN 60079, 2004- Electrical apparatus for potentially explosive atmospheres.

- PD CLC/TR 50404: 2003 - Code of practice for avoidance of hazards due to static electricity.

- Energy Institute Model Code Of Safe Practice, Part 15 (IP15)- 2005  Area classification code for installations handling flammable fluids.

# J) Pricing Schedule

The Contractor shall submit a fixed price for each of the elements of defined work detailed in the schedule below.

| Item | Schedule Task to be performed | Price £ |
| --- | --- | --- |
| 1 | Remove existing Fire Pumps and Engines |  |
| 2 | Wreck out existing Pump/Engine Bedplate footplate slab |  |
| 3 | Recast new Bedplate footplate slab to achieve correct pump centrelines |  |
| 4 | Install New Fire Pump/Diesel Engine and ancillary skid |  |
| 5 | Remove and wreck out dust suppression pumps |  |
| 6 | Wreck out existing footplate slab |  |
| 7 | Recast footplate slab |  |
| 8 | Install Jockey Pump and ancillaries and pipework tie ins |  |
| 9 | Commission and performance test equipment and system to proposed standard |  |

PRICING SCHEDULE (excluding VAT)

CONTRACT REFERENCE: ****

Participating organisations shall not take advantage of any error or omission contained within this Information Pack or within subsequent tender documents and shall review all documentation and promptly report any error, inconsistency or omission to LEL.  These shall be considered by LEL and if appropriate, shall be addressed through written clarifications addressed to all participating organisations during the submission period.  Clarifications shall include additions, alterations, or deletions to the documentation, and any other instructions, as appropriate.

# K) Fire Pump Drawings Collection