| Document Title: | Horniman Museum and Gardens Estates Maintenance Scope of Works |
| --- | --- |
| Version: | 00 |
| Date: | 07.03.2025 |

1.	VERSION CONTROL	6

2.	DESCRIPTION OF THE SERVICE	7

3.	Overall objectives	8

3.1.	Description of the Service	8

3.2.	Affected Property	9

3.3.	Type of Contract	9

4.	GENERAL CONSTRAINTS ON HOW THE CONTRACTOR PROVIDES THE SERVICE	9

4.1.	Use of the Affected Property	10

4.2.	Access to the Affected Property	10

4.3.	Deliveries	10

4.4.	Noise and vibrations	10

4.5.	Working Hours	11

4.6.	Parking	11

4.7.	Use of Equipment	12

4.8.	Restrictions on the use of hazardous materials	13

4.9.	Storage of fuel and chemicals	13

4.10.	Pollutions, ecological or environmental impacts	13

4.11.	Client specific policies and procedures	14

4.12.	Constraints imposed to meet the requirements of Others	14

4.13.	Travelling and Travel	14

4.14.	Confidentiality	14

4.15.	Security and protection of the Affected Property	14

4.16.	Protection of the Affected Property	15

4.17.	Protection of the work on the Affected Property	16

4.18.	Consideration of Others	16

4.19.	Cleanliness	16

4.20.	Waste Material	17

4.21.	Advertising	17

5.	CONTRACTOR’S PLAN	17

6.	TASK ORDER	17

7.	QUALITY MANAGEMENT	18

8.	TESTS AND INSPECTIONS	18

8.1.	Testing	18

8.2.	Certification, licenses and approvals	19

9.	MANAGEMENT OF THE SERVICE	19

9.1.	Project Team	19

9.2.	Communication System	20

9.3.	Helpdesk	21

9.4.	Management Procedures	21

9.5.	Contractor’s Application for payment	23

10.	WORKING WITH THE CLIENT AND OTHERS	23

11.	SERVICES AND OTHER THINGS TO BE PROVIDED BY THE CLIENT	23

11.1.	Contractor Space	23

11.2.	IT	24

11.3.	Telephones	24

11.4.	Radios	24

11.5.	Catering Facilities	24

11.6.	Utilities	24

12.	HEALTH & SAFETY	24

12.1.	General	24

12.2.	Affected Property Users	25

12.3.	Unsafe Conditions	25

12.4.	Fire or Water Hazards	25

12.5.	Asbestos	25

12.6.	Equality Act	26

12.7.	Legal Compliance	26

12.8.	Records	27

12.9.	PPE	27

12.10.	Safe Systems of Work	27

12.11.	Permit to Work System	27

12.12.	Signage	28

12.13.	Competent Persons	28

12.14.	Authorised Persons	28

12.15.	INCIDENT REPORTING	29

12.16.	Construction (Design & Management) Regulations	29

12.17.	HEALTH & SAFETY SUPPORT	29

12.18.	Risk Assessments, Method Statements and Safe Systems of Work	29

12.19.	Sub-Contractors	30

13.	SUBCONTRACTING	30

13.1.	General	30

13.2.	Existing Subcontractors	30

13.3.	Vetting	30

13.4.	Change Management	31

14.	CLIENT’S SERVICE SPECIFICATIONS	31

14.1.	SERVICE SPECIFICATION INTRODUCTION	31

14.2.	MOBILISATION	31

14.3.	ASSET REVIEW	32

14.4.	PERSONNEL AND SERVICES TO BE PROVIDED	32

14.5.	SKILLS & TRAINING	33

14.6.	SITE COVER	34

14.7.	INFORMATION MANAGEMENT SYSTEM	34

14.8.	PLANTROOMS	35

14.9.	PLANNED PREVENTATIVE MAINTENANCE	35

14.10.	WARRANTEES	37

14.11.	BREAKDOWN	37

14.12.	REACTIVE WORK ORDER	37

14.13.	SMALL WORKS INSTALLATIONS (e.g. under £10,000)	37

14.14.	MINOR WORKS	37

14.15.	EMERGENCY LIGHTING TESTING	38

14.16.	LAMP REPLACEMENT WORKS	38

14.17.	CONTROLS	39

14.18.	HOLIDAY AND SICKNESS COVER	39

14.19.	MAINTAINING ENVIRONMENTAL CONDITIONS	39

14.20.	LIMITED COMPRENHENSIVE ELEMENT	40

14.21.	EXCLUSIONS	41

14.22.	EQUIPMENT AND TOOLS	41

14.23.	SPARES AND CONSUMABLES	42

14.24.	WATER TREATMENT	43

14.25.	WATER TEMPERATURES	44

14.26.	SHOWER HEADS AND SPRAY TAPS	45

14.27.	ANNUAL CHECK	45

14.28.	WATER SAMPLING	45

14.29.	FILTERS	45

14.30.	GAS FIRED BOILERS	45

14.31.	HUMIDIFIERS	46

14.32.	PERIODIC FIXED WIRE TESTING	46

14.33.	PORTABLE APPLIANCE TESTING	47

14.34.	OUT OF HOURS WORKING	47

14.35.	HELPDESK	47

14.36.	KEY PERFORMANCE INDICATORS	48

14.37.	METHOD STATEMENTS	50

14.38.	APPRENTICES	50

14.39.	WORKS REQUESTS	50

14.40.	WORKS PRIORITISATION	50

14.41.	DUCTWORK	51

# VERSION CONTROL

| Revision History | Date | Author | Notes |
| --- | --- | --- | --- |
| Draft 00 | 27.02.25 | Julieanne Mollen | Draft |
| Draft 01 | 14.03.25 | Julieanne Mollen | Amendments from workshop |

| Colour | Meaning | Action |
| --- | --- | --- |
| Green | Once text has been reviewed and agreed it will be changed to green. | No further action. |
| Red | Text that is to be removed from final version of specification. | Remove text |
| Orange | Areas for focus for update or removal. | Focus for review and update |
| Purple | Purple is new proposed sections/text to be reviewed and moved to green. | New text |
| Black | Original Text | Original Text |

# DESCRIPTION OF THE SERVICE

| Term | Definition |
| --- | --- |
| Affected Property | The Client estate |
| Asset | A physical item such as a building, plant or machinery which is acquired by a user and then employed by him in the pursuance of his business, trade or profession |
| Building Fabric | Elements and components of a building other than furniture and services. |
| Competent Person | A person who has sufficient training and experience or knowledge and other qualities to enable him/her properly to assist in devising and applying preventive and protective measures to control the risks presented by the business. Or: A person who, by virtue of training and experience, can perform specified tasks satisfactorily and safely. |
| Consumables | An item of equipment or material that is purchased for a specific job or an item that requires regular replacement. |
| Equipment | means the Supplier’s equipment, plant, materials, and such other items supplied and used by the Supplier in the performance of its obligations under the Agreement. |
| KPI’s | means Key Performance Indicators as referred to in the appendices of this Agreement. |
| Lead Site Representative | The most senior member of Contractor staff who will regularly attend the Affected Property |
| Maintenance | Maintenance includes all works necessary to respond to a problem on site and complete the solution, including planned maintenance, breakdown, spares, specialist, out of hours works, access equipment, replacement of redundant parts or redundant systems where required to keep the sites fully operational at all times |
| Procedures | The term refers to any written statement describing how an activity should be performed. Work instructions, method statements, process maps are all forms of procedure. |
| Reactive Maintenance | Maintenance, carried out after a fault, intended to put an item into a state where it can perform a required function in a safe and efficient manner. |
| Relationship Manager | The senior executive of the Contractor who will have authority over all those working on the Service and be the point of escalation. |
| Specification | Means the description of the Services to be provided under the Agreement. |
| Staff | Means all persons employed by the Supplier to perform the Services together with the Supplier’s servants, agents and sub-Suppliers used in the performance of the Services. |
| Stores | Means all storage facilities including grounds, F&B, retail, collections and zoo. |
| Supplier | Means the supplier of this Service outlined in the Specification. |
| The Client | The Horniman Public Museum and Public Gardens Trust |
| The Collection | All material held in trust including zoological collection by the Client |
| The Contractor | The supplier of the Service |
| The Scope | The document providing the specification for the Service |
| The Service | Provision of full planned and reactive maintenance of the Affected Property for the period stated in Contract Data |
| The Service Manager | The member of the Client team to which the Contractor is accountable, individual named in the Contract Data |
| Working Day | Means any working day from Monday to Friday excluding bank holidays. |

## Overall objectives

The Contractor shall provide Estates Maintenance (planned and reactive) for the Client’s unique estate (the Affected Property), as outlined below in the Scope and the Scope appendices. The Client is looking to partner with an experienced contractor of maintenance and reactive works who can deliver best in class service.

The Service should reflect the unique environment and address the challenges of working in historic public buildings, around The Collection and alongside Client staff and the Public.

## Description of the Service

### The Contractor shall provide full planned and reactive maintenance service as outlined in the Scope for all assets and activities detailed within the Scope.

### For the avoidance of doubt all assets, unless otherwise stated, shall be considered to be inclusive of all associated infrastructure including, but not limited to controls, valves, pipework and ductwork.

### The Contractor shall comply with all requirements of the Scope to ensure that all spaces are fully functional, with minimal downtimes, that responses to call-outs are within specified time periods, and that the pre-determined environmental conditions in each area are maintained. A high standard will be required and appropriate resources provided to ensure the safety and security of the Client’s employees/resources and the general public.

## Affected Property

### The Client estate is;

- The Horniman Museum and Gardens, 100 London Road, Forest Hill, SE23 3PQ

- The Study Collection Centre, Dreadnought Building, Old School Close, Greenwich, London, SE10 0PU

### During the course of the Service, it is possible that elements of the Affected Property may be exited or acquired. In these circumstances, the Client and the Contractor shall be required to review the Scope and if changes are necessary issue a Task Order.

### The Affected Property will be restricted to those areas defined in Appendix A

## Type of Contract

The works covered by this Scope and associated documents shall be undertaken as a fixed price contract between the Client and the Contractor utilising the New Engineering Contract 4 (NEC4) Term Service contract.

## GENERAL CONSTRAINTS ON HOW THE CONTRACTOR PROVIDES THE SERVICE

## Use of the Affected Property

### When the works area is in an occupied part of the building every effort shall be made by the Contractor to ensure that any interference is kept to a minimum. All storage space, offices, corridors, galleries etc. and especially access ways, fire exits etc. shall be kept clear of equipment, materials etc. at all times

### When working in public areas, the working area shall be barried off.

## Access to the Affected Property

### The Affected Property contains a secure series of buildings within which priceless Collection items are exhibited and stored. The Contractor shall remember at all times that the safekeeping and public display of the Collection are the primary function of the Client. All work should intrude as little as possible on these functions.

### The Contractor shall make every effort to minimise the disruption to visitors and staff, particularly when working in public areas.

### Due to the public nature of the Client heightened periods of security may be required from time to time and the Contractor shall ensure all their staff and subcontractors are fully conversant with the associated access restrictions and requirements in this regard on an ongoing basis.

### There is no permanent Contractor parking available on the Affected Property. Limited parking is available for open use to all Client contractors and visitors with access needs.

### The Contractor may for various operational reasons be denied access to buildings or areas of buildings and may at times be required to work under escort. Maintenance programmes, times and work patterns shall be tailored to suit the Client’s operation, occupation and other requirements/activities on the Affected Property.

## Deliveries

### Access for delivery of materials to be arranged via security at each site by the Contractor.

### All deliveries at the Affected Property will enter the site through the Horniman Drive gate at the London Road site and through the access gate at the SCC.

### For all exceptional circumstances not covered by the above must be arranged via the Service Manager.

## Noise and vibrations

### Noise Control shall be provided to comply with the current relevant part(s) of BS 5228 and with the following requirements:

- No radios or other noise making leisure instruments to be allowed on the Affected Property.

- No noise of any form will be tolerated before 0800 and after 1800 hours without the permission of the Client.

- The Contractor’s staff, subcontractors and others under their control are only permitted to use radios as guided by the Service Manager.

- No excessively noisy power tools, i.e. pneumatic drills etc. will be permitted on the Affected Property without prior approval of the Service Manager.

- Adequate supervision shall be provided by the Contractor to ensure no annoyance, damage or nuisance due to noise occurs within the public areas of the Affected Property while undertaking the Scope works.

## Working Hours

### The normal opening hours for the museum are as follows:

- Monday to Sunday 10:00 – 17:30

- Four lates every year from 10:00 – 21:00 however, some may extend until 22:00

### There is 24/365 security presence based at Horniman Museum, London Road.

### Events and commercial activity regularly take place outside of core hours, opening hours and hours of security coverage. Where a support of these activities is required access shall be arranged with the Service Manager.

## Parking

### The Contractor will have use of limited parking for all Client contractor allocated vehicles at the following locations;

- Contractor parking bays, London Road

- Study Collection Centre, Greenwich

### Access for delivery of materials to be arranged via the Service Manager

### No casual parking is allowed

### The Client shall not be liable for vehicle damage, losses, penalties etc. against Contractor vehicles either on or off the Affected Property.

## Use of Equipment

### Tools

- Hand tools, including powered hand tools, must not be left unattended. If an operative leaves a job temporarily all tools must be secured.

- All tools should be adequately labelled with the Contractor’s logo or name. All losses shall be immediately reported to the Service Manager.

- The Client does not accept responsibility for any losses of materials etc. however caused.

- At the end of the day all tools must be removed to a place of security within the Contractor’s accommodation.

- All tools shall be transported around the Affected Property by suitable means, such as a tool box or bag in order to minimise the risk of damage to the Collection and building fabric.

### Scaffolding and Plant

- The Contractor is to provide all equipment required for access (e.g. scaffolding, access ladders etc.), and the Contractor shall ensure all users of this equipment are fully trained and compliant with permits to work, RAMS, and all relevant regulations.

- The Client owns access equipment detailed in Appendix D, which is available for use by the Contractor, the Contractor shall utilise and maintain the equipment as if owned by the Contractor. Liability for use shall be held by the Contractor, including maintaining ladder register.

- No steps, ladders or other plant shall be left accessible for unauthorised persons to enter the building or adjoining buildings.

- No fixed or external scaffolding shall be used without the expressed permission of the Service Manager. When used a certificate of approval shall be issued and be followed up by regular inspections in accordance with good practice. All necessary licenses shall be obtained, all fees shall be paid by the Contractor.

- No scaffolding or other access equipment shall be attached to the fabric of the building without prior permission of the Service Manager.

- All ladders in permanent use, either singly, or forming part of scaffolding external to the main structure must be firmly padlocked and chained against removal. A single ladder or, where appropriate, the bottom section of multiple ladder access to scaffolding shall, at the end of work activity be returned to secure storage or removed from the Affected Property.

- All fixed external scaffolding shall be alarmed

- Appropriate lightning protection shall be in place on all external scaffolding.

### Client Equipment

      - If the Contractor is permitted to use equipment, plant and materials or other such property belonging to the Client the following provisions shall apply;

- All Client property remains the Property of the Client.

- The Contractor is responsible for their own costs resulting from any failure of the Client’s property, unless it can be demonstrated the Client was responsible for repair and replacement of the Client’s property and caused undue delay in its repair or replacement.

- The Contractor maintains all items of Client property in good and serviceable condition in accordance with the manufacturer’s recommendations

- The Contractor is liable for any loss of or damage to any Client property save to the extent that the Contractor is able to demonstrate that such loss or damage was caused by the Client.

## Restrictions on the use of hazardous materials

### The Contractor shall deliver the Service in accordance with the current CoSHH (Control of Substances Hazardous to Health) Regulations and include the information within their site-specific risk assessments and method statements.  Key risks shall also be included and update in the Early Warning Register.

### The Contractor shall provide and maintain at the Affected Property a copy of the current Material Safety Data Sheet (MSDS) for all substances used together with any COSHH Risk Assessments required under the CoSHH regulations. Where the use of hazardous substances has the potential to impact upon the Client’s staff or other visitors a copy of the current MSDS and CoSHH Risk Assessment is provided to the Service Manager before using the substance.

### The Contractor is responsible for all necessary secure and safe storage, fire-fighting equipment, and environmental protection measures required for the substance. Any additional space or storage requirements are to be brought to the Service Manager’s attention at the earliest possible opportunity.

## Storage of fuel and chemicals

### The Contractor is responsible for all necessary secure and safe storage, fire-fighting equipment, and environmental protection measures required for the substance. Any additional space or storage requirements are to be brought to the Client’s notice at the earliest possible opportunity.

## Pollutions, ecological or environmental impacts

### Smoking is not permitted anywhere within the Affected Property and its environs and vaping is not permitted in the buildings.

### All assets shall be maintained to high levels of cleanliness, safety and performance in order to minimise dust and pollutants entering in to the Affected Property, in particular areas housing the Collection.

## Client specific policies and procedures

### The Contractor shall provide a professional service which as well as being fully compliant with all statutory and good industry practice requirements shall also be compliant with Client policies as determined by the Client for all areas of the Service. The policies shall include but are not limited to those outlined in the appendices.

## Constraints imposed to meet the requirements of Others

### Catering Areas: The Client’s contractor delivering catering services shall be responsible for maintaining the catering equipment, including cleaning of kitchen extract fans and grease traps, the Contractor shall be responsible for all other maintenance services within these areas as defined in the Scope.

## Contractor Travel

### The Contractor shall include in their prices and rates for all services, all subsistence, travel, transport and all associated costs. Rates and prices quoted in the Price List shall be deemed to be inclusive all such charges, rates and associated costs.

### No claim for travel, transport, subsistence or any other such charge will be entertained.

## Confidentiality

### The Contractor shall at all times ensure the confidentiality of the Client is protected as set out in the contract documentation.

### Any concerns in this regard concerning or raised by the Contractor, their staff or their Specialists shall be brought to the attention of the Service Manager.

### The Client may be subject to Freedom of Information requests, the Contractor shall be required to provide information to the Service Manager in support of these.

## Security and protection of the Affected Property

### The Contractor shall adhere to the Client’s security processes for all operatives whom it is intended will work either on the site or have reason to visit the Affected Property during the course of the Service.

### The operatives will then be security cleared. Should any operative fail to be cleared they will not be allowed to work on the contract. Any Contractor staff working on the site shall adhere to the Client safeguarding behaviours guidance.

### The Contractor shall work with the Client ensure all Contractor staff have Disclosure and Barring Service clearance in place in order to work unescorted on the Affected Property.

### The Contractor shall issue all requests for access to the Service Manager.

### All the Contractor’s operatives are to observe the Client’s security requirements both verbal and written instructions given by authorised personnel.

### Prior to being security cleared, the operatives shall report to the Security control room and shall sign in. A pass shall be issued to each operative which shall be visibly carried at all times by the operative whilst on the Affected Property.

### If requested when working within an occupied area the operative shall, as a matter of courtesy, explain why they are there and briefly advise what they are proposing to do. When leaving the Affected Property, the operative shall report back to Security Staff, hand back the pass and sign out.

### No operative is to go beyond the working area or the access routes to and from it, along with the designated access route to the toilet accommodation, as identified on the drawings or advised by the Client, without the specific permission of the Service Manager.

### Access to stores will be supervised by the Client and agreed in advance with the with Service Manager.

### It is the responsibility of all Contractor staff to ensure all areas of the Affected Property are left secure.

### The Contractor’s staff, their subcontractors or those working on behalf of the Contractor shall all wear clear identification in the form of the Contractor’s company name and photographic identification at all times whilst on any of the Affected Property or undertaking works associated with the Affected Property.

### Client ID cards shall be displayed at all times when on the Affected Property.

### The Contractor shall have complete responsibility for the safety of their own staff and subcontractors.

### No keys are to be removed from site by the Contractor. The Contractor shall be responsible for the safekeeping of any keys issued to them and shall be responsible for the cost of replacing the locks of any compromised entry points due to lost keys. Upon completion of the services, all keys shall be returned to the Client at the end of each working day.

### Due to the high-profile nature of the Client the Contractor can expect for all infringements to be fully investigated.

## Protection of the Affected Property

### The Contractor and all those working on behalf of the Contractor are to take due care to avoid causing damage to the Affected Property and its contents when delivering the Service.

### The Contractor shall not handle or move the Collection nor move Collection storage furniture. If access is only feasible by doing so, then only Client staff will carry out the access preparation work, after due notice period with the Service Manager.

### If the Contractor’s staff or those working on behalf of the Contractor cause damage to the Affected Property or it’s contents in the course of delivering the Service, this shall immediately be reported to the Service Manager and the Contractor shall bear responsibility for prompt repair, rectification or replacement of the damaged equipment or material, at no additional cost to the Client at the discretion of the Service Manager. If the Service Manager decides that this work is best delivered by a 3rd party then the Contractor shall pay compensation to the Client in accordance with the extent of the damage, the remedial work necessitated and any other costs associated works associated with mitigating the impact to the Affected Property, contents or Client activities.

### The Contractor shall be responsible for producing high level works and will gain prior approval from the service manager for access to high level lighting in galleries etc. together with the required protection of the Collection below. The Contractor will be responsible for the supply of all plant and equipment and in liaison with the Client, the programming of such work required in this regard form part of the Scope.

## Protection of the work on the Affected Property

### The Contractor shall, at all times, take all necessary precautions to minimise inconvenience and avoid disruption to the business of The Client.

### They shall take all necessary precautions to prevent injury to persons or damage to the Affected Property arising from the carrying out of the Service.

### For planned Works that effect activity of the Affected Property (PPM and reactive calls), the Contractor shall have responsibility to liaise with Client staff, to discuss their requirements, advise Client staff of their estimated time of arrival, details of any potential disruption and advise completion of the Works.

## Consideration of Others

### The Contractor shall ensure that all works are to proceed so that they may cause the minimum of inconvenience to Client staff, visitors and neighbours.

### Prior to the commencement of any works which are likely to cause disruption Client staff, visitors and neighbours the Contractor shall apply for approval to commence from the Service Manager and give notice of at least 5 working days.

### No obscene literature or language of any variety will be tolerated on the Affected Property.

### No pets will be allowed on the Affected Property.

### At all times Contractor staff should be aware that they are representing the Client when interacting with the public. If they are unable to deal with a member of the public’s request they shall ensure that they are referred to the nearest member of public-facing Client staff.

## Cleanliness

### The Contractor shall keep all areas where they are working in a clean and tidy condition at all times.

### All plantrooms and working areas shall be maintained in a clean and tidy condition

## Waste Material & Sustainability

### The Contractor shall remove all waste generated by them and their subcontractors in accordance with the Client’s guidance.

### The Contractor shall clean and remove from the Affected Property all rubbish, debris and redundant material arising from the provision of the Service in a safe, sustainable and certified manner.

### The Contractor shall ensure that all used filters are removed from site and recycled, where possible.

### Where replacement parts are provided and installed, the Contractor shall ensure that any redundant plant and equipment is removed from the Affected Property and disposed of in accordance with the requirements of the Waste Electrical and Electronic Equipment (WEEE) 2002 and other relevant regulations.

### All waste held temporarily on the Affected Property shall be deposited in a location approved by the Service Manager at the end of each working day

### All waste should be minimised by The Contractor and Subcontractors and it should be diverted away from zoo areas.

## Sustainability

## Zoo : Aquarium, Animal Walk and Butterfly House

## Advertising

### The Contractor shall not display nor permit others to display any advertisement on or about the works or site without the prior written consent of the Service Manager.

### No temporary or permanent advertisements, board, notices or signs will be permitted on the works, the Affected Property or boundary walls and fences thereof.

### The Contractor shall not use the name, logo or reference to the Client in any advertising or promotional material without seeking written consent from the Service Manager.

## CONTRACTOR’S PLAN

### The Contractor’s Plan shall be submitted for approval by the Service Manager prior to contract commencement, as part of the mobilisation, with the exception of the full asset verification report.

### The Contractor’s Plan will set out a detailed method statement of scheduled maintenance activity for the first year of the Service, based on routine works being carried out within the advised working hours and in line with manufacturer maintenance recommendations, British Standards, HVCA guide, SFG20, BSRIA guidelines and the specific requirements of this Scope unless agreed with the Service Manager.

### The Contractor shall provide the Client with a Planned Preventative Maintenance (PPM) Schedule for the Affected Property as part of the Contractor’s Plan based upon the asset information provided in Appendix B.

## TASK ORDER

### The Client reserves the right to submit additional assets/activities for inclusion in the Scope during the contract.

### If additional Scope is identified it shall be instructed to the Contractor by the Client through a Task Order.

### The Contractor shall provide the Service Manager with an updated Contractor’s Plan including a Task Order programme in response to the Task Order within 30 days.

### The Contractor shall submit the Task Order programme to the Service Manager for acceptance.

### The Contractor does not proceed with the relevant work until the Service Manager has accepted the Task Order programme.

### When a Task Order is issued;

- The Task price list is inserted in the Price List and

- The work involved is added to the Scope

### The issue of a Task is not a compensation event

### All task orders shall be issued and managed in a format agreed by both parties during the mobilisation period

## QUALITY MANAGEMENT

### The Contractor shall deliver the Service in line within it’s own Quality Management Policy and all quality management objectives as expressed by the Client.

### The Contractor shall detail within the Contractor’s Plan the approach to quality management plan in accordance with the best practice.

### All works carried out in the Service are to be governed by the Contractor’s quality methodology detailed within the Contractor’s Plan, which shall include quality assurance processes and frequencies both on and off the Affected Property.

## TESTS AND INSPECTIONS

## Testing

### When works are completed as part of the Service or as a Reactive Work Order, the Contractor shall be responsible for testing the complete installation and associated systems.

### The Contractor shall provide all necessary certified instruments, labour and materials to carry out the specified tests.

### The Client shall provide, free of charge, electricity, water and fuel as may reasonably be required to carry out the specified tests.

### If in the opinion of the Service Manager any part of the works fails the specified tests then the Contractor shall remedy any defects and re-test that part of the installation to the satisfaction of the Service Manager at the Contractor’s expense.

### The Service Manager may also invite a Client representative to witness and sign off tests.

## Certification, licenses and approvals

### The Contractor, on behalf of the Client and in its own right as applicable, shall obtain and maintain for the period of the Contract all necessary statutory and regulatory approval certification and licensing to provide the Service and for the assets, plant and equipment associated with the Scope.

### All certification and records shall also be clearly identified and logged as part of the Contractor’s record management system for the Client’s review.

### The Contractor shall include in their monthly reporting any upcoming testing or other requirements associated with maintaining the full compliance of the installations and / or any areas where current compliance is at risk.

### The Client may carry out annual compliance checks with outside consultants in respect of Fire Certification, Asbestos, Water Risk Assessments etc.

### Any additional recommendations identified may be passed to the Contractor to be quoted as reactive works orders; however, this in no way removes the requirement for the Contractor to maintain the works in a compliant state on a day to day basis.

## MANAGEMENT OF THE SERVICE

## Project Team

### The Contract Data identifies the Client, Service Manager, Health & Safety Advisor and Contractor and the conditions of contract state what each is required to do.

### Client Team

The Client shall be members of the Client team or their designated representatives. In all matters the Service Manager shall ultimately instruct the Contractor.

### Contractor Team

#### The Contractor shall ensure there is a high level of management associated with the works under this Scope with suitable experience and expertise within the maintenance field available within the Contractor team at both a site and management level.

#### The Contractor staff shall remain consistent throughout the period of the Service and only be changed by agreement with the Client and giving a minimum of 1 months’ notice of any such proposed change.

#### This to include monitoring of attendance and management of any required holiday or sickness cover to maintain the agreed minimum resource levels detailed in the Scope with staff fully conversant with the Affected Property, assets and buildings covered by the Scope. Equally all staff employed are to be able to move across the Affected Property as required with full knowledge of the installed services at each individual site.

#### The Contractor shall provide and maintain a method statement in the Contractor’s Plan detailing how the Service will be managed in terms of on-going management including:

              - Management roles and responsibilities,

              - Administration/back office support roles and responsibilities,

              - A reporting structure chart

              - The CVs for the proposed Contractor roles who will be responsible for managing the Service, demonstrating appropriate experience and qualifications, including, but not limited to those listed below;

### Lead Client Representative

#### The Contractor shall identify the most senior member of Contractor staff in regular attendance on the Affected Property as the Lead Client Representative.

#### This Lead Client Representative shall be authorised to receive instructions and to be the point of contact between the Contractor and the Client on a day to day basis throughout the course of the Service.

#### This individual will, on behalf of the Contractor attend all meetings with the Client regarding the Service and authorise and sign all reports submitted to the Client by the Contractor.

#### Any change to this role is to be agreed by the Client with a minimum of 1 months’ notice of such a proposed change.

#### This Lead Client Representative shall take responsibility for the day to day relationship with the Client, coordinate, and manage the Client’s requirements

### Client Relationship Manager

#### The Contractor shall name a Client Relationship Manager who shall be a senior executive of the Contractor who will be have authority over all those working on the Service and be the point of escalation.

### On-site management of subcontractors

#### The Contractor shall be responsible for the day to day management of their subcontractors and that for all subcontractors the Client’s Permit to Work System is adhered to at all times.

#### This shall also include arranging and escorting subcontractors or others under the Contractor’s control both to gain access to the Affected Property and to the work area concerned, arranging necessary permits and H&S documents as may be required. In no way should the Client be required to provide this service.

#### The Contractor shall also provide such attendance as required by their subcontractors or others under the Contractor’s control in respect of access to the Affected Property and restricted areas and or local service isolations.

#### The Service Manager shall be advised of any planned attendance by subcontractors or others under the Contractor’s control on a minimum of a weekly basis.

## Communication System

### All communications between the Contractor and the Client are to be undertaken using electronic mail as the preferred method of communication.

### All verbal communication or instructions received by the Contractor or others under their control are to be recorded as above and stored in an agreed location.

## Helpdesk

### The Client operates a Helpdesk that covers multiple services.

### Client staff are directed to email maintenance job requests and faults to a central email address.

### The Client reviews the requests and assigns them to the Contractor

### The Contractor shall provide regular updates on every job to the Client

### The Contractor shall define the process for managing helpdesk requests in the Contractor’s Plan

### The Contractor shall provide the Client with information relating to their management of this element of the Service as part of the regular reporting.

### The Client operate a Helpdesk that covers multiple services.

### Client staff are directed to email maintenance job requests and faults to a central email address.

### A Client estates co-ordinator reviews the requests and assigns them to the Contractor utilising the following fields;

- Request Type: Plumbing, Electrical, Lighting etc.

- Location: Area within the Affected Property

- Secondary location: Further detail

- Status: New, Acknowledged, Awaiting Parts, Complete, Cancelled

- Department: Including sub-departments

- Owner: Contractor or Client

- Priority: High/Medium/Low

- Comment: Additional details

### The Contractor shall provide regular updates on every job to the Client

### The Contractor shall define the process for managing helpdesk requests in the Contractor’s Plan

### The Contractor shall provide the Client with information relating to their management of this element of the Service as part of the regular reporting.

## Management Procedures

### Meetings

The Contractor shall include for attending regular meetings on-site with the Client staff and the Service Manager to discuss the progress of the Service and any issues relating to it.

### Meeting Frequency/Attendance

### The Contractor shall make the following Contractor staff available for the defined meetings;

### Weekly Meeting

#### The Contractor shall provide the Client with the following information, as a minimum, at the weekly meeting;

- Any H&S or operational impact issues in the week ahead

- A review of planned work for the following 2 weeks

- A review of known Reactive works to be undertaken

- A review of the previous weeks works

- A review of planned resource (Contractor and Subcontractor)

- Any local access requirements

- Any local isolations required / planned

- Resourcing (inc. holiday/sickness)

- Any other matters raised by the Client team

### Monthly Meeting

#### This meeting will require the Contractor’s Lead Client Representative to provide an update and assessment of Contractor’s performance in accordance with the Scope.

#### The Contractor shall issue an agenda a minimum of 3 working days ahead of the monthly meeting and shall produce minutes.

#### The Contractor shall present a proposal for a monthly reporting template as part of the Contractor’s Plan. This template shall be agreed with the Client. As a minimum, this document shall include key information relating to performance for the reporting period and forward planning for the next period.

#### The Contractor shall issue the report a minimum of 3 working days ahead of the monthly meeting.

#### The report shall contain;

- a dashboard of key contract metrics including financial performance and KPIs.

- Actions from the previous monthly meeting

- KPI Report including data

- Orders issued over the year and status of each individual order.

- Small project work summary

- List and date of subcontractors attending the Affected Property

- Building update and plant conditions

- Finance

- Holidays and cover used

- Events carried out and any future events listing engineer’s hours

- Health and Safety identifying accidents, Near Misses, Any concerns

- Training requirements or undertaken and Toolbox talks carried out.

- Utility data trends for the Affected Property, classifying any outliers in the trends

#### During the period of Service the Client and Contractor shall by agreement have the opportunity to add further measurable items to this list, such items to be implemented by the Contractor within 30 days of request.

#### The Contractor shall take minutes of the meeting and issue them for review a maximum 5 working days after the meeting.

### Quarterly & Annual Review Meetings

#### These meetings will require the Client Relationship Manager supported by the Contractor’s Lead Site Representative to provide an update and assessment of Contractor’s performance in accordance with the Scope.

#### The Contractor shall issue an agenda a minimum of 5 working days ahead of the meetings and shall produce minutes.

#### The Contractor shall present a proposal for a quarterly and annual reporting template as part of the Contractor’s Plan. This template shall be agreed with the Client. As a minimum, this document shall include key information relating to performance for the reporting period and forward planning for the next period.

#### The Contractor shall issue the report a minimum of 5 working days ahead of the monthly meeting

#### The report shall contain a dashboard of key contract metrics including financial performance and KPIs.

#### During the period of Service the Client and Contractor shall by agreement have the opportunity to add further measurable items to this list, such items to be implemented by the Contractor within 30 days of request.

## Contractor’s Application for payment

### All works shall be agreed prior to commencement with the Service Manager.

### All works shall require a purchase order to be in place before commencement.

### Correct and accurate monthly invoices shall be submitted to the Client, giving a clear breakdown of service solutions provided and include all maintenance, supervision, consumables and sundries as separate items. Invoices should be submitted at the end of the month.

### All invoices shall be checked and signed off by the Service Manager.

## WORKING WITH THE CLIENT AND OTHERS

### The Contractor shall be responsible for identifying where delivery of the Service may clash with the activities of others operating in the Affected Property. In such instances, the Service Manager shall decide which activity takes priority.

### Where the Client team or other contractors are appointed by the Client to deliver activity within the Affected Property the Contractor shall cooperate fully at the direction of the Service Manager.

### The Contractor shall inform the Client of any complaints received in connection with the Service.

### The Contractor shall deal directly with any such complaints and provide a senior employee and any specialists required to attend meetings at the Client’s request and at no additional cost to resolve such complaints.

### Where the Contractor is required to incorporate work provided by others, the Contractor’s responsibility in respect of such work shall be limited to reviewing it and co-ordinating such work to the extent required to ensure the satisfactory performance of the Service.

### The Contractor shall be responsible for obtaining such information as necessary to update the Client Asset Register following such works.

### The Contractor shall at all times be the primary contact for liaison with and coordination of works within the Affected Property in respect of the statutory supply authorities and utilities providers (Gas, Water, Electricity, Telecoms etc.) in order to deliver the Service.

## SERVICES AND OTHER THINGS TO BE PROVIDED BY THE CLIENT

## Contractor Space

### The following Contractor space is available at the Affected Property for use by the Contractor:

- Communal mess (used by Client staff)

- Store (Horniman Museum)

- Desk Space in Client Security Office (Horniman Museum)

- Ad hoc storage on the sites of the Affected Property

### There is little on-site storage available other than for lamps and critical spares, critical spares can be stored in plantrooms associated with the spares but this must be done in a manner compliant with H&S guidance.

### For dedicated Contractor spaces, sole responsibility for cleanliness and decoration shall be with the Contractor.

## IT

### Basic PC provision linked to the Client BMS is available in the Client Security Office

### Additional PC’s and software required for the Service are to be supplied and maintained by the Contractor.

## Telephones

### The Contractor will have access to the relevant Client’s mobile phones at each site, however all other mobile communications are to be provided and maintained by the Contractor.

### The Contractor shall provide a mobile phone for use of the other on-site operatives to be used when they are ‘on-call’ or when they leave the Affected Property.

### Out of hours phone calls should be X

## Radios

### The Client will provide radios to cover both sites which shall be signed out and returned within the duration of the time on site by the Contractor.

## Catering Facilities

### There are no Client catering facilities at the Affected Property, however Contractor staff are at liberty to use the various public catering outlets within the Affected Property at break times subject to availability and provided a clothing is clean and tidy.

### The Contractor shall have access to the staff mess rooms where kettles, microwaves and fridges shall be available.

### Identification must be displayed at all times when on the Affected Property including catering outlets. However, high visibility clothing shall be removed when in public catering outlets.

## Utilities

### Electricity and water required for the delivery of the Service can be utilised where available on the Affected Property by the Contractor.

## HEALTH & SAFETY

## General

### The Contractor shall ensure compliance with all relevant statutory and good industry practice obligations regarding Health, Safety and Environmental management that arise out of, or in context with, the work undertaken by the Contractor. The Contractor is also expected to comply with any additional requirements as detailed in the Client’s Health and Safety Policies and any other instructions issued by the Client Health & Safety Advisor.

### The Contractor shall be responsible for all statutory or mandatory legislation affecting this Scope in its entirety, now and as it may change.

### The Contractor will be responsible for the H&S management directly associated with the Service only, overall Health and Safety management of the Affected Property is supervised by the Client’s Health and Safety Advisor.

### The Client will arrange ad hoc inspections to ensure that the Contractor complies with the relevant health and safety control measure and requirements. The Contractor shall allow the Client access to observe tasks in progress for this purpose.

### The Contractor shall be mindful that significant parts of the Affected Property are open to the public and consideration for this should be made when undertaking all activities.

## Affected Property Users

### The Contractor shall, when delivering the Scope, ensure at all times the protection of the health and safety of all occupants of the Affected Property; Staff, employees, users, visitors and others that might reasonably be affected by their acts or omissions.

## Unsafe Conditions

### If the Contractor discovers any dangerous situations, inside or outside of the Affected Property, they shall bring these to the attention of the Service Manager by phone, then follow up in writing.

### Should any of the Contractor’s access equipment become damaged or unsafe they shall be scrapped and replaced by the Contractor.

## Fire or Water Hazards

### Any works performed by the Contractor likely to give rise to hazards from fire or water, such as the use of a naked flame, or cutting in to pipework, will be carried out in such a way as to observe the safety and protection of the Affected Property and staff and must be carried out in the presence of suitably equipped members of Contractor Staff. The Service Manager must be made aware of the use of a naked flame before any such work is undertaken.

### The Contractor shall adhere to the Client permit to Work process as detailed in the Client’s Health and Safety Policy.

### The Contractor shall ensure all existing, new or temporary fire escape routes are maintained clear and accessible at all times.

## Asbestos

### The Asbestos Register is available for inspection at Head of Estates Office.

### The Contractor shall provide updates for the Client’s Asbestos Register to the Service Manager and update all of the Contractor’s own records and associated risk analysis, of all areas within the Affected Property, identifying those which:

- Are presumed by the Contractor to contain asbestos;

- It has been concluded by The Contractor that they do contain asbestos;

- It has been concluded by the Contractor that they do not contain asbestos;

- Are presumed by the Contractor that they do not contain asbestos (if in doubt, asbestos shall be presumed present).

### The Client has removed or identified most of the asbestos from the Affected Property. However, it is possible that some areas of the Affected Property may include asbestos based materials that have not been previously identified within the Asbestos Register.

### It is the Contractor’s responsibility to bring to the attention of the Service Manager any area they consider asbestos based material is evident.

### In the event of suspect material being found the Contractor shall immediately stop works, carry out procedures as set out in their risk assessments, method statements or site safety guidance and inform the Service Manager.

### Where asbestos based materials have been discovered in the past and not removed, the asbestos has been encapsulated and labelled accordingly and recorded in the Asbestos Register.

### The Contractor shall not use asbestos, or asbestos based materials in the execution of the works.

### The Contractor shall discharge its obligations under the Control of Asbestos at Work Regulations 2006 and any other subsequent regulations and its amendments and associated Approved Codes of Practice.

## Equality Act

### The Contractor shall be aware at all times of the implications of the Equality Act 2010 (including all subsequent amendments thereto and associated statutory instruments) and shall draw to the attention of the Client any issues at the Affected Property in relation to this legislation.

## Legal Compliance

### The Contractor is to comply with the Health and Safety at Work etc. Act 1974, including all associated statutory instruments subsequent amendments thereto and, to ensure the provision of premises, equipment and systems of work that shall be safe and without risks to the health of the public, occupants or third parties. This shall include including the Workplace (Health, Safety and Welfare) Regulations, Management of Health and Safety at Work Regulations, Provision and Use of Work Equipment Regulations, Personal Protective Equipment Regulations, Manual Handling Operations Regulations, Display Screen Equipment Regulations, Electricity At Work Regulations, Control Of Substances Hazardous to Health Regulations.

### The Contractor shall be obliged to conform to all EC and UK statutory and legislative requirements and to keep up to date with all changes in law that may affect the Service on the Affected Property, and shall alter the provision of Service in reaction to those changes as appropriate. Full cognisance of British Standards, Professional and Trade Codes of Practice shall be taken. All changes shall be communicated to the Service Manager and the Contractor’s Plan updated if required.

### The Contractor shall demonstrate the ability to interpret future legislative changes and advise the Client of the potential for operational and financial impact. This ability shall be further demonstrated by the acknowledgement that only emergency legislation shall affect the Client financially in any one contract year.

## Records

### If requested by the Client or Client’s Representative, the Contractor shall provide evidence that materials, workmanship and processes used or intended to be used in Providing the Service comply with the standards required under the Scope and other contract document.

### The Contractor shall regularly update all maintenance records for the Client, including the plant and equipment asset registers, PPM Schedule and logbooks, to enable an audit trail to be established in accordance with the agreed quality standards for the contract

### All maintenance records are to be held onsite at each site on the Affected Property, along with back-up copies that the Contractor holds off-site.

### The Contractor shall retain throughout the period of the Service copies of drawings, specifications, reports, calculations and other documents which record the Service; documents and information obtained or prepared by the Contractor or any of their subcontractors in connection with the Service.

## PPE

### The Contractor shall supply all necessary PPE to all those under its control, applicable to the tasks being performed.

### There are honeybees hives on the grounds of the Horniman Museum and Gardens. The Supplier’s Risk Assessments and Method Statements shall include working around bees.

### The Client will not permit tasks to proceed if inappropriate or no PPE is found to be in use. In such cases the Client will not be liable for any abortive time etc. associated with providing the correct PPE.

## Safe Systems of Work

### Safe systems of working shall be provided for all areas where high-level access is required for the purpose of maintaining and or upgrading building elements or services

## Permit to Work System

### The Client operates a ‘Permit to Work’ system across the Affected Property

### The Contractor shall adhere to all elements of the Client’s Permit to Work process as detailed in the Health and Safety Policy.

### The Contractor is to ensure all staff and subcontractors understand the implications of the conditions listed on the Permit.

### A request for a Permit to Work form is required in advance of any works being carried out and shall be made to the Service Manager or authorised Estates Department Staff (Security). Hot Works permits must be authorised by the Service Manager.

### Before commencing any work that is likely to interrupt normal operational activities at the Affected Property, a request for authorisation is to be submitted by the Contractor to the Service Manager in the form of a Permit to Work request.

### All works requiring access will require a Permit to Work including, but are not limited to:

- Working in confined spaces

- Hot works

- High and low voltage electricity works

- Working with asbestos

- Working at height including on roofs and scaffold towers.

### The permit to work system is owned and managed by the Client and the Contractor, or others employed by them in connection with the Service, shall conform in all respects to the Permit to work system.

### The Client’s permit to work system will be managed by the Service Manager.

### During the mobilisation period the Contractor and all under their control will be required to become fully conversant with the Client’s local Permit to Work system.

### For all regular activities not specified above there may be the opportunity, in liaison with the Service Manager, to apply for an annual permit to work for low risk activities.

## Signage

### The Contractor will publish all Health and Safety notices for all users of the Affected Property and all other relevant signage related to the Contractor’s works and areas of responsibility.

## Competent Persons

### The Contractor shall advise the Client of the competent person or persons appointed to assist with undertaking the measures required to meet the statutory duties under health; safety and fire legislation in accordance with Regulation 7 of the Management of Health and Safety at Work Regulations 1999. This named person(s) shall liaise on a regular basis with the Client’s Health and Safety Advisor and attend monthly, quarterly and annual review meetings.

### The Contractor shall notify the Client of those persons having management responsibility for health and safety, and their specific duties, on a day-to-day basis where they differ from the person(s) identified above.

### The Contractor shall identify the line management responsibilities for health and safety and the measures taken to ensure these are being executed effectively, to the Client.

### The Contractor shall ensure that their staff or those working on behalf of the Contractor receive training, including induction training in accordance with their duties under health and safety (including fire) legislation and provide a copy of all such training and induction training programs to the Client.

## Authorised Persons

### The Contractor shall ensure that there are persons available with the appropriate technical qualification to undertake the following activities;

#### Electrical

- To carry out electrical risk assessments

- To make LV systems safe for work

- To prepare method statements

- To prepare Safety Programs

- To issue Low Voltage Permits to Work

- To issue Low Voltage Isolation Certificates

- To issue sanction to work on/adjacent live electrical equipment at Low Voltage

#### Mechanical

- To carry out risk assessments for Mechanical systems

- To make Mechanical systems safe for work

- To prepare method statements

- To prepare Safety Programmes

- To issue Mechanical Permits to Work

- To issue Mechanical Isolation Certificates

- To issue sanction to work on/adjacent Mechanical equipment

## INCIDENT REPORTING

### All reportable incidents shall be notified to the Service Manager in addition to the enforcing authorities. The Contractor shall ensure that all accident reports arising from for all accidents and incidents on the Affected Property are copied to the Client. The Contractor shall be proactive in the recording of near miss incidents on the Affected Property, and provide copies of any reports to the Client.

### The Contractor shall be responsible for monthly reporting on accidents to The Client, including ‘nil return’ reporting.

### The Contractor is responsible for providing updated copies of health and safety documentation to the Client, in the event of changes in legislation or other relevant event.

## Construction (Design & Management) Regulations

### Where the Construction (Design and Management) Regulations apply, the Contractor will undertake the duties of Principal Contractor (in accordance with Regulations 13 and 14) and/or Contractor (in accordance with Regulation 15) as applicable.  The Contractor is also the Principal Designer and/or Designer unless an alternative Principal Designer and/or Designer is appointed, and undertakes the relevant duties (in accordance with Regulations 11 and 9 respectively).

## HEALTH & SAFETY SUPPORT

### The Contractor shall provide access to competent help for all Contractor staff and the Client in applying the provisions of health and safety law relevant to the Service.

## Risk Assessments, Method Statements and Safe Systems of Work

### The Contractor shall ensure that Risk Assessments, Method Statements and Safe Systems of work, are produced and maintained up to date for all significant risks arising out of or in context with the Scope, and other associated activities for which he has responsibility/control, and has provided these to the Client and that all  local H&S Risk Assessments, Method Statements etc., remain up to date with regard to the works for which he has responsibility / control. Risk Assessments shall be site-specific and take full account of the effects of any work on building occupants and or the local environment.

### During the mobilisation period and prior to the commencement of the Service, and at regular intervals thereafter, the Contractor shall undertake a full risk assessment of the Service at no additional cost to the Client.

### The Contractor shall also provide site specific method statements (based on risk assessment(s)) for the activities identified within the Scope.

### Risk assessments and method statements are to be site specific and documented by the Contractor, and a copy provided to the Client. The Contractor shall implement such procedures and practices in relation to the Service as are necessary to remove or reduce the identified risks.

## Sub-Contractors

### The Contractor shall ensure that all of their subcontractor’s comply with all legal and Client Health & Safety requirements.

## SUBCONTRACTING

## General

### It is expected that the majority of the works to be carried out under the Scope will be self-delivered by the Contractor; however, a certain limited number of specialist areas may be undertaken by Contractor employed Subcontractors.

### All sub-contractors shall operate within the performance and payment mechanisms of the Contractor.

### The Contractor is responsible for providing the service as if he had not subcontracted the work.

### The Contractor will submit the proposed conditions of contract for each subcontract to the Client for acceptance unless the Client has agreed that no submission is required.  The Contractor shall not appoint a subcontractor on the proposed subcontract conditions submitted until the Client has accepted them.

### It shall be the responsibility of the Contractor to ensure the Client is continuously updated with the names of the Contractor’s staff, supply chain and consultants and their staff operating within the Affected Property.

## Existing Subcontractors

### A list of current subcontractors who activities fall fully/partially within the Scope can be found in Appendix E.

### A number of these subcontractors have specialist skills and knowledge of the Affected Property and systems and although the Client is not specifying contract elements the Contractor should consider the value of this knowledge.

## Vetting

### The Contractor shall institute a stringent vetting procedure when working with his supply chain. Any relationship entered into shall be subject to the headline terms of The Contractor and any reference to The Contractor shall be taken as reference to any sub-contractor working with or on behalf of The Contractor.

### The Contractor shall warrant that the performance measures, within which they are expected to operate, have been transferred contractually to any supply chain sub-contractors.

### The Contractor shall ensure that all subcontractors and supply-chain partners carry adequate insurance for their activities and that they are legally and professionally compliant in all activities performed as part of the Service.

## Change Management

### The Contractor shall maintain consistent performance throughout the Contract term and changes to Subcontractors shall only be by agreement with the Service Manager and subject to a minimum of one month’s notice.

## CLIENT’S SERVICE SPECIFICATIONS

## SERVICE SPECIFICATION INTRODUCTION

### This section is concerned with the particular details of the maintenance of the mechanical, electrical, plumbing and fabric services, and the associated works, required within the Affected Property.

### The Contractor shall be required to work closely with the Client team and the Service Manager will manage the contract on behalf of the Client.

### The Contractor shall provide competent, fully trained and qualified personnel to carry out the contract works within the Affected Property.

## MOBILISATION

### The activities that shall be carried out after the Client has selected the Contractor, but before the Contractor commences work on the Affected Property;

#### The Contractor shall submit the Contractor’s Plan detailing how the Service will be provided, reflecting the requirements of the Scope within the timeframe set out in the Contract Data

#### During the mobilisation period the Contractor is not responsible for undertaking the Service, but shall:

- Ensure that the Client’s rules and procedures are fully understood

- Become acquainted with the Affected Property, layouts and access arrangements

- Allow for attendance of key Contractor personal at meetings with the Client to discuss the actions required in the mobilisation and procedures to be adopted

- Ensure that all Contractor staff are appropriately trained to undertake the scope of work identified

- Ensure that Contractor staff are appropriately trained on the Client BMS and other systems such that they are competent in their correct use

- Ensure that all available information is gathered for the execution of the Service

- Undertake local Health and Safety induction where required by the Client.

- Provide electronic copies of any schedules produced against the Client’s asset registers.

- Provide written reports to the Client covering the following:

          - Asset Exception Report

          - Provide a safety audit of the installations and working areas together with associated RAMs

          - Liaise with the Client to review and update the Client’s Risk registers as required

          - Provide a schedule of suggested spares.

          - Provide disaster recovery plans / method statements for all key systems to be discussed and agreed with the Client

## ASSET REVIEW

### During the first 3 months of the Contract the Contractor shall undertake an asset verification across the Affected Property and produce an Asset Exception Report to bring to the attention of the Client any variance from the data provided, which could materially affect the price submitted, together with costs where appropriate. By the end of this period the Contractor shall be deemed fully aware of the level of installed plant and to be fully satisfied unless, the Client has been notified to the contrary.

### The Client will review the Asset Exception Report with the Contractor to identify defects and may require (but offers no commitment to) the Contractor to;

- Undertake proposed remedial work, based on price breakdowns provided. Or;

- To review the tender scope of work in respect of the plant item concerned

### Each asset shall be given a unique asset number on the Asset Register, either as a QR that can be read electronically or a tag label.

### The Contractor will enter all the updated asset data on the Client’s Asset Register.

## PERSONNEL AND SERVICES TO BE PROVIDED

### Suitably competent and qualified personnel are to be provided as minimum to support the Service.

### The personnel shall provide regular attendance on the Affected Property, to carry out routine maintenance, breakdown maintenance, remedials and small works

### The following specialist trades shall attend the Affected Property as and when required;

- Refrigeration Engineer

- Combustion Engineer

- Gas Safe Engineer

- Additional specialists as required

### The Contractor shall be responsible for providing adequate staff and resources to complete all of the various tasks as detailed in the Scope.

### The Contractor shall state in its tender return the numbers and details staff to provide the cover required.

### The Contractor shall be responsible for devising a suitable shift pattern to provide the Client with the requisite cover.

### The Lead Client Representative shall be equipped with a mobile phone by the Contractor so that they are contactable at all times during normal working hours.

### The Lead Client Representative shall act as the point of contact and shall take instructions from the Service Manager.

### The Lead Client Representative shall liaise, instruct, programme, guide and manage the other operatives on the Affected Property.

### The Contractor shall provide a mobile phone for use of the other on-site operatives to be used when they are ‘on-call’ or when they leave the Affected Property.

### The Contractor shall notify the Service Manager a minimum of one month in advance of any change to personnel working on the Affected Property. The Contractor shall also provide a list of replacement personnel.

### During any period that the personnel are not fully utilised on the necessary routine maintenance they shall carry out minor works and repairs as directed by the Service Manager at no extra cost to the Client.

### Unless otherwise agreed with the Service Manager, if the Contractor does not provide staff to cover the posts detailed by the Contactor in the Price List, The Client shall have the right to make appropriate pro-rata adjustments to the monthly charges. The Contractor shall detail within the Contractor’s Plan how they will provide holiday and sickness cover to ensure the smooth operation of the Scope.

### All personnel attending the Affected Property do so upon the approval of the Service Manager and all non-approved staff shall be replaced by the Contractor.

### The Contractor shall ensure that all new staff are familiar with the Affected Property, fully qualified and trained for the work required before commencing work in the Affected Property.

### The Contractor shall provide CVs for all proposed staff for approval by the Service Manager.

### The Contractor will be required to provide attendance for special events or additional activities; where these occur out of core hours these shall form a Reactive Works Order at the agreed rates when supplemented by time sheets.

### The Client requires maintenance cover 24hrs 365 days per year, with a call-out facility when there are no Contractor staff on site.

### There will be a requirement for a minimum of one call out per month which will be out of hours.

### At least one Contractor operative will be required on the Affected Property on regular day(s) as agreed with the Client during mobilisation.

### All Contractor staff supporting special events and additional activities shall, as a minimum, be fully inducted on the Affected Property. In providing this cover there should be no impact to the Service.

### Commercial activity requiring Contractor support is anticipated to increase during the contact period.

## SKILLS & TRAINING

### The Contractor shall, if required by the Client, provide evidence of staff competence on request and provide the Client access to a regularly updated training matrix.

### The Contractor shall provide the Client with evidence of personnel’s competence on each anniversary of the contract award

### The Contractor shall provide and training plan and skills matrix for all Contractor staff, these documents shall be available to the Client and reviewed by the Contractor on a monthly basis.

### The Skills/training shall include, but not limited to;

- Planned preventative maintenance for the Client’s M&E plant and equipment

- Breakdown maintenance

- Small works, installations

- Replacements to electrical and mechanical services

- Emergency lighting maintenance and testing

- Water treatment

- Chlorination of cold water services and tanks

- Cleaning and chlorination of DHWS calorifiers and chilled water buffer vessels

- Cleaning of plantrooms

- Lamp replacement works

- Fire damper testing

- Boiler efficiency testing

- Controls maintenance

- Annual High Voltage maintenance for main Horniman Museum site

## INFORMATION MANAGEMENT SYSTEM

### The Contractor shall provide a systematic process of information transfer and storage that is to form the central focus for all planned and reactive service provision.

### The Contractor shall include full details of their plan for this process within the Contractor’s Plan.

### The process shall ensure the recording of the location and type of assets within the Affected Property.

### The Contractor shall deliver the results of cyclical maintenance and reactive works through this process

### It will be the responsibility of the Contractor that all data is stored and made available to the Client upon request.

### The Contractor will be responsible for ensuring that their employees are adequately trained to deliver the process

### Assets, each of which are individually numbered are capable of being identified in a system based system hierarchy.

### All managerial, quality monitoring, PPM tasks and reactive activities are to be managed, executed, and monitored through these processes.

### The Contractor have processes in place capable of issuing maintenance work orders to their staff

### The Contractor is to provide the necessary resources to integrate, maintain, extend, and enhance both the quality and the depth of the information held to the mutual benefit of both itself and the Client.

### The Contractor shall capture maintenance costs, both for direct labour and for sub-contract labour, in addition to materials costs for each asset, the Contractor is also to capture other material and sub-contract costs.

### The Client shall in part review the Contractor’s performance (KPI) by regularly and routinely querying the data held by the Contractor to ensure the feedback information associated with its activities is promptly and accurately recorded.

### The Contractor is to ensure that the requirements for full access to Contractor’s records, service information, and assets is achieved.

### The Contractor is to recognise the Client’s ownership of all data used or generated in the delivery of the Scope.

### In relation to reactive activities that result in a repair which cannot be completed due to lead times of replacement parts or the need for Client sanction of costs, the Contractor shall create a measure allowing for the suspension of any activity under this scenario. The Contractor is to agree in advance with the Service Manager the exact criteria for any such potential suspension and / or where this would not be acceptable

### Information systems should be capable of tracking, client visibility and transparency of service reports and service information

## PLANTROOMS

### All plantrooms and working areas shall be maintained in a clean and tidy condition

### The Affected property contains plant rooms that will not be the direct responsibility of the Contractor, however, the Contractor may still be required to access these plantrooms to deliver the Service. Permission of the Service Manager shall be sought where required to access these spaces. The Contractor shall be aware that some of these plant rooms contain live zoological collection and due consideration shall be given to this.

## PLANNED PREVENTATIVE MAINTENANCE

### Planned Preventative Maintenance is to be maintenance activity undertaken on a planned regular/cyclical basis to maintain the condition of an asset to an operational standard at least equal to that it is in at the start of the Service.

### The Contractor shall provide the Client with a Planned Preventative Maintenance (PPM) Schedule for the Affected Property as part of the Contractor’s Plan based upon the Asset Register provided in Appendix B.

### In the Asset Register Appendix B the Client has nominated it’s assets in to 2 catergories and has a different base maintenance requirement for each asset type. It shall be for The Contractor to provide a service that meets the base requirements of each maintenance type. The Contractor shall, where appropriate, make proposals to enhance the service to meet the broader requirements of the Client.

| Asset Classification | Base Maintenance Requirement |
| --- | --- |
| Critical | Planned Preventative & Reactive |
| Non-Critical | Reactive |

### The PPM Schedule shall be developed to ensure;

- Useful lifespan of the asset is maximised

- Efficient and cost-effective use of the asset

- The asset enables Client operations

- The asset is operated safely and compliantly

### The Contractor shall include within their tender and make adequate arrangements to provide the following to deliver the PPM for ME plant and equipment;

- Site familiar staff

- Specialist trades

- Additional labour

- Materials and tools

- Equipment

### The schedule for the planned preventative maintenance shall be controlled by the Contractor and be made accessible to the Client at all times. As a minimum the Contractor shall provide a full copy of the PPM schedule to the Service Manager on an annual basis.

### The PPM Schedule shall set out the timing and frequency of planned maintenance activity for the first year of the Service, based on work being carried out within the working hours identified in the Scope, in line with SFG20 (where applicable), manufacturer maintenance recommendations, British Standards, BSRIA guidelines and this Scope.

### The Client shall be given the opportunity to comment on the PPM Schedule prior to the start of the Service.  Any amendments are to be made by the Contractor at no additional cost before final acceptance is sought from the Client. If the changes result in cost savings these savings shall be deducted from the contract price.

### For each subsequent year of the Service, the Contractor shall review the PPM Schedule with the Client and generate a new annual PPM Schedule for the Affected Property and gain agreement from the Client at least two months in advance of implementation.

### On an ongoing basis during the Service the Client will carry out reviews of the PPM activities being undertaken as set out in the Contractor’s PPM Schedule. The Contractor will provide resource, at no additional cost to the Client, to assist in the planning and undertaking of these review activities.

### Records of these reviews may be forwarded to relevant governance bodies to demonstrate compliance is being achieved across the Affected Property.

## WARRANTEES

### Certain items of plant and equipment are still within the manufacturers warrantee periods.

### The Contractor shall identify these plant items and to ensure any and all maintenance to maintain the manufacturers / installers warrantees is carried out whether specifically identified as a SFG20 requirement or not.

### This shall also apply to any new plant and equipment installed by the Contractor during the Service. Maintenance of all such plant and equipment shall be as required to maintain the manufacturers warrantee for the period of the manufacturers warrantee or 3 months whichever is the longer period.

## BREAKDOWN

### The Contractor shall provide suitably qualified staff to carry out repairs to any item of plant that breaks down or fails to operate.

### The staff provided shall be capable of completing the necessary repair works and re-commissioning the plant.

## REACTIVE WORK ORDER

### Reactive Work Orders shall be used to instruct reactive maintenance requirements where the total cost is in excess of the Comprehensive Reactive Allowance threshold (CRA threshold) of £200.

### Reactive work orders will be raised by the Client to the Contractor

### The Contractor will respond with up to 3 quotes for consideration by the Client with indication of materials, labour and associated mark-ups. The Contractor is to respond with quotes being returned within 5 days unless these periods are changed with the agreement of the Client.

### The Client will monitor progress of the Contractor quotes and resultant works as part of the KPI process.

### The Price List shall be constructed to include a comprehensive element for each site, line item ‘Comprehensive Pot’, which includes all staff, sub-contractors, spares, consumables, tools, training, access equipment, protective clothing and any other cost that is incurred to deliver the Comprehensive Element. The ‘Comprehensive Pot’ should be a standalone line item which allows the remaining Price List submission to operate independently of it’s inclusion.

### All spares are to be included and the Contractor is to allow for replacing redundant parts or systems where required to keep the site fully operational.

### Replacement of parts will be undertaken by the Contractor, where required. All parts replacement up to of Comprehensive Threshold of £200 in each case (including labour, materials, profit margin, overheads, and any other relevant costs) will be carried out within the Contractor’s Plan within the costs identified in the Price List

### Where the cost for an individual event is more than £200 + VAT, the Contractor shall pay for the first £200 excluding VAT.

### An accumulation of a number of small events like lamp replacements would be met by the Contractor as these would be considered to be separate events.

### With the exception of emergencies, no parts replacement with a value in excess of £200 excluding VAT, is to be undertaken without prior agreement from the Service Manager or their delegate.

### Where it is agreed by the Client that the Contractor will undertake a parts replacement with a value in excess of the Comprehensive Threshold of £200 the element above the Comprehensive Threshold will be priced separately by the Contractor on the basis of labour rates and a percentage addition to the net cost of any materials required, as set out in the Price List.

### The Contractor will provide photographic evidence to the Client to evidence that all replacement parts not included as part of the agreed consumable items are necessary. Where the value of the parts replacement is in excess of £200 excluding VAT, photographs will be submitted along with the pricing breakdown.

### The Contractor will not include in its main pricing the cost of works additional to the Scope over £200. These will be priced separately on the basis of labour rates (where capacity labour is not being utilised) and a percentage addition to the net cost of any materials required, as set out in the Price List, and will be supported by photographic evidence of the identified fault.

### The expenditure of the Contractor against their tender pricing will be indicated within the Contractor’s monthly reporting with indication of original allowance, expenditure to date and expenditure in the reporting month.

## SMALL WORKS INSTALLATIONS (e.g. under £10,000)

### As part of the Service where there is capacity for the Contractor’s on-site staff they shall be required to complete small M&E works as directed by the Service Manager. Materials which are not considered Consumables for these works will be charged to the Client by a Reactive Work Order.

### The Client reserves the right not to offer any or any particular Small Works to the Contractor to price and may use an alternative procurement route to deliver such works.

## MINOR WORKS

### Minor Work is work other than Planned Preventative or Reactive Maintenance required by the Client. Minor Works include but are not limited to, replacement, remedial works, major repairs (normally over £10,000), refurbishment, upgrade/improvement works, redecoration, and removal.

### Minor Works will be instructed by the Client to the Contractor via a Reactive Work Order.

### The Client may also request that regular Minor Works to be included in the Service via a Task Order.

### The Client reserves the right not to offer any or any particular Minor Works to the Contractor to price and may use an alternative procurement route to deliver such works.

## EMERGENCY LIGHTING TESTING

### Emergency lighting shall be tested to the requirements of BS 5266. The works shall be completed by the on-site staff. These works are to include both maintained and non-maintained fittings along with associated control and power equipment. The Contractor will also arrange for the programmed testing of all Emergency light fittings

### Testing of emergency fittings will include flick testing (monthly), 1 hour discharge tests (every 6 months) and 3-hour discharge tests (annually).

### For office areas, the Contractor shall endeavour to undertake work at a time that minimises impact to staff based in these areas.

### For gallery areas, emergency lighting testing shall be completed outside of public opening hours.

## LAMP REPLACEMENT WORKS

### The Contractor shall be responsible for monitoring and carrying out lamp replacement works for the Affected Property.

### These works fall into the following broad categories;

- Offices

- Galleries

- External

- Security

### Offices

- Lamp faults to be advised to Service Manager. The Service Manager then instructs Contractor when to replace these lamps

- Lamp replacement works in offices can be completed at any time providing;

- The office occupants agree

- Replacing the lamps does not cause a safety hazard

### Galleries

- Lamp replacement works need to be completed before or after opening hours

- The Contractor will be required to complete regular tours of all gallery areas to identify and replace and defective lamps or fittings. Also as part of moving around the Affected Property they should capture any failed lamps or fittings

- The following shall be excluded from these works;

- Lighting in showcases

- Projectors

### External

- The Contractor is to be responsible for the replacement of all defective external lamps

- The Contractor is responsible for cleanliness and operation of all fittings.

### Stock

#### The Contractor shall be responsible for ordering and keeping stocks of lamps, ballasts and fittings at the Affected Property.

#### As part of the Contractor’s mobilisation activities the existing stock of lamps will be reviewed and discussed with the Client with any deficiencies brought to the attention of the Client.

#### It shall be the Contractor’s responsibility to arrange for the certified disposal of replaced and or broken lamps

#### All lamp consumables must meet the required specification of the Client, in particular for Collection areas. If replacements are not like for like then approval must be sought from the Service Manager.

### Strategy

Where recommendations for upgrading to energy efficient alternatives are viable they shall be brought to the attention of the Service Manager. These recommendations shall also reflect Client conservation requirements.

## CONTROLS

### The Contractor shall provide an experienced controls engineer who is fully conversant with the Building Management Systems installed on the Affected Property

### The Client has a minimum expectation of attendance from the Controls Engineer of one day a month. During attendance, they should make themselves known to the Client.

### When the Controls Engineer is not present on the Affected Property access to specialist support.

## HOLIDAY AND SICKNESS COVER

### The Contractor shall notify the Service Manager a minimum of two weeks in advance of any planned holidays by the site personnel and shall arrange to provide suitable on-site cover.

### Sickness cover shall be provided as soon as possible after the Contractor’s office is notified. A replacement shall be provided no later than 3 hours after the normal start time on the first day of the reported illness. On subsequent days, the replacement shall be required to attend the Affected Property at the normal start time and shall only stop attending the day the normal operative returns.

### Planned resource levels are to include provision for holiday and sickness cover. Any and all events of lack of minimum resource / site attendance are to be logged by the Contractor / Client with corresponding reduction in monthly charge to the Client.

## MAINTAINING ENVIRONMENTAL CONDITIONS

### The Contractor shall be fully aware of the specific environmental conditions required in each of the Client’s gallery and storage spaces and how the installed plant and equipment is to be used to achieve this.

### The Contractor shall pay particular regard to this requirement when planning PPM works / shut downs and shall liaise with the Service Manager to ensure such temporary arrangements, services or equipment are allowed to maintain required environmental conditions.

### The Contractor shall monitor conditions via the BMS and their own local monitoring as required and advise the Service Manager of any concerns in maintaining the required conditions.

### Any deviance from the required conditions shall be logged by the Contractor and reported in the monthly Contractor report with cause, rectification carried out and any further recommendations by the Contractor to avoid re-occurrence.

### For critical Collection areas, reporting of alarm status to Client staff must be undertaken immediately in the event notification (e.g. BMS and Aquarium alarm) during core hours. A follow up report stating reasons for each digression to be produced within 1 week.

### The Contractor’s performance in maintaining required conditions will be assessed as a KPI.

## EXCLUSIONS

### For the avoidance of doubt the following are excluded from the Scope;

- Loss of power from Utility Supplier (other than works associated with agreed disaster recovery works).

- Costs in excess of the Comprehensive Threshold of £200 in each case for Reactive Maintenance tasks including repairs and replacement parts.

- Minor Works (instructed via Reactive Works Orders)

## EQUIPMENT AND TOOLS

### The Contractor is to provide all plant, equipment, and tools to enable full and complete delivery of the Service.

### This includes the provision of uniforms, personal protective equipment, scaffold towers and mobile access equipment, where required, unless otherwise specified. Equipment and tools provided are in every respect to be suitable for the activity being delivered.

### The Contractor is to use all equipment and tools for the delivery of the Service in accordance with the manufacturers’ instructions and guidance and only for their intended purpose.

### All equipment and tools used are to be checked for compatibility with the fabric and finishes of the Affected Property.

### The Contractor is to ensure all equipment and tools used in the delivery of the Service do not present safety hazard to persons operating such equipment or to other building users. The use of all powered or automatically operated tools or equipment is permitted only after agreement has been reached with the Client Health and Safety Advisor and suitable precautions taken by the Contractor.

### All tools used for measurement are to have a valid calibration certificate, all electrical devices are to be suitably PAT tested and possess valid certification which shall be clearly displayed on the equipment.

### Any equipment requiring testing is to have a valid test or inspection certificate which shall be clearly displayed on the equipment.

### The Contractor is to ensure safe and secure storage of all plant and equipment, no claims for loss or damage relating to equipment will be considered in this regard.

### The Contractor shall arrange regular “Tool Box Talks” in the safe operation and use of the tools and equipment utilised in the delivery of the Service.

### The Contractor shall provide a register of all such equipment with certification, re-testing, and replacement dates for review by the Client.

## SPARES AND CONSUMABLES

### The Contractor shall keep a comprehensive stock of critical and high usage spares on site at the Affected Property.

### These spares shall be kept in a secure location.

### There is little on-site storage available, other than for lamps and critical spares, critical spares can be stored in plantrooms associated with the spares but this must be done in a manner compliant with H&S guidance.

### Spares which may be required in the event of failures of plant as a contingency measure; such items may include portable humidifiers / de-humidifiers, heaters, cooling units etc. but which may not be available on site. The Contractor shall put in place a procedure with contact details for local hire or procurement of such specific items (and keep this up to date quarterly).

### During mobilisation, the Contractor shall review the stock of spares held at the Affected Property and make a proposal for ongoing maintenance of the stock of spares as part of the Contractor’s Plan.

### The Contractor shall provide all consumable items required to deliver the Service. All consumables should meet with relevant standards. The Contractor shall keep the stock up to date. The Client reserves the right to request alternate comparable consumables and no additional cost to the Client.

### The Contractor shall provide, as part of a monthly report, a full breakdown of all consumables utilised in the delivery of the Service during the reporting period.

### The Contractor is to provide all consumable items required to satisfactorily deliver the Service, including but not limited to;

- Lubricating oils and greases

- Sealants

- Jointing compounds and materials

- Gaskets, seals and washers

- Valve packing

- Humidifier bottles

- Nuts, bolts, screws and plugs

- Cable, conduit and trunking

- Pipe brackets and supports

- Corrosion inhibitors, scale inhibitors and antifreeze chemicals

- Replacement air filters (air handling units) including bag filters

- Disposable test equipment

- All paints for general repainting of plant, anti-corrosion and colour coding

- Cleansing, degreasing and anti-corrosion fluids and materials

- Descaling acids and neutralisers

- Distilled water

- Dip slides

- Rags

- Replacement lamps (internal and external)

- Replacement indicator panel lamps

- Pump/fan belts

- Fuses and wires

- Miniature circuit breakers

- Cable clips, connectors and grommets

- General purpose mastics.

- Salt

- Grease trap enzyme chemicals

## WATER TREATMENT

### The Contractor is to undertake all water services management and testing on behalf of the Client to manage all hygiene risks associated with water-based systems within the Affected Property, including legionella, E-coli and other water-borne bacteria.

### The Contractor shall analyse and dose (as required) all of the closed heating and chilled water circulation systems installed in the Affected Property.

### The Contractor is to provide the Service Manager with written reports on the type of water treatment used and dosing quantities added to the various systems. These reports shall be issued to the Service Manager on an annual basis.

### The Contractor shall provide dosing agents in accordance with a schedule agreed with the Client as part of the Contractor’s Plan.

### In so far as the law does not permit the Client to allocate, devolve, or transfer any task, responsibility, or role, the Contractor is to identify in writing to the Service Manager the required task, responsibility or role and supports them to meet their associated obligations.

### All compliance tasks and roles relating to water-based systems carried out under this Scope shall meet the standards and requirements of HSE’s Approved Code of Practice, Legionnaire’s Disease: the control of legionella bacteria in water systems (ACOP L8), Edition 4, 2013 revision, and any later revisions, together with the HSG274 part 2, BS6700:2006 and the Water Supply (Water Fittings) Regulations 1999. The contractor undertaking this work shall be a member of the legionella control association.

### The Contractor is to manage all hygiene risks associated with water-based systems on the Premises in accordance with SFG20, any statutory obligations and specific requirements of this Scope.

### The assets concerned set out in the Asset Register this shall include but not be limited to; the Client’s Water Storage and Boosting plant, and all associated monitoring and dosing equipment.

### The Contractor is to implement a management and testing programme including but not limited to;

- Identifying and evaluating all potential sources of risk with respect to legionella bacteria

- Making recommendations of the particular means by which exposure to legionella bacteria is to be prevented or, where prevention is not reasonably practicable, controlled

- Setting out the boundaries of demarcation of responsibility for the water-based systems and the control of any associated exposure to legionella between any tenants/occupiers and the Client

- Providing and maintaining a set of up-to-date system schematics in line with the requirements of ACOP L8.

- Providing water testing and laboratory analysis services for water-based systems.

- Preparing and implementing a control written scheme as described in the Code of Practice and in particular with section 53 including the items listed in paragraphs (a) to (e).

- Establish an inspecting and monitoring regime and maintain records of the assessments, inspections, tests and procedures described in the following sections of this Term Brief in a format which meets the requirements of the Control of Substances Hazardous to Health Regulations 1999 and the Health and Safety at Work Act and is in accordance with the recommendations contained within the Approved Code of Practice 'The Prevention or Control of Legionella (Including Legionnaires' Disease) published by the Health & Safety Commission and local water by laws.

### The management and testing programme shall be included within the Contractor’s Plan.

### Prior to undertaking any works, the Contractor shall provide all necessary risk assessments, method statements, proposed techniques, and detailed operatives experience. Establish safe systems of work, including compliance with Permit to Work procedures.

### The Contractor shall follow and implement all the relevant provisions of the ‘Approved Code of Practice - Legionnaires’ disease - The control of legionella bacteria in water systems’ published by the Health and Safety Executive and approved by the Health and Safety Commission.

### All records associated with the maintenance and testing of the Client’s cooling towers shall be provided on a monthly basis to the Service Manager.

## WATER TEMPERATURES

### The Contractor shall carry out the following procedures and measurements;

### On a monthly frequency measure and record the temperatures in the DHWS calorifiers and adjust as found necessary to maintain a flow temperature of water of 60 C. and a return temperature of at least 50 C.

### On a monthly frequency measure and record the temperature at the sentinel outlets and at not less than 10% of the DHWS outlets in the Affected Property.

### Plan the selection of outlets in a manner which will ensure that they are all used for sampling at least once in each ten-month period and on each occasion, include the sentinel outlets i.e. nearest to and furthest from the DHWS plant.

### Report to the Client immediately any circumstances in which the measured temperatures are less than 50 C within a minute of running water.

### On a monthly frequency measure and record the temperatures in any water storage tank.

### Report to the Service Manager immediately any circumstances in which the cold water measured temperatures exceed 20 C within two minutes of running water.

### On a six-monthly frequency measure and record the temperature of the incoming water supply to the Affected Property.

### Report to the Service Manager immediately any circumstances in which the measured temperatures exceed 20 C.

### All dead legs shall be identified and purged on a monthly basis.

## SHOWER HEADS AND SPRAY TAPS

### In month one of the Contract and at three monthly intervals thereafter clean and chlorinate all shower heads and spray taps.

### The Contractor shall carry out regular testing of TMVs to ensure they are delivering safe water temperatures between 39C and 43C

## ANNUAL CHECK

### Whether or not it is a requirement of the agreed written scheme carry out the procedures described in Section 182 of the Approved Code of Practice and note that these include the cleaning and sterilisation of all of the water storage tanks together with all hot and cold water down services pipework and fittings in the Affected Property and the internal inspection, and if necessary, the cleaning of the direct gas fired water heaters.

## WATER SAMPLING

### Whether or not it is a requirement of the agreed written scheme carry out the microbiological testing on a quarterly basis as described in Sections 183 to 189 of the Approved Code of Practice.

### The Client shall also undertake an independent annual audit of the Affected Property water services and shall liaise with the Contractor regarding any recommendations made therein.

## FILTERS

### Main air handling panel pre-filters are to be changed every 4 weeks with the main bag filters changed every 3 weeks or as required by the filter manometer gauges.

## GAS FIRED BOILERS

### Clean burners, flues and flue-ways, check for obstruction. Re-commission burners in accordance with manufacturer’s instructions, record flue gas readings and retain in site log books.

### Wire brush, treat and paint any corroded surfaces.

### Check all valves, safety valves and controls for correct operation and emergency use.

### Check all water connections for leaks.

### Ensure all boiler plant rooms are maintained free of debris to reduce dirt infiltration in to boiler burners and flue ways.

### Ensure all condensing boiler drains are free running and free from debris and corrosion.

### All works undertaken to the boilers are to be undertaken by fully qualified CORGI registered engineers.

## HUMIDIFIERS

### All fixed units shall be serviced every 3 months.

### All portable units shall be serviced every 4 months.

### The humidifier, both steam injection an evaporation, both fixed and portable types are to be cleaned and serviced strictly in accordance with the manufacturers instructions, with the water bottles being replaced before component failure.

### All scale and slime shall be removed to prevent component failure from bacteria.

### The condensate tray is to be cleared of any debris and sterilised plus the drain is to be checked and free running.

### Any corroded metal sections are to be wire brushed, treated and painted.

### Where the units are supplied with treated water the water treatment and monitoring is to be undertaken by a competent person.

### The fixed humidifier units and system at the Study Collection Centre is to be checked during the scheduled site attendance. In addition the evaporative drum humidifiers and the distribution pipework is to be thoroughly cleaned, chlorinated and treated with biocide. These works are to be carried out at least annually by a specialist contractor.

## PERIODIC FIXED WIRE TESTING

### The Contractor shall be responsible for planning and undertaking scheduled periodic testing of the entire fixed wiring installations across the Affected Property.

### Testing to be in accordance with BS 7671:2008 Requirements for Electrical Installations 17th Edition and as indicated under SFG20 across all of the Affected Property. The electrical services for the aquarium must be tested annually, a plan shall be put in place by the Contractor to ensure no critical aquarium systems are affected during the works. This plan shall be agreed by the Service Manager before any works progress.

### The planned works shall be undertaken so as not to disrupt the day to day operations of the Client, these being undertaken out of hours where required. Any potential disruption to day to day services shall be advised at least 1 month prior to the planned date and agreed with the Service Manager in advance.

### The Contractor shall plan the fixed wiring testing to be scheduled on a basis of completing 20% per year so that the entire installations are tested over a 5-year period.

### In addition, the Contractor will carry out annual thermal imagery testing of main intake low voltage switch boards and agreed (20%) local power and lighting distribution boards.

### Any remedial works identified as a result of testing are to be brought to the Service Manager at the earliest opportunity and included in the Contractor’s monthly reporting.

## PORTABLE APPLIANCE TESTING

### The Contractor shall undertake regular Portable Appliance Testing (PAT) at a maximum interval of 24 months. These shall be more frequent if directed by the Service Manager for higher risk items.

### PAT of 3rd party catering equipment under the control of others will not be in scope and will be the responsibility of those operating that equipment areas.

### Planning and records of the testing shall be recorded on the Contractor’s record management system. This shall include renewal dates.

### Testing and certification shall be carried out by a competent person.

### All tested equipment shall be labelled with relevant information.

### Any remedial works identified as a result of testing are to be brought to the Service Manager at the earliest opportunity and included in the Contractor’s monthly reporting. All equipment that is unsafe shall be taken out of operation until made safe.

### All equipment brought on to the Affected Property by the Contractor shall be accompanied by PAT test records and records made available to the Client.

## OUT OF HOURS WORKING

### The planned works shall be undertaken so as not to disrupt the day to day operations of the Client, these being undertaken out of hours where required. Any potential disruption to day to day services shall be advised at least 1 month prior to the planned date and agreed with the Service Manager in advance.

### The Contractor is to ensure that there is a facility for out of hours call out for Sub-Contractors that service and maintain specialist pieces of equipment. The Contractor must be aware of call out rates for sub-contractors and agree these as part of the procurement process.

### For all out of hours call-outs the maximum time for attendance is 4 hours.

### The Contractor is to create layout sheets of key plant areas with key plant and equipment highlighted for use by out of hour’s team when responding to emergencies to assist in meeting the following priority levels

## KEY PERFORMANCE INDICATORS

### Appendix F details the Contract SLAs and KPIs. This is an outline of expected performance indicators which, when the Contract is awarded, shall be agreed and formalised between the Client and the Contractor.

### The agreed SLA’s and KPI’s shall be presented to the Client as part of the monthly contract review process.

### Performance against these SLAs and KPIs, as certified by the Client on a monthly basis, will have a direct effect upon the monthly payments payable to the Contractor as described in the Contract Data.

### Additional SLAs and KPIs may also be agreed between the Contractor and the Client to monitor performance of the Contractor and sub-contractors, and these can be agreed at any time during the life of the contract, but are expected to be finalised initially during Mobilisation.

### KPI Categories

- General: A single measure shall apply to the Affected Property

- Site Specific: Shall be reported individually against each property

### In the case of site specific Service Levels / KPI’s each of the 5 zones will be scored independently, with any failure to achieve the penalty threshold for any one zone being taken as a failure for that Service Level / KPI.

### Rectification of SLA/KPI failure

#### If at any time the Scope is not delivered in accordance with the Service Levels and other components of the Scope, the Contractor shall at the Client’s option and without prejudice to the Client’s other rights and remedies:

- Arrange all additional resources necessary to perform the Scope in accordance with the Service Levels as soon as possible and at no additional charge to the Client; and

- Promptly remedy any default or re-perform any non-conforming Scope elements at the request of the Client at no additional charge.

- The Client may by written notice to the Contractor require the Contractor to remedy the deficiency as soon as reasonably practicable in the light of the nature of the Scope and the type of deficiency.

- If any deficiency has not been remedied to the Client’s reasonable satisfaction within a reasonable period, the Client may notify the Contractor of such a failure and the Client and Contractor shall meet as soon as practicable after such notification (a “Rectification Meeting”).

- At the Rectification Meeting, the parties shall attempt to agree on the cause of the deficiency, one or more ways in which the deficiency could be remedied, and a timetable within which this will be done. The parties will also agree a suitable date for a follow up meeting to discuss the Contractor’s progress or otherwise in remedying the deficiency.

- If the Contractor fails to meet the required Performance Standard / KPI in any one month the Client can reasonably determine that a deduction be made.

- If at the follow up meeting the Client decides that the Contractor has not successfully remedied the deficiency then the Client may elect to:

- require the Contractor and the Client to meet again to discuss the deficiency or ;

- reimburse the Client for all associated costs for a 3rd party to complete the works.

### KPI Performance Deductions

The Contractor shall use the original KPIs tracker (excel format) as provided with the Invitation to Tender for their monthly KPIs reporting.

Each of the Service Levels / KPI’s (Performance Standards) set out in Appendix F will be marked on a “Pass / Fail” basis with the associated weighted score being achieved or rejected.

The Profit element of the Price as set out in the Price List, Contractor Profit shall be adjusted to give the actual profit due to the Contractor in any month as 1/12th of the Annual profit.

Performance Score shall be determined by the pass/fail of each KPI against scoring lower than the Penalty Threshold. The Performance Score shall be the total accumulated score of all KPIs expressed as a single % score.

Payment to the Contractor shall be reduced by an amount equal to the deduction stated here against the profit element of the Price List;

| Actual Performance Score | % deduction |
| --- | --- |
| 95% – 100% | Nil |
| 85% – 94% | 10% |
| 75% – 84% | 25% |
| 65% – 74% | 50% |
| 0% – 64% | 100% |

Worked Example

If there are a total of 20 KPIs and in that month 5 score lower than the Penalty Threshold the Contractor shall score 75% in that month:

15 Passes (75% of total score) and 5 fails (25% of total score) = 75% Performance Score

The % deduction against the profit for the stated month shall be 25% (see table)

If Core Profit for the stated month is £1000 then the payment to the Contractor shall be reduced by £250.

## METHOD STATEMENTS

### Detailed method statements are to be issued by the Contractor to the Client prior to the start of the Service as part of the Contractor’s Plan.

### The Contractor shall be responsible for the production and maintenance of the detailed method statements during the Service, which are to be updated periodically to reflect progress of the works, changes to the PPM programme or methodology and Client comments.

## APPRENTICES

### The Contractor is to take all reasonable steps to employ apprentices and to report to the Client the numbers of apprentices employed and the wider skills training provided.

## WORKS REQUESTS

### 14.36.1.  The Contractor shall implement their own process for logging all Client works requests received by telephone, email or other agreed means.

### This process to be fully detailed in the Contractor’s Plan, tested and demonstrated to the Client. The process shall be agreed by the Client and operational for the start of the contract.

### Works requests of any nature are to be acknowledged by the Contractor in line with the priority schedule below

### Each works request is to be allocated a unique reference and the Contractor is to keep the originator of the service request abreast of actions taken and timescales for resolution of the maintenance activity. Logging is to be undertaken by a process owned and managed by the Contractor according to local arrangements set out below.

## WORKS PRIORITISATION

### The Client requires the Contractor to operate under a formal service request system as above. The response and fix times for incidents managed through the service request system are as follows for core hours:

### For all out of hours High Priority events the Contractor shall attend within 2 hours.

### The Client will set the priority level of service requirements, these shall only be revised by agreement with the Contractor.

### The Contractor is to keeps records of all incoming service requirements, the priority level allocated and the response time achieved. These records are to be made available to the Client as part of the monthly management reporting.

## DUCTWORK

### The Contractor will include the planning of and inspection of the Client’s ductwork and Air Conditioning systems as indicated in CIBSE TM44 and SFG20.

### Any and all ductwork cleaning will be planned and carried out by the Contractor as part of the Service. All cleaning shall be agreed with the Service Manager.

### Planning and records shall be illustrated and recorded on the Contractor’s record management system.

### Any remedial works identified as a result of testing are to be brought to the attention of the Service Manager at the earliest opportunity and included in the monthly reporting to the Client.

### The Contractor shall be required to undertake Fire damper testing of the Affected Property as a minimum annually. The Contractor shall produce a fire damper register, containing accurate locations, and keep it up to date at all times. The Contractor shall undertake a full documented cause and effect test on the inter links with the fire alarm system as part of the alarm service.