## GENERAL
Hollymount Primary School & Malmesbury Primary School, LB of Merton
Fire Door Package
Contractor Pricing Document
Note: Contractor to note that the Schedule of Works, drawings and appendices take precedence over the descriptions provided in this document and as such these should be priced. This document has been provided in editable format to make it easier for the contractor to insert their costs.
Ref Nr | Item/Description | Item/PC | Cost (£)
Section 1 | Preliminaries
Section 2 | Schedule of Works |  | (price within breakdown below)
A
1 | GENERAL
A | Works relate to the fire door improvement package of works to be undertaken over the summer holidays 2025 at Hollymount Primary School and Malmesbury Primary School, on behalf of the London Borough of Merton. Works will largely involve the replacement of existing doors deemed to not be sufficient in providing compartmentation as per the appended door schedule, in addition to overhaul of existing fire doors to be retained and isolated other remedials, such as replacement of non fire rated glazed screens, such as with fire rated MF partition or fire rated glazing.
Note: Where Named Sub-Contractors have been included, the Main Contractor is to allow for appointing them, referring back to their appended quotes, in addition to managing them throughout the process, attendance and OHP. This will include all engagement, formalising appointment, liaising with them throughout the process and through to completion of works.
Works will largely involve a small number of different trades. It is assumed that Main Contractors pricing these works will have their own internal specialist trades to undertake the door installations and remedials.
Works largely involve replacement of specific fire doors where identified to not be providing sufficient compartmentation following survey by others on behalf of the school and recent review by McBains, as per the Door Schedules and drawing appended. In addition the Contractor will be required to overhaul existing fire doors to ensure correct operation such as ease and adjusting to ensure correct operation/close within the lining, replacement of damaged overhead closers, joinery repairs, replacement of non-fire rated vision panels with fire rated. There are also non fire rated glazed screens to be renewed with either fire rated MF partition or fire rated glazing, in addition to replacement of serving shutter to the Kitchen with a fire rated unit connected back to the fire alarm.
Named Sub-Contractor quotes have been appended to the tender pack in relation to specialist portions of work for the Main Contractor to appoint largely Fire Alarm Contractor.
The Contractor is to note that works are expected to commence by the 11th August 2025 and complete no later than the 5th September 2025. Works post the 2nd September will need to be competed by the Contractor outside of normal working hours (post 3.30pm/Weekends) following term commencing on the 3rd September. As there will be holiday clubs present over the summer break all employees inc regular visitors to site must hold valid enhanced DBS Certificates, with proof being provided with tender submission. Failure to provide will result in tender returns being voided. Should these timescales not be possible Contractor should price for completing either/or outside normal working hours and/or October half term (27/10 - 31/10).
If this is not possible the Contractor is to provide an alternative achieve programme with their tender return clearly stating the programme length and any long lead-in items which may impact on this being achieved. Likewise if the Contractor believes they are able to complete within a quicker timeframe they should confirm this on the Tender Form and covering letter.
Contractor to allow for developing a sufficient Construction Phase Plan in order for the works to be executed in a safe and professional manner. The Contractor will need to allow for making safe the working areas and compound through use of herras fencing and barriers. Contractor to allow for liaising closely with the site managers of each site on a daily basis. Given scope of works it is assumed that either a floating site supervisor or working foreman will be employed.
The Contractor will need to allow for acting as Principal Contractor under the CDM Regulations 2015 and must allow for this within their pricing. Given timescales for the project it is anticipated that works will NOT be notifiable to the HSE. The Contractor will also need to allow for taking on the PD role under the Building Safety Act post contract award, taking on board the schedule provided by the PD prior to tender issue and providing all information to the Building Control Officer to allow issue of their sign off Certificate. There will be other smaller Contractors on-site undertaking external repair and isolated internal works at the same time. Contractor to allow for liaising with them on a regular basis to ensure risk is mitigated. It is paramount that the Contractor allows for developing a sufficient Construction Phase Plan for the works to be executed in a safe and professional manner.
Services
B | The Contractor will be provided access to the sites water and electrical supply. Meter readings will be taken on the day of works commencing and on completion of works. Although energy will be FoC to the Contractor they will be responsible for utilising efficiently. | Item
Protection
C | All site personnel to wear appropriate PPE and the Contractor is to make an allowance for site protection / access restriction as identified by site RAMS. | Item
D | Waste Materials
| Remove all rubbish and debris from the site from time to time as it accumulates and at the completion of the contract. Leave the site neat and tidy to the satisfaction of the Contract Administrator. A skip may be placed on site in addition to a compound area, in a location to be agreed with the Contract Administrator. | Item
Cleaning
E | The Contractor is expected to leave works areas particularly external areas clean and tidy upon completion of each day’s work. Contactor to lay protection to working areas and where doors are transported across. Providing partial cover over flooring will NOT be acceptable. The Contractor is deemed to have included projection within costs. | Item
Parking/ Storage
F | The Contractor will be provided with the area highlighted on the appended logistics plan, although this may reduce once he school staff arrive on-site towards the end of August. No parking will be allowed on site from the 1st September during normal working hours. The surrounding roads to each site are a mixture of restricted (Hollymount) and unrestricted (Malmesbury). No parking costs incurred on these roads will be reimbursed to contractors or subcontractors. The Contractor must not block vehicles movements or fire escapes at any time and must move their vehicles as necessary upon any reasonable request from the Client, other contractors or maintenance teams working on site. | Item
Access
G | The sites are located in residential areas of Wimbledon and Morden in South London, with major roads and public transport network within close vicinity. The Contractor is to undertake a full photographic record at both sites of the site access, delivery and communal areas, including the route to the work site and submit to the Contract Administrator prior to commencement. | Item
Contractor to allow for developing a sufficient Construction Phase Plan in order for the works to be executed in a safe and professional manner. The Contractor will need to allow for making safe the site from the adjacent school site through use of herras fencing. Contractor to allow for liaising closely with the site manager of the adjacent school site during the school term.
The Contractor will be responsible for developing the Construction Phase Plan following appointment to detail how they will safely execute the works and manage the site.
Note: As such it is paramount that the Contractor ensures the access into the site is not obstructed at any time during the course of the works.
Note: The end-user will NOT be expected to take deliveries on behalf of the Contractor.
Handover Documents
H | The Contractor must collate all required Handover Documentation as the work proceeds, submitting to the Contract Administrator all information requested by McBains by the completion date to enable Practical Completion to be issued. | Item
| Working Hours | Item
I | As previously detailed, given the Client’s requirements for works to be completed by the 5th September and school term commencing on the 3rd September, the Contractor must allow for OOH working from the 3rd September.
Normal working hours are expected to be Monday to Friday 7.30am – 6.00pm. It is expected that the Contractor will be given keys to access the working areas/site and as such will be responsible for locking up at the end of each working day.
With regards to noisy works the Contractor will need to undertake within normal working hours Monday to Friday to ensure no disruption to adjoining properties at weekends.
Welfare Facilities
J | The Contractor will be responsible for determining the best method of providing welfare facilities at tender stage for development if appointed. Note. A condition survey of the working areas will be undertaken prior to commencement by the CA for agreement by the Main Contractor, which will be reviewed on completion. Should any damage be identified the Main Contractor will be responsible for rectifying back to the condition prior to works commencing. | Item
Note: The Contractor is expected to develop the site logistics plan at tender return stage. This is to ensure that a practical and acceptable approach is provided.
The Contractor will be able to make use of existing services on site but will however be responsible for making all connections and ensuring these have been carried out safely (no trip hazards etc).
Health and Safety
K | It is considered that due to the nature of the works and anticipated contract period these works will NOT be notifiable under the CDM Regulations 2015. As such the Contractor is to allow for providing all necessary information for the compilation of the Health and Safety Folder, in addition to providing a Construction Health and Safety Plan to the satisfaction of the Principal Designer prior to works starting on site. The Contractor is to review any existing building plans/health & safety documentation prior to starting the works. Asbestos information has been appended to the tender documents. A Pre-Construction Information Document will be issued to all tendering Contractors during the tender period. | Item
During the Construction phase and as works progress, the Contractor is expected to act as Principal Contractor and supply all required method statements/obtain from sub-contractors where applicable, to the satisfaction of the Principal Designer, including collation of information from the named underpinning sub-contractor. The Principal Contractor will be responsible for amending their Construction Phase Plan if required during the progress of works and the collation and submission of Health & Safety File on completion of the works to the satisfaction of the Principal Designer. The Principal Designer will be responsible for issuing all F10 notices to the HSE and distributing to all relevant parties.
The Contractor will also be responsible for closing out the requirements under the Building Safety Act although this is envisaged to be limited following sign off from our internal BSA PD at prior to tender stage. Contractor will need to allow for closely liaising with the BCO in order to satisfy requirements.
Security
L | The Contractor shall ensure that the building is left secure at all times. Should there be any security issues during the scheme the Contractor should notify the Client. | Item
The Contractor will be responsible for ensuring the site/compound is secure throughout the duration of the works, including buildings where welfare/storage is provided and will be responsible for any loss of materials from site. As such it is advised that materials/items of value be brought to site on day of install etc.
Note: The Client will not be responsible for any loss or damage caused where utilising existing buildings for these purposes.
Preliminaries
M | Allow here for all contractors’ preliminary costs for undertaking these works. Please append a breakdown to reflect breakdown in terms of site management, contracts management, H&S supervision, welfare, IT, allowance for consumables etc. | Item
Qualifications
N | Main Contractors must be able to demonstrate experience of installing fire doors within the education sector, in addition to their registration to a relevant fire door accreditation schemes, where such schemes are available such as CERTIFIRE, BRE Certification, BWF and BM TRADA, as an installer and provide conformity certificate on completion. | Item
2 | STRIP OUT
i | Prior to works commencing the Contractor is to allow for isolating all services to the working areas to minimise hazards. | Item
ii | Following suitable access being provided, Contractor is to allow for stripping and disposing of all existing doorsets as per the appended door schedule and drawings, allowing to appropriately dispose of doorsets. | Item
iii | Contractor to allow for carefully stripping out existing doorsets ensuring no damage to adjoining surfaces is caused. | Item
iv | A copy of the Asbestos Register has been included within the tender pack. It not believed that any asbestos will be present behind door linings however for the avoidance of doubt, should sampling and any subsequent asbestos removal be required, the CA will instruct utilising PC SUM. Contractor to allow for the following Provisional Sum as part of their submission. | PC SUM | 3000
3 | NEW FIRE DOORS
A | New Fire Doors
NOTE: All new doorsets are shown in red on the appended proposals and detailed within the Door Schedule per room
i | As directed by the appended Door Schedule and proposed drawings, Contractor to supply and install new FD30s rated timber doorsets (double doors) finished in to match existing doorsets such as Corridor and Canteen as per the Fire Engineers comments. The doorsets will incorporate fire rated impact resistant vision panels as shown in the appended drawing. Internal door set to match the existing corridor doors in terms of red finish, complete with linings, architrave and stops. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. | Item
Include for routing out and installation of smoke seals and intumescent strips to new doors inc thresholds, linings and fire rated vision panels. Doors made to measure to suit existing and new structural openings. Allow for adjustment to suit existing openings. Doors to be self-closing and to achieve ½ hour fire resistance in accordance with Building Regulations.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Supply and install overhead door closers in polished chrome to new doors inc chrome plate fire door signage as depicted on the proposed plans.
Note: All new barrel locks are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
ii | As directed by the Door Schedule and appended proposed drawings, Contractor to supply and install new sets of FD30s rated timber internal door sets finished in red to match the existing to the rooms coming off corridors as shown on the Door Schedule, complete with linings, architrave and stops, complete with fire rated glazed viewing panels as requested on the 'Door Schedule', to provide means of separation between areas. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. | Item
Include for routing out and installation of smoke seals and intumescent strips to new doors inc thresholds, linings and fire rated vision panels. Doors made to measure to suit existing and new structural openings. Allow for cutting down of doors and adjustment to suit existing openings. Doors to be self-closing and to achieve ½ hour fire resistance in accordance with Building Regulations. Allow for providing polished chrome handles to accept new Laidlaw 6 pin euro cylinder locks.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Supply and install overhead door closers in polished chrome to new doors inc chrome plate fire door signage as depicted on the proposed plans. Polished chrome lever on rose door handles to be provided to match the existing. Where provided to Classrooms thumb turn locks (50mm screw on-rose) finished in polished chrome are to be provided to allow doors to be locked from the inside, inclusive of means to open from the outside.
Note: All new barrel locks are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
D | New Non-Fire Rated Doors
i | As directed by the appended proposed drawings, Contractor to supply and install new non-fire rated timber internal door sets finished in red to match the existing, complete with linings, architrave and stops, as requested on the 'Door Schedule'. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. Contractor to allow for vision panels where required to be impact resistant glass. | Item
Doors made to measure to suit existing and new structural openings. Allow for cutting down of doors and adjustment to suit existing openings. Allow for providing brushed steel handles to accept new Laidlaw 6 pin euro cylinder locks.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Polished chrome lever on rose door handles to be provided to match the existing.
Note: All new barrel locks are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
ii | As directed by the appended proposed drawings, Contractor to supply and install new sets of non-fire rated timber internal door sets finished in red to match the existing, complete with linings, architrave and stops, as requested on the 'Door Schedule'. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. Contractor to allow for vision panels where required to be impact resistant glass. | Item
Doors made to measure to suit existing and new structural openings. Allow for cutting down of doors and adjustment to suit existing openings. Allow for providing brushed steel handles to accept new Laidlaw 6 pin euro cylinder locks.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Polished chrome lever on rose door handles to be provided to match the existing.
Note: All new barrel locks are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
E | Existing Internal Doors
i | Where existing FD30S doors to the corridor are to be removed and retained, Contractor is to install within new space following construction of fire rated bulkhead, as identified on the floor plans. Contractor to allow for installing within new door frames to be constructed and architraves following, allowing to shave down doors in a way that will not invalidate warranty, hang and ensure in full working order. | Item
ii | To all existing doors to be retained to the working areas the Contractor is to allow for overhauling doors to ensure correctly operate/close and lock with ease. | Item
iii | Replacement of Overhead Closers with Concealed Perco's
a | Contractor will be required to remove all existing overhead closers to internal doors and renew with new perco's where determined self-closing requirement is needed in order to remove the ligature hazard. Where deemed not required, Contractor will be required to remove and make good notching. Contractor will be required to make good to redundant notches/where fixings were present and redecorate doors in full on completion to match existing finish. Contractor to price for the following; | Item
b | Removal of existing overhead closers, making good to notching and supply/install of new Genuine Perko R2 Door Closer - Square Plate - Satin Chrome, assume 2.nr per door required. Contractor to allow for making good around new fixing points following install and ensuring working correctly and with ease on completion. For pricing purposes allow to supply and install 10.nr doors (20.nr units) to be firmed up on-site with the CA. | PROV QUANT
c | To designated fire doors, allow for removal of existing overhead closers, making good to notching and supply/install of new Astra 3003 Series Concealed Fire Door Closers, assume 2.nr per door required. Contractor to allow for making good around new fixing points following install and ensuring working correctly and with ease on completion. For pricing purposes allow to supply and install 10.nr doors (20.nr units) to be firmed up on-site with the CA. | PROV QUANT
d | To doors where it is deemed auto closers are not required, Contractor required to remove and dispose of existing, prior to filling notching with two part wood filler, rubbing down to ensure a flush surface is provided and redecorating lining/architrave in full on completion to ensure a uniform finish is provided. For pricing purposes allow to supply and install 10.nr to be firmed up on-site with the CA. | PROV QUANT
iv | Where replacement of parts is required such as ironmongery Contractor to allow Provisional Sum of £1,000 to be expended by the CA to cover such repairs. | PROV SUM | 1000
v | To isolated rooms where shown on the proposed plans, the Contractor is to allow for changing the opening of selected doors from current opening onto corridors to within the Classrooms where this is a clash with fire escape doors etc. Contractor to allow for removing doors, door stops, before re-hanging doors, making good previous notches to lining to ensure flush surface is provided and redecorate linings in full on completion, ensuring doors operate smoothly on completion. For pricing purposes Contractor to allow for changing the swing/opening to 8.nr single door leaf's. | PROV QUANT
vi | Contractor to allow Provisional Sum of £2,500.00 in relation to any further repairs required to the existing doors outside of those listed above. | PROV SUM | 2500
vii | Contractor to allow the Provisional Sum of £5,000 in relation to any potential viewing panel replacement to fire doors to be expended by the CA. | PROV SUM | 5000
viii | To viewing panels where it is determined that anti-shatter safety film is inadequate or not currently provided, the Contractor will be required to renew with new anti-shatter film compliant with BS EN 12600, allowing to cover either side of glass panes. Contractor to price the following sizes and quants; | Item
a | 10.nr doors 450x450mm vision panels allowing for either side (20.nr sheets) | PROV QUANT
b | 10.nr doors with 6.nr 250x250mm vision panels allowing for either side (120.nr sheets) | PROV QUANT
F | Storage
i | To existing cupboards being retained, the Contractor will be required to remove existing locks and providing new t bar locks to ensure they are suited on the same keys/for ease of operation. For pricing purposes Contractor to price for installing 50.nr to be agreed by the CA. | PROV SUM
ii | Where new sink units are shown to the classrooms in red to the Ground Floor, 4.nr in total, the Contractor will be required to supply and install new Benchmark Art & Design (or equal and approved) SGL 1000mm wide base units and 30mm thick granite effect worktop incorporating lockable doors, stainless steel sink and drainer with waste ready for plumbing connections in white. | Item
G | Existing Cubicles
i | To the existing Ground Floor washrooms being retained the Contractor is to allow for undertaking a light overhaul in order to ensure that all doors inc locks, sanitaryware etc is in working order ahead of handover. Contractor to allow for easing and adjusting doors, renewing seats and lids where required and ensuring levers operate correctly. | Item
ii | Contractor to allow the Provisional Sum of £2,000 for any repairs/replacement of parts damaged as required to be instructed by the CA. | PROV SUM | 2000
H | New Cubicles and Sanitaryware
a | New KS1 WC's to Canteen
i | In accordance with the appended quote (supply only) provided by Trovex Washrooms (or equal and approved), the Contractor is to allow for the supply and fitout of the new KS1 WC's to the Canteen inclusive of provision of new cubicles, pre-plumbed sanitaryware, services void to rear of units, IPS panelling, vanity units, TMV percussion taps etc. | Item
Doors - Uniform Blue - CU3859 Pilasters - Uniform Blue - CU3859 Partitions - Uniform Blue - CU3859 Fittings - Brushed steel Wall Ducting - Uniform Blue - CU3859 Wall Flash Gaps -Uniform Blue - CU3859 Vanity Top - White Vanity Under Panels - Uniform Blue - CU3859 Vanity Flash Gaps - Uniform Blue - CU3859
Supply and install aforementioned in accordance with manufacturers instruction, including all fixings. Units to be adapted to suit revisions proposed within the sketch detail provided.
Trovex Contact Details
Rhain Brown - Rhain.Brown@trovex.com - 07384 801 770
ii | Contractor to allow for undertaking all BWIC with the washroom installation such as building out void to back of pans/cisterns, chasings, routing out units, adapting existing walls, ceilings etc, in addition to providing fixings and sealants to surround of all units etc. | Item
b | Sanitaryware to all other Washrooms
i | In accordance with the appended quote (supply only) provided by Trovex Washrooms (or equal and approved), the Contractor is to allow for the supply and fitout of either new washrooms or those being refurbished as listed below. This is inclusive of new pans/cisterns to void, pre-plumbed sanitaryware, services void to rear of units, IPS panelling, sinks, TMV percussion taps etc. | Item
Ground Floor Staff Unisex WC's (not the existing single WC)
Ground Floor Hygiene Rooms x2
First Floor KS3/KS4 Unisex WC's
First Floor Staff Unisex WC's
Supply and install aforementioned in accordance with manufacturers instruction, including all fixings.
Trovex Contact Details
Rhain Brown - Rhain.Brown@trovex.com - 07384 801 770
ii | Contractor to allow for undertaking all BWIC with the washroom installation such as building out void to back of pans/cisterns, chasings, routing out units, adapting existing walls, ceilings etc, in addition to providing fixings and sealants to surround of all units etc. | Item
I | Classroom Sinks
i | To the 5.nr Classrooms being provided to the Ground Floor where new sink units are shown in green, the Contractor will be required to supply and install new Benchmark Art & Design (or equal and approved) SGL 1000mm wide base units and 30mm thick granite effect worktop incorporating lockable doors, stainless steel sink and drainer with waste ready for plumbing connections and localised water heaters (inc in MEP spec) in white. | Item
ii | Contractor to allow PC Sum of £500 for any repairs to existing units being retained. | PC SUM | 500
J | Food Tech Classroom
i | In accordance with the appended quote provided by Innova Design Group Ltd, the Contractor is to allow for their appointment as Named Sub-Contractor, to design, manufacture and install the new Food Tech Classroom to the First Floor, in accordance with their appended design. As part of the works they have allowed for the design, manufacture and fit out of the specialist Classroom. Contractor to allow for their quote, attendance and OHP, ensuring that they appoint them in good time prior to works being required. | Item
ii | Contractor will be expected to undertake BWIC with the works such as penetrations, fixings, support work and sealants on completion. All MEP services to be provided to the room have been itemised within the MEP section for the Contractor to price there. | Item
K | Misc
i | Contractor to allow the Provisional Sum in relation to any unforeseen timber repairs required to be expended by the Contract Administrator. | PROV SUM | 3000
ii | To the new Store being constructed to the First Floor adjacent to new KS3/KS4 WC's, the Contractor is to allow for erecting new shelving to 2.nr walls (left and back walls), circa 2000mm in length to each and 3 rows (6 in total) using primed MDF and 50x47mm treated timber battens to support the new shelves beneath. Contractor to fit at heights of 1000, 1500 and 1800mm above FFL. Contractor to allow for providing mitred joints where the shelves but each other at the wall junction, sufficiently sand down all edges, surfaces etc. | Item
8 | FINISHES
A | Contractor to apply 2.nr mist coats to all new wall (excl WC’s where wall cladding is proposed) surfaces following plastering prior to decorating all (inc all other wall and ceiling surfaces, with 2.Nr finishing coats of Dulux Trade Diamond Matt Emulsion to match the existing finish. | Item
B | Contractor to apply 2.nr mist coats to all new ceiling surfaces following plastering prior to decorating all (inc all other wall and ceiling surfaces, with 2.Nr finishing coats of Dulux Trade Diamond Matt Emulsion to match the existing finish. | Item
C | To isolated areas where decorations are in poor condition to walls, the Contractor will be instructed to redecorate. Contractor to allow for thoroughly preparing, removing all loose paint, prior to providing 2.nr mist coats where bare brick and finishing with 2.Nr finishing coats of Dulux Trade Diamond Matt Emulsion to match existing finish following repairs. For pricing purposes Contractor to allow for redecorating 500m2 of existing wall surfaces, with areas to be agreed on-site with the CA. | PROV QUANT
D | To isolated areas where decorations are in poor condition to ceilings, the Contractor will be instructed to redecorate. Contractor to allow for thoroughly preparing, removing all loose paint, prior to applying 2.nr mist coats to all new ceiling surfaces and 2.Nr finishing coats of Dulux Trade Diamond Matt Emulsion to match existing finish, following repairs. For pricing purposes Contractor to allow for redecorating 250m2 of existing ceiling surfaces, with areas to be agreed on-site with the CA. | PROV QUANT
E | Redecoration of Specific Rooms
i | Contractor to itemise out costs below for redecorating the following rooms in full inc preparation, 2.nr finishing coats to ceilings, walls and joinery, in accordance with previous clauses above; | Item
a | Canteen (Ground Floor) | Item
b | Staff Room (Ground Floor) | Item
c | Sensory Room (Ground Floor) FINISH TBC | Item
d | Main Hall (BACK WALL ONLY) FINISH TBC | Item
e | Home Economics Classroom (First Floor) | Item
f | Office (adjacent to Staff Kitchenette First Floor) | Item
g | Intervention Room (adjacent to Home Economics Classroom First Floor) | Item
F | To all new primed joinery surfaces, Contractor to allow for applying 1.nr undercoat and 2.nr finishing coats of Dulux Trade Diamond Gloss in white. | Item
G | To isolated areas where decorations are in poor condition, Contractor will be required to redecorate existing joinery surfaces. Contactor to thoroughly prepare ensuring all loose paint is removed, prior to applying 2.Nr finishing coats of Dulux Trade Diamond Gloss to match existing finishes, such as skirtings, dado and picture rails etc. For pricing purposes Contractor to allow for redecorating 200lm of existing decorated joinery such as skirtings, architraves etc to match existing finish, with areas to be agreed on-site with the CA. | PROV QUANT
H | Flooring Renewal
i | To all WC's to be refurbished as part of the works (costs to be itemised to areas set out below), the Contractor is to allow for preparing existing concrete floor surface prior to applying new DPM latex to ensure that a level finish free of moisture is provided. Contractor will be required to demonstrate floor surface is free of moisture prior to applying vinyl. Following Contractor to supply and fit new Polysafe Standard PUR sheet vinyl flooring in Dolphin Grey(or equal and approved) including cap and coving in the below chosen finishes. Available from Polyfloor (Tel: 0161 767 1111). Install in accordance with manufacturer instructions and include for adhesive wastage, stainless steel transition and threshold strip bars. Colour to be confirmed. Include for all adhesives and the like and threshold strips as required. Allow for all cutting and waste, for dressing the vinyl up and providing coved skirtings min 100mm above floor level. | Item
GROUND FLOOR
a | Ground Floor Accessible WC | Item
b | New KS1 WC's to Canteen & Hygiene Room | Item
c | New Staff Unisex WC's to Corridor (excl existing single wc) | Item
d | Medical Room | Item
FIRST FLOOR
e | New unisex Staff WC's | Item
f | New Accessible WC | Item
g | New Food Tech Classroom | Item
h | New KS3/KS4 Unisex WC's | Item
ii | To commercial Kitchen inc Stores, Changing Room, Prep Area and Office, the Contractor is to allow for preparing existing concrete floor surface prior to applying new DPM latex to ensure that a level finish free of moisture is provided. Contractor will be required to demonstrate floor surface is free of moisture prior to applying vinyl. Following Contractor to supply and fit new Polysafe Apex sheet vinyl flooring in colour Chromite (or equal and approved) including cap and coving in the below chosen finishes. Available from Polyfloor (Tel: 0161 767 1111). Install in accordance with manufacturer instructions and include for adhesive wastage, stainless steel transition and threshold strip bars. Colour to be confirmed. Include for all adhesives and the like and threshold strips as required. Allow for all cutting and waste, for dressing the vinyl up and providing coved skirtings min 100mm above floor level. | Item
iii | To the new external doorways being formed to the 2.nr EY Classrooms and the 3.nr exit doors within the Canteen, the Contractor is to allow for forming new recessed matwells measuring the width of the entrance in width by 1500mm deep minimum using Heckmondwike Hippo barrier matting in colour TBC and inclusive of all trims in brushed chrome finish. | Item
iv | To the First Floor new Classrooms being created following removal of existing dividing partition, the Contractor is to allow for providing new Carpet tile finish to both Classrooms using Heckmondwike Supacord in Anthracite. Install in accordance with manufacturer instructions and include for adhesive wastage, stainless steel transition and threshold strip bars. Colour to be confirmed. Include for all adhesives and the like and threshold strips as required. Allow for all cutting and waste, for dressing the flooring upto the existing skirting boards. | Item
v | To the new classroom sinks being provided in locations where currently not provided (KS2 Classrooms 1&2, KS2/KS3 Classroom 1 and EY/KS1 Classroom), the Contractor is to allow for providing new vinyl covering to the sink surround approx 1000mm in depth by 2000mm in length, utilising Polysafe Standard PUR sheet vinyl flooring in colours TBC. Install in accordance with manufacturer instructions and include for adhesive wastage, stainless steel transition and threshold strip bars. Colour to be confirmed. Include for all adhesives and the like and threshold strips as required. Allow for all cutting and waste, abutting upto skirting/room perimeter inc kick boards, clear sealant to be used on completion to surround. Transition strip in black to be used with boarder to carpet tiles. | Item
vi | Contractor to also allow for renewing carpet tile finish to the following areas in accordance with Clause H.iv above; KS2/3 Classroom next to PPA Room (First Floor), Office adjacent to Staff Kitchenette (First Floor), 2.nr new EY Classrooms where new external doorways being provided (Ground Floor), Staff Room (Ground Floor) and the new Reception Office (Ground Floor). | Item
vii | Should any further flooring renewal works be required where existing surfaces are determined to be worn etc, the Contractor is to allow Provisional Sum of £5,000 for instruction by the CA. | PROV SUM | 5000
9 | MEP
A | The Contractor is responsible for the design, install and alteration of all electrical, mechanical and public health installations in order to provide compliant and appropriate service provisions to meet the end-users requirements and facilitate the build, as detailed within the proposed drawings. This will include but not be limited to the following system; • Additional small power and data outlets, inc new circuits where required, to meet requirements shown within the appended drawings, such as for the new interactive teaching screen locations, new washroom locations, improvement of existing washrooms, improvements to existing Commercial Kitchen, new Commercial Kitchen, new Server Room location,
• Adaptions to the existing lighting layout to reflect spatial changes inc emergency luminaries and luminated exit signage, inc new external lighting
• Adapting the existing means of smoke detection so that all new areas are provided with coverage back to the control panel
• Providing emergency lighting where deemed required by Fire Engineer, inc upgrade of existing lighting to LED where economically viable
• Additional door access control points to add to the existing system both externally and internally in order to control access • Adaptions to existing heating system, provision of heating to new rooms (advise using electric rads)
• New below ground drainage runs where new outlets are proposed inc connections to existing/inspection chambers
• Provision of new hot, cold water and waste to new washroom and classroom sink locations, inc provision of localised electric water heaters
• Adapt/new CW, HW and waste supplies where required to adapted washrooms
• Provide new mechanical through wall extraction to washrooms
Works are to be undertaken in accordance with the following standard clauses; General Mechanical & Electrical Clauses
• Electrical work is to be carried out by a suitably qualified Electrical Engineer to comply with the Current edition of the IEE Regulations and BS7671:2001 • The Contractor is to allow to produce Record Drawings to record the new installations and alterations • Allow to provide Maintenance details for the Health and Safety File • Allow for all necessary fire stopping for new service runs • Allow for all required and necessary BWIC with regards to MEP works • All new electrical fittings to be supplied by either MK Electrics or Crabtree • All new electrical wiring and outlets to be surface mounted in plastic conduit for ease with flush surface fixings (power outlets/light switches etc) to be provided • In accordance with Building Bulletin’s and DFE design guidance including but not limited to the following; • Technical Annex 2E – Daylight and Electric lighting, Version 9 • Technical Annex 2F – Mechanical Services and Public Health Engineering, Version 9 • Technical Annex 2G – Electrical Services, Communication, Fire and Security, Version 9 • Building Bulletin 100 – Design for Fire Safety in Schools • Building Bulletin 101 – Guidelines on ventilation, thermal comfort and indoor air quality in schools, Version 1.
B | Electrical
i | Prior to strip out commencing Contractor to allow for isolating all services and removing services from walls, locations to be demolished/adapted and ensuring safe on completion. | Item
ii | Contractor to allow Provisional Sum should any electrical repairs or upgrades be required to be expended by the CA. | PROV SUM | 5000
iii | In accordance with the proposed electrical and data (CAT6) layout plans, Contractor is to design and install the adaptions shown on the appended drawings and detailed below, inc new supplies, circuits, with all new cabling to run within protected conduit in white. Junction boxes at desk/worktop level to be provided in relation to the outlets to the Food Tech Classroom, Commercial Kitchen HoC/OP Office. Services to new partitions are to be run within the partitions rather than surface mounted. New fused spurs to be provided to all fixed installations as required under good working practise such as extracts, white goods, electric water heaters, radiators etc. Note proposed layouts are purely indicative and the Contractor will be responsible for designing final locations to ensure sufficient number of electrical outlets are provided to serve necessary appliances, fittings etc referenced within this document. For clarity 2.nr double electrical and 2.nr single CAT6 data outlets to be provided within the dado trunking to each new interactive teaching board location. Individual rings to be provided to all oven/hobs, with 2.nr double sockets to be provided to each workstation (4.nr workstations) to the Food Tech Classroom. | Item
New services as detailed on the appended drawings in relation to the following but not limited to;
New washrooms and adaptions to existing washrooms, such as for water heaters, hand dryers, mechanical extraction, lighting, earthing.
Refurbishment of Commercial Kitchen and new room spaces being provided
New Food Tech Classroom to First Floor, inc supplies for ovens, convector hobs, white goods, extractors, water heaters, earthing.
New interactive teaching walls to classrooms.
iv | Contractor to allow for providing new dado trunking and containment to the new teaching wall in accordance with the proposed plans and indicative elevation, utilising chamfered 3 part dado trunking in white uPVC and pulling supplies through ready for use. All new data cabling is to be taken back to the new data cabinets ready for Named Sub Contractor to terminate and commission. Contractor to allow for supply and install of new 65” C Touch interactive screen in accordance with the proposed plans, ensuring that unit is fully functioning on completion in accordance with manufactures guidance. Contractor to also allow for relocating 1.nr interactive screen to the First Floor new KS2/KS3 Classroom as shown on the plans, allowing to commission on completion to ensure correctly functioning. | Item
v | Contractor to allow for the appended quote provided by the end-users incumbent IT Contractor (Joskos), in relation to the 2nd fix IT works. Contractor to liaise with the Named Sub-Contractor and allow for their attendance, OHP etc. In particular the Contractor should allow for liaising with them at an early stage in order to ensure programme activities are correctly sequenced in a way that doesn't incur delays at a later date. Note: Named Sub-Contractor quotation includes for all electrical works within the new Server Room. | Item
vi | For clarity the Main Contractor will be responsible for installing running the new CAT6 cabling to each outlet back to the new Server Room location ready for the Named Sub-Contractor (Joskos) to terminate, patch and commission etc. Contractor to allow said cost here. | Item
vii | The Contractor will be required to design and install adaption of existing lighting to suit the new layout, new rooms to be provided inc controls, including wiring utilising ceiling mounted lights all with new LED lighting, incorporating emergency lighting to meet Building Regulations and BS EN 12464-1 and Figure 2 of BS 5266-1 where deemed required, such as rooms over 60m2 floor area and those at high risk. As such the Contractor is to provide cost for design, supply and install of new LED lighting, allowing for any new wiring, and connections to new distribution boards/circuits. All new wiring is to be surface mounted in uPVC conduit. | Item
1) New surface mounted LED Lighting to be provided inc of emergency lighting, min. LUX 500 with motion sensor lighting. To all WC's lighting to be controlled via PIR sensors. (This assumes existing power supply will be to current standards where a modification certificate can be issued (i.e.: must be on an RCD distribution board)).
2) New lighting to be provided to the KS1 WC's to Canteen inc to the new suspended grid ceiling to be LED flush mounted and controllable via PIR to be located by the door entrance.
viii | Externally, the Contractor is required to design and install new lighting as indicated on the proposed drawings, incorporating LED floodlights over external doors and footpath with PIR sensors and manual timers that can be adjusted as required to suit the changing seasons. | Item
ix | Contractor to allow for adaptions to the existing fire alarm system in terms of providing means of detection and warning to all escape routes and rooms off escape routes in accordance with the appended Fire Strategy and in accordance with BB100 recommendations, ensuring that a compliant L3 system is provided on completion of works. As the building is currently vacant the Contractor will be able to utilise their own supply chain for these works. | Item
Contractor will be required to install mains powered with battery backup smoke detection units capable of being interlinked so that in the event of one alarm being triggered they all sound so that the building can be evacuated. Battery packs are to be minimum 10 year lifespan in case of power cut. All cabling is to be hidden within ceiling voids, chased etc. Units are to provide 85 dba from 3m distance, comply with BS EN 14604:2005 and incorporate a test button feature
Means of heat detection to be provided to the Commercial Kitchen and Food Tech Classroom.
X | Door Access Controls
a | In accordance with the appended quote and plans, Contractor to allow for appointing Named Sub Contractor CRL Security Systems Ltd, in relation to design, supply and install of new door access control system to the site inclusive of new isolated biometric scanners. Contractor to liaise with the Named Sub-Contractor and allow for their attendance, OHP etc. In particular the Contractor should allow for liaising with them at an early stage in order to ensure programme activities are correctly sequenced in a way that doesn't incur delays at a later date. | Item
b | The Main Contractor will be required to provide new power supply and data supplies to each location prior to the door access controls specialist attending, as such it is crucial they engage with them from an early stage. For pricing purposes, each door access control point will require a 3amp spur and single network data socket to be located adjacent to the controller. Where the system requires a Biometric reader a 3amp spur and two network data sockets (one for Paxton & one for Ievo) will need to be provided by the Main Contractor. Main Contractor to allow for all BWIC inc trunking as required to facilitate. Contractor to allow for steel conduit externally and uPVC trunking internally. | Item
c | The Main Contractor will also be required to provide new fire alarm interface to each door access control location and the serving hatch to the Canteen for the door access specialist to connect to, in order for doors to release on activation of the fire alarm system. Main Contractor to allow for all BWIC inc trunking as required to facilitate. Contractor to allow for steel conduit externally and uPVC trunking internally. | Item
d | Contractor to allow the Provisional Sum of £2,500 for any further works which may be required in relation to the new door access control system to be expended by the CA. | PC SUM | 2500
xi | Subject to investigations and discussion with the end-user, Contractor to allow Provisional Sum of £5,000.00 for any additional camera's to be required. | PC SUM | 5000
xii | In accordance with the proposed drawings, the Contractor will be required to form an opening to the load bearing wall in order for a new serving hatch/counter to be provided to the Reception Office to improve security. This will also be where the new Inventry signing in system will be located. The Contractor will be required to design and install lintel to be provided to the load bearing wall, providing structural calculations before undertaking works, breaking out brickwork beneath and making good to the surround. Opening to be formed roughly 800mm above FFL and extend 1800mm above FFL by 1500mm in width. | Item
xiii | To each of the new accessible WC's, the Contractor is to design, supply and install means of fall arrest alarm, utilising a pull cord within the WC as shown on the appended drawings, with connecting sounder and beacon located within the main corridors outside, in order to alert staff in the event of user requiring assistance. Test switch to be provided within the corridor for manual testing and means of manual reset. Units are to be hard wired and incorporate battery backup packs. Disabled call alarm system to comply with BS EN 8300:2009. | Item
XIV | CCTV
a | The Main Contractor will be required to relocate and provide additional cameras to supplement the existing CCTV system which is provided to the building through a PoE basis. Contractor will be responsible for design and install of the new cameras/relocation of existing in order to provide suitable means of coverage as reflected within the proposed drawings. The existing control panel is located within the proposed Medical Room where new supplies will be terminated. Contractor to provide new POE HDMI faced wide lens IP 65 rated cameras as indicated on the proposed plans. Contractor to commission and demonstrate successful operation on completion so that system can be managed remotely. For pricing purposes Contractor should price for the following to be firmed up once works are on-site; | Item
b | Provisionally supply and install 300lm of new CAT 6 cabling to supply existing cameras to be relocated and new cameras back to the control panel and patch in. | PC QUANT
c | Provisionally supply and install an additional 4.nr Avigilon Cameras IP EXT H/PHERIC 6MP 1,45MM 6MP SENSOR Wall /Ceiling Mounted in locations to be confirmed on site. | PC QUANT
d | Contractor to allow the Provisional Sum of £1,250 for any upgrades or repairs required to the existing CCTV control panel. | PROV SUM
xvi | Contractor to allow for all BWIC with the electrical works inc new data runs, such as penetrations, sleeving, any excavations in relation new power supplies, firestopping, sealants etc in order to complete the works to an acceptable and compliant standard. | Item
D | Mechanical
i | Prior to strip out commencing Contractor to allow for isolating services and removing from walls to be demolished/adapted and re-securing as required to suit the new use. | Item
ii | Contractor will be required to design and install new means of hot water production to the new sink locations shown such as to the new Washrooms, First Aid Room, Food Tech Classroom and Classrooms, in order to meet the demands of the number of new outlets shown on the proposed drawings. Contractor will be responsible for suitably sizing the electric water heaters based on the expected demand, running new electrical supplies, pipework, lagging and valves as required. All surface mounted pipework to be boxed in. Contractor will need to demonstrate that new outlets can provide hot water between 38-43 degrees Celsius and not exceed this temperature. | Item
iii | Contractor will be required to design and install new cold water supplies, hot water pipework and waste pipework, to all new sink outlets, toilets and showers shown on the drawings, such as to the new Washrooms, First Aid Room, Food Tech Classroom and Classrooms, in order to meet the demands of the number of new outlets shown on the proposed drawings. Contractor will be responsible for suitably sizing the pipework, providing lagging and valves as required. All surface mounted pipework to be boxed in. | Item
iv | Contractor to allow for adapting existing pipework (CWS, HWS and waste) where existing sanitaryware layout is to be adapted such as the Ground Floor Staff WC's. Contractor to ensure that sufficiently sized pipework to match the existing is utilised, pressure tested and demonstrated as fully functional on completion to the CA. Contractor will need to demonstrate that new outlets can provide hot water between 38-43 degrees Celsius and not exceed this temperature. | Item
v | Contractor to allow the Provisional Sum of £5,000.00 for any upgrades required to the existing hot water production system should any issues be identified during the Construction Period, such as the electric water heaters to the existing Ground Floor WC's adjacent to Entrance. | PC SUM | 5000
vi | Contractor will be required to design and install all waste water and foul connections to new external drainage being laid by the Named Sub-Contractor, Drainsmart, allowed elsewhere within the pricing document. Contractor to allow for liaising with them prior to making connections. | Item
vii | To the new rooms being created the Contractor will be required to design and provide new means of spatial heating in order to achieve an ambient room temperature of 21 degrees Celsius using LST electric radiators given the difficulty which would be caused by teeing off the existing wet system. Means of controlling the radiator to each room to be provided through a thermostat to the wall adjacent to the light switch where practical so that rooms can be individually controlled to suit use. | Item
viii | Contractor to design and install new mechanical extraction as shown on the drawings to all washrooms including both new and existing and the First Floor Staff Room (given there is none currently provided to existing toilets), including chasing out external walls, allowing for all BWIC, making good works, wiring and connections back to distribution board. Extract rate of no less than 54m3/h 15 l/sec to be provided. Extraction fans to the WC's to be automatically operated when humidity level threshold reached. | Item
ix | To the new Food Tech Classroom, the Contractor will be responsible for the designs, supply and installation of new mechanical extract system capable of achieving an appropriate extract rate of minimum 216m3/h 60 l/sec. For calculation purposes we recommend a minimum air change rate of 15 per hour. Contractor to allow for chasing out external walls, allowing for all BWIC, making good works, wiring and connections back to distribution board. | Item
x | To the Commercial Kitchen, the Contractor will be required to relocate the existing gas safety shut off valve as indicated on the attached drawings, in addition to making adaptions to the existing gas supplies in preparation for connection to the new range being installed. | Item
xi | Contractor will be required to service, overhaul and clean the existing extract hood and system currently provided to the Commercial Kitchen to ensure it is in full working order prior to handover. Contractor should allow a cost for a specialist engineer to attend and advise. | Item
xii | Should any repairs be required to the existing extract system to the Commercial Kitchen, the CA will instruct works utilising the Provisional Sum of £1,250.00. Contractor to allow for this Provisional Sum within their submission. | PC SUM | 1250
xii | To the new First Aid Room, the Contractor is to supply and install new porcelain wall hung hand wash basin with TMV circa 300-400mm dia, such as the Nuie 350mm Wall Hung Basin - 1 Tap Hole, supplied by Victorian Plumbing. All supplies, connections and waste allowed previously within this section of the document. Contractor to allow for sealants to surround of splashback specified previously. | Item
xiii | To the 2.nr Hygiene Rooms, the Contractor is to allow for forming waste outlets within the floor slab to each location prior to new screed and finish being laid, in addition to providing new electric wall mounted shower units, utilising Triton Omnicare Design Thermostatic Shower with Grab Riser Rail Kit or equal and approved. Provision of new electric supplies should be allowed within the electrical section, equally new pipework should be allowed with the associated mechanical clause. | Item
xiv | Contractor to allow for all BWIC in connection with mechanical works such as sealants to surround of new sinks, penetrations through walls/partitions, making good to surrounds, firestopping etc. In particular contractor will be required to install new Rockwool FirePro Collars to provide minimum 1 hour protection to the surround of the existing heating distribution pipework where passing through the new partitions to be constructed around the existing pipework. | Item
E | Commercial Kitchen
i | In accordance with the appended quotation, the Contractor will be required to allow for the appointment of Named Sub Contractor Nisbets catering in relation to the supply and install of equipment to the commercial Kitchen. Contractor to liaise with the Named Sub-Contractor and allow for their attendance, OHP etc. In particular the Contractor should allow for liaising with them at an early stage in order to ensure programme activities are correctly sequenced in a way that doesn't incur delays at a later date. | Item
ii | As the named sub-contractor has only allowed for the install of specific items highlighted within their appended quote (rationale oven, gas oven, dishwasher), the Main Contractor will need to allow for positioning and installing all other equipment being supplied by Nisbets, ensuring that they are correctly supported and in accordance with the manufacturers guidance. NOTE. We have approached Nisbet for comment but they were unable to install the remaining order. | Item
F | Documentation
i | Following completion of the works the Contractor is to provide the following, but not limited to, in date test certificates to the satisfaction of the CA in relation to all works prior to Practical Completion being issued; | Item
• NICEIC install certificates to account for new work • Test log for all new data wiring back to servers • Emergency Lighting test Certificate inc LUX levels drawing for all luminaries • All new cabling to be suitably protected by uPVC conduit where not run within new partitions • Fire alarm and access control test certificates in relation to planned adaptions • Chlorination and pressure test certificates in relation to new pipework • Demonstration of operation of all new installations to the satisfaction of the CA and Clients IT Engineer prior to issue of PC • Note: Contactor to allow for all required and necessary BWIC with the above MEP scope of works.
NB: Contractor is to test all electrical items upon completion of the above works in order to ensure that they are in correct working order prior to completion of the works and carry out a Five Year Test, including the issue of all statutory certification.
10 | EXTERNAL WORKS
A | Civils Works to Boundary
i
ii
B | Fencing
i | Contractor is to undertake a CAT scan survey to all working areas prior to carrying out the new installation in order to locate any cable runs within close proximity to the area of work. On completion Contractor is to provide a marked up plan highlighting identified services, marking out of area to identify new wiring runs and locations of fixings and posts for new fencing. | Item
ii | Contractor to excavate for new fence posts to a depth of min 600mm/in accordance with manufacturers recommendations prior to install of posts. Note: Contractor to allow for cutting back vegetation as required in order to complete works. Note: New posts are to be installed behind the fence line to match the existing timber fencing. | Item
Existing Fencing along Canterbury Road
iii | Along Canterbury Road the Contractor will be required to adapt the existing bow top iron railings where the new Pedestrian entrance and vehicle entrance to the adjacent school site are to be provided. Contractor should allow for cutting back neatly to the nearest post as shown on the drawings in order to provide the desired opening shown on the drawings. | Item
iv | Where new opening has been formed for pedestrian entrance, Contractor will be required to supply and install new set of 1800mm wide low level pedestrian gates using galvanised steel bowtop fencing in black to match the existing. | Item
v | Where new opening has been formed for new vehicle entrance/exit to the adjacent school site, Contractor will be required to supply and install new set of 4000mm wide 358 weldmesh steel vehicle gates, 2000mm high in black to match the existing. Contractor will be required to fix 1.nr side panel to connect one of the posts to the existing 358 weldmesh fencing to the school pedestrian entrance. The other fence post at the opposite end of the gates will need to tie-in with the existing low-level bow top railings. | Item
Fencing to Separate Sites & Secure Rear of Site
vi | As detailed on the appended plans, the Contractor will be required to supply and install new fencing to separate the two sites using new 358 weldmesh steel fencing in black to match the existing along the street at 2000mm height. Contractor to allow for tieing in the fence posts to brickwork as shown on the layout plan, cutting down panels to suit without affecting integrity. | Item
vii | To the rear and flank sections of the fence line separating the two sites and to the South Boundary of the site as shown on the appended drawings, the Contractor will be required to provide new 2000mm high 358 weldmesh fencing in black in order to ensure the site is secure in terms of preventing access to the rear. | Item
viii | Contractor will be required to supply and install new 1200mm wide pedestrian gates in 3.nr locations to the new fence line as shown on the appended plans using 358 weldmesh steel gates at a height of 2000mm in black. Contractor to ensure that new steel posts are min 600mm secured below ground. | Item
ix | To the far rear corner of the site as shown on the drawings, the Contractor will be required to supply and install new 200mm high 358 weldmesh vehicle gates in black 3000mm wide to match the fencing proposed to the rear in order to provide vehicle access to the rear of the site. | Item
New EY Playgrounds
x | To the 2.nr new early years playgrounds being created to provide direct external space to EY Classrooms, the Contractor is to supply and install new 1000mm high picket fencing and gates utilising treated timber fencing in accordance with the appended drawings. Contractor is to ensure that surfaces are free of sharp edges, splinters and smooth on completion. 2.Nr timber picket gates to be provided should be provided with latches to secure into place when closed. | Item
New Soft Play Playground
xi | To the surround of the new soft play playground located centrally to the Playground, the Contractor is to allow for the supply and install of new 1800mm high flatform weldmesh fencing in green as indicated on the plans. | Item
xii | As indicated on the plans, the Contractor is to allow for the supply and install of 2.nr 1000mm wide flatform weldmesh pedestrian gates in green to the new soft play playground at 1800mm in height. | Item
C | Creation of New Soft Play Playground
i | In accordance with the appended quote and design, the Contractor is to allow for appointing the Named Sub Contractor Rhino Play (SW) Ltd for the design, supply and construction of the new soft play playground to be provided centrally to the rear of the site. Their appended quote is inclusive of all ground works with exception of providing a land drain beneath the new trampoline where void will be formed. Main Contractor should allow for their quote plus attendance and OHP in relation to managing them. | Item
ii | Contractor will be required to design and construct a new land drain from the pit excavated beneath the new trampoline connected back to the nearest manhole laid to a fall towards the rear of the site. Contractor will need to allow for excavating across the playground and backfilling with removed soil. Perforated land drain to be a minimum of 100mm diameter. | Item
D | Landscaping Works General
i | To the new enclosed EY Playground to be provided to the EY Classrooms, the Contractor is to allow for providing a new rubber crumb soft play surface in accordance with the design and quote provided by Rhino Play (SW) Ltd. Main Contractor should allow for their quote plus attendance and OHP in relation to managing them. | Item
ii | Contractor to allow for adapting growth along the boundary to Canterbury Road in order to allow for the adaption works to the form new pedestrian entrance and vehicle entrance to be provided. Contractor should allow for trimming back and cutting back growth, removal and disposal from site.
iii | To the Car Park, the Contractor will be required to repair sections of the tarmac where wearing course has deteriorated and sub base has been affected. For pricing purposes the Contractor should price for provisionally undertaking 50m2 of tarmac patch repairs to small areas between 1-10m2 ensuring that a flush surface is provided on completion. | PROV QUANT
iv | Contractor to allow the Provisional Sum of £3,500.00 for any further landscaping works required to be instructed by the CA. | PC SUM | 3500
v | Contractor to thoroughly clean down all external surfaces on completion of the works, such as jet washing all tarmac and hardstanding areas. | Item
vi | Contractor to allow for mowing all lawned areas on completion of works and allow for watering the lawns on completion. | Item
vii | Contractor to allow for removing all weeds to the surround of the building in particular where currently growing at the base of external walls. Contractor to allow for applying non-glyphosate weedkiller prior to removing and re-applying on completion to ensure they do not re-grow prior to handover. | Item
viii | Should any seeding works be required the Contractor should allow Provisional Sum of £500.00 to be instructed by the CA. | PC SUM | 500
E | External Miscellaneous
i | To the rear elevation of the main building over the proposed EY Playground, the Contractor is to allow for the design and install of new freestanding canopy supplied by Broxap in accordance with the appended quote. Contractor will be required to undertake setting out works on-site and liaising with the specialist prior to placing order. | Item
ii | Beneath the canopy roof, the Contractor is to allow for installing a new sand pit constructed from treated 2400x200x100mm timber sleepers measuring roughly 2400x2400mm in length and 600mm in height above ground level. Contractor to thoroughly rub down to ensure there are no sharp edges, splinters prior to filling minimum depth of 300mm using play pit sand. On completion Contractor to supply sheet of OSB Board which can be secured at the end of each working day onto of the sleepers to prevent use by foxes etc. | Item
iii | Beneath the canopy to the EY Playground, the Contractor will be required to construct a new temporary stage that can be easily moved as required by the school. Stage is to be constructed from sound timber pallets roughly 2400mm in length by 800mm in depth in location to be confirmed. OSB boards are to be fitted on the top surface of the pallets and back with 2x2 timbers to provide support and prepared ready for decoration. | Item
iv | To the EY Playground Perimeter, Contractor will be required to supply and assemble 10.nr moveable long planters 900x400x300mm supplied by EE Supplies (or equal and approved), ensuring that units are free of sharp edges, splinters prior to handover. Contractor to allow for sanding down each unit. Following assembly Contractor to allow for lining with plastic sheeting and drilling several drainage holes through to the base of the units for drainage. Following allow to fill upto 50mm from the top of the unit with all purpose compost. | Item
v | To the main entrance and entrance to the Commercial Kitchen, the Contractor is to allow for the design and install of new wall mounted canopies supplied by Broxap in accordance with the appended quote. Contractor will be required to undertake setting out works on-site and liaising with the specialist prior to placing order. Contractor to allow for securing back to brickwork and junctions silicone sealed with external grade product. | Item
vi | Contractor is to allow for relocating the existing metal framed Bin Store currently bolted into the hardstanding along the boundary to Canterbury Road and relocate to the flank of the Store, as shown on the proposed plans. Contractor to allow for removing the bins within and setting aside, prior to carefully deconstructing the unit and reconstructing in the new place, including replacing bolt fixings if needed. On completion, Contractor to allow for making good previous fixing holes using hot pour tarmac from the car park works and giving a thorough clean, overhaul. | Item
vii | As indicated on the appended plans, the Contractor will be required to renew all existing thermoplastic markings to the Playground such as parking bays, yellow hatches, entrance, exit wording, noting that some of those shown on the proposed external plans are new. | Item
F | Below Ground Drainage Works
i | Contractor to allow the appended quote provided by the Named Sub Contractor Drainsmart, for undertaking below ground drainage repairs in accordance with their previous findings/breakdown provided. Contractor to allow for their quote, attendance and OHP. | Item
ii | Contractor to allow the appended quote provided by the Named Sub Contractor Drainsmart, for providing new below ground drainage and connections to existing chambers, in relation to new washrooms and classroom sinks, where locations are currently not served, in accordance with their drawings. Contractor to allow for their quote, attendance and OHP. | Item
G | To the rear corner of the site shown on the external drawing where highlighted, the Contractor is to allow for carefully relocating 1.nr steel container to the adjacent area as requested by the end-user. For pricing purposes please allow a days hire for a telehandler and two operatives. | Item
11 | MISCELLANEOUS
A | Contractor to allow for a builders clean and sparkle clean on completion of all working areas and external areas to ensure that sufficient cleanliness is provided at handover to the Client. Contractor to also allow for thorough clean of all associated external areas in relation to site setup/access on completion. Contractor to make good all soft and hardstandings following dismantling of access and site setup to ensure in the same condition as prior to works undertaken. | Item
On completion of all works the Contractor is to make good all surrounding/landscaped areas such as existing surfaces so that areas are left tidy and presentable on completion.
Note: It is advised that the Contractor undertakes a Schedule of Condition prior to commencing works to use a reference at a later date.
B | Blinds
i | In accordance with the appended quote provided by Surrey Blind & Curtain Co Ltd, the Contractor is to allow for their appointment as Named Sub-Contractor, in order to undertake all adaptions to the existing blinds as necessary in order to ensure they are anti-ligature compliant. As part of the works they have allowed for the supply and install of a small number of new units. Contractor to allow for their quote, attendance and OHP, ensuring that they appoint them in good time prior to works being required. | Item
C | Specialist Sensory Equipment
i | Contractor to allow the Provisional Sum of £5,000.00 in relation to electrical adaptions required to the Sensory and Therapy Rooms to suit the new specialist equipment layout being provided by the end-user. CA to instruct once requirements have been firmed up by the end-user. | PROV SUM | 5000
ii | Contractor to allow Provisional Sum for any further specialist equipment to be provided as directed by the CA. | PROV SUM | 3000
D | LST Radiator Covers
i | Contractor to allow for supply and install of new bespoke LST covers over each cast iron radiator (circa 8.nr) to the new ARP unit in accordance with the quote obtained by the CA, to be provided during the tender period. Contractor will be required to firm up the order prior to placing order ensuring that they take measurements on-site to confirm they are correct. | Item
i | To all existing conventional radiators, the majority of which are not boxed and so present a potential scalding issue, the Contractor is to allow for supply and install of pre-finished MDF perforated radiator covers in white to all radiators where currently none are provided. Contractor to allow for measuring prior to ordering, MG surrounding surfaces following install etc, to ensure a good level of finish is provided on completion. | Item
E | Acoustic Treatment
i | The Contractor will be required to supply and install new Ecophon Solo Rectangle acoustic panels to rooms as detailed within the Acousticians recent report in order to reduce reverberation times, improve the learning environment and aim to achieve compliance with BB93 performance requirements. Given budget constraints, practicality of working within an existing building etc, we are merely reducing current reverberation times in order to improve the facility for the school. Contractor will be required to mechanically fix these panels back to the ceiling soffit as advised by the Acoustician and in accordance with manufacturers recommendations, allowing to position in between lighting rafts and the buildings structure such as beams. Panels will need to be fixed between lighting rafts in accordance with the general layout plan provided within the tender pack. Contractor will need to allow for developing these and confirming setting out on-site to the CA prior to commencing works. | Item
ii | In accordance with the above and plans provided, Contractor should allow for supply and installing of the specified acoustic panels inc allowance for setting out to the below areas;
a | Main Hall/ Multi Use Space - 2400 x 1200mm panels | Item
b | Canteen - 2400 x 1200mm panels | Item
c | Multi Purpose Area (to Canteen) - 2400 x 1200mm panels | Item
d | Flexible Space - 1800 x 1200mm panels | Item
e | Sensory Room - 1800 x 1200mm panels | Item
f | Therapy Room - 1800 x 1200mm panels | Item
g | Ground Floor Classrooms (5.nr) 1800 x 1200mm panels | Item
iii | It is expected that some services may require minor adjustments and alterations to allow for acoustic panels to be fixed directly back to the ceiling soffits. For pricing purposes Contractor to allow Provisional Sum to cover for the CA to utilise. | PROV SUM | 2000
F | Contractor to allow Provisional Sum for any firestopping remedials to be undertaken (above and beyond firestopping to new service runs etc) to be instructed by the CA. | PROV SUM | 5000
G | Contractor to allow for the Contingency Sum to be expended by the Contract Administrator. | PROV | 12000
3 | SCHEDULE OF WORKS |  | £
SUMMARY
1 | GENERAL
2 | ACCESS
3 | STRIP OUT
4 | EXTERNAL ENVELOPE
5 | STRUCTURAL ADAPTIONS
6 | DRYLINING
7 | JOINERY
8 | FINISHES
9 | MEP
10 | EXTERNAL WORKS
11 | MISCELLANEOUS
SOW TOTAL
PRICING SUMMARY
1 | Preliminaries
2 | Schedule of Works
TOTAL

## HOLLYMOUNT
Hollymount Primary School & Malmesbury Primary School, LB of Merton
Fire Door Package
Contractor Pricing Document
Note: Contractor to note that the Schedule of Works, drawings and appendices take precedence over the descriptions provided in this document and as such these should be priced. This document has been provided in editable format to make it easier for the contractor to insert their costs.
Ref Nr | Item/Description | Item/PC | Cost (£)
Section 1 | Preliminaries
Section 2 | Schedule of Works |  | (price within breakdown below)
B | HOLLYMOUNT PRIMARY SCHOOL
1 | STRIP OUT
i | Prior to works commencing the Contractor is to allow for isolating all services to the working areas to minimise hazards. | Item
ii | Following suitable access being provided, Contractor is to allow for stripping and disposing of all existing doorsets due to be renewed as per the appended door schedule and drawings, allowing to appropriately dispose of doorsets. | Item
iii | Contractor to allow for carefully stripping out existing doorsets ensuring no damage to adjoining surfaces is caused. | Item
iv | Contractor to allow for carefully removing, carting away and appropriately disposing of Georgian wire glazing above corridor door to Ground Floor of single storey adjacent to Music Room, as per the appended drawings, ensuring no damage is caused to the adjacent surfaces. | Item
v | A copy of the Asbestos Register has been included within the tender pack. It not believed that any asbestos will be present behind door linings however for the avoidance of doubt, should sampling and any subsequent asbestos removal be required, the CA will instruct utilising PC SUM. Contractor to allow for the following Provisional Sum as part of their submission. | PC SUM | 2000
2 | NEW FIRE DOORS
New Fire Doors
NOTE: All new doorsets are shown in red on the appended proposals and detailed within the Door Schedule per room
A | As directed by the appended Door Schedule and proposed drawings, Contractor to supply and install new FD30s rated timber doorsets (double doors) finished in to match existing doorsets to this area of the building. The doorsets will incorporate fire rated impact resistant vision panels as shown in the appended drawing. Internal door set to match the existing doors to this area of the building as per the Door Schedule complete with linings, architrave and stops. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. | Item
Include for routing out and installation of smoke seals and intumescent strips to new doors inc thresholds, linings and fire rated vision panels to BS EN 1634 & BS 476. Doors made to measure to suit existing and new structural openings. Allow for adjustment to suit existing openings. Doors to be self-closing and to achieve ½ hour fire resistance in accordance with Building Regulations.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Supply and install overhead door closers in polished chrome to new doors inc chrome plate fire door signage as depicted on the proposed plans.
Note: Where new barrel locks are requested these are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
Dorguard and links to fire alarm to be provided where stated within the door schedule.
B | As directed by the Door Schedule and appended proposed drawings, Contractor to supply and install new sets of FD30s rated timber internal door sets finished to match the existing to this part of the building as shown on the Door Schedule, complete with linings, architrave and stops, complete with fire rated glazed viewing panels as requested on the 'Door Schedule', to provide means of separation between areas. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. | Item
Include for routing out and installation of smoke seals and intumescent strips to new doors inc thresholds, linings and fire rated vision panels to BS EN 1634 & BS 476. Doors made to measure to suit existing and new structural openings. Allow for cutting down of doors and adjustment to suit existing openings. Doors to be self-closing and to achieve ½ hour fire resistance in accordance with Building Regulations. Allow for providing polished chrome handles to accept new Laidlaw 6 pin euro cylinder locks.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Supply and install overhead door closers in polished chrome to new doors inc chrome plate fire door signage as depicted on the proposed plans. Polished chrome lever on rose door handles to be provided to match the existing. Where provided to Classrooms thumb turn locks (50mm screw on-rose) finished in polished chrome are to be provided to allow doors to be locked from the inside, inclusive of means to open from the outside.
Note: Where new barrel locks are requested these are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
C | As directed by the Door Schedule and appended proposed drawings, Contractor to supply and install new sets of solid FD30s rated timber internal door sets finished to match the existing to this part of the building as shown on the Door Schedule, complete with linings, architrave and stops as requested on the 'Door Schedule', to provide means of separation between areas. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. | Item
Include for routing out and installation of smoke seals and intumescent strips to new doors inc thresholds and linings. Doors made to measure to suit existing and new structural openings. Allow for cutting down of doors and adjustment to suit existing openings. Doors to be self-closing and to achieve ½ hour fire resistance in accordance with Building Regulations. Allow for providing polished chrome handles to accept new Laidlaw 6 pin euro cylinder locks.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Supply and install overhead door closers in polished chrome to new doors inc chrome plate fire door signage as depicted on the proposed plans. Polished chrome lever on rose door handles to be provided to match the existing. Where provided to Classrooms or washrooms, thumb turn locks (50mm screw on-rose) finished in polished chrome are to be provided to allow doors to be locked from the inside, inclusive of means to open from the outside.
Note: Where new barrel locks are requested these are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
D | To the surround of new linings Contractor to apply Intumescent Acrylic and Acoustic mastic sealant, (Product 58) from Envirograf. | Item
E | Replacement refers to complete replacement of the doorset, the doorset product must be inclusive of conformity certification or by independent registered installer schemes, where such schemes are available such as CERTIFIRE, BRE Certification and BM TRADA. Sample of door type and finish to be provided to CA prior to order and installation. | Item
F | Where provided Contractor to allow for isolated and reconnecting existing hold open's ensuring correct operation on completion. | Item
G | To the new doors except to Stores are to be provided with finger guards either side of the hinges to provide protection to children. Contractor to allow for supply and install of new Firestop Little Fingers Slimline Front Projector fingerguards, to either side of the door leaf's to cover hingers, in accordance with the manufacturers recommendations. | Item
3 | EXISTING FIRE DOORS
A | First Floor
i | Where existing fire doors are deemed to be of sufficient construction to provide protection and can be re-utilised, the Contractor will be required to remove door leaf's to allow thorough overhaul inc repair, replacement of defective/non compliant parts, joinery repairs, intumescent sealants, decorations etc. Contractor to price in accordance with the below re-measurable quantities; | Item
ii | Door Adjustment: Contractor is to allow for easing and adjusting (likely repair method to be re-hanging doors) door to ensure that the door shuts flush with no gaps larger then 4mm to the perimeter and a compliant base gap. Fire door is to close within time frames as stated within BS 9999:2017, BS 8214:2016. Doors must not be reduced or altered on site beyond the manufacturers guidelines as this will void certification. Please refer to Appendix B for areas and photos of affected areas. • For pricing purposes allow for 15.nr doorsets to be adjusted inc overhead closers | PC QUANT
iii | Intumescent Seals: Contractor is to allow for the replacement of missing intumescent fire seals to door. Contractor is to ensure that the door has a rebate suitable for the application of new rebated intumescent fire and smoke seals (Product 68) from Envirograf or similar approved. Contractor is to allow for works to all edges of the door. All works must be undertaken in line with manufacturer recommendations and guidelines. Please refer to Appendix B. • For pricing purposes allow for 15.nr doorsets to surround of lining • For pricing purposes allow for 15.nr doorsets for install including routing of rebate to leading edge of door leaf | PC QUANT
iv | Threshold Gaps: The threshold gap must not exceed 10mm. If it is more than 10mm then a face fixed or drop down threshold seal must be fitted. Please see ironmongery schedule on intumescent & cold smoke seals Door frame New Drop Seal: Contractor is to allow for the installation of new fire rated drop seal to suit fire rating of door set to be fitted in line with manufacture’s recommendations and guidelines. All works are to be in accordance with BS EN 1154:1997 and EN 1154:1996. • For pricing purposes allow for 15.nr drop down seals, pro rata if more is required. | PC QUANT
B | Ground Floor
i | Where existing fire doors are deemed to be of sufficient construction to provide protection and can be re-utilised, the Contractor will be required to remove door leaf's to allow thorough overhaul inc repair, replacement of defective/non compliant parts, joinery repairs, intumescent sealants, decorations etc. Contractor to price in accordance with the below re-measurable quantities; | Item
ii | Door Adjustment: Contractor is to allow for easing and adjusting (likely repair method to be re-hanging doors) door to ensure that the door shuts flush with no gaps larger then 4mm to the perimeter and a compliant base gap. Fire door is to close within time frames as stated within BS 9999:2017, BS 8214:2016. Doors must not be reduced or altered on site beyond the manufacturers guidelines as this will void certification. Please refer to Appendix B for areas and photos of affected areas. • For pricing purposes allow for 6.nr doorsets to be adjusted inc overhead closers | PC QUANT
iii | Intumescent Seals: Contractor is to allow for the replacement of missing intumescent fire seals to door. Contractor is to ensure that the door has a rebate suitable for the application of new rebated intumescent fire and smoke seals (Product 68) from Envirograf or similar approved. Contractor is to allow for works to all edges of the door. All works must be undertaken in line with manufacturer recommendations and guidelines. Please refer to Appendix B. • For pricing purposes allow for 6.nr doorsets to surround of lining • For pricing purposes allow for 6.nr doorsets for install including routing of rebate to leading edge of door leaf | PC QUANT
iv | Threshold Gaps: The threshold gap must not exceed 10mm. If it is more than 10mm then a face fixed or drop down threshold seal must be fitted. Please see ironmongery schedule on intumescent & cold smoke seals Door frame New Drop Seal: Contractor is to allow for the installation of new fire rated drop seal to suit fire rating of door set to be fitted in line with manufacture’s recommendations and guidelines. All works are to be in accordance with BS EN 1154:1997 and EN 1154:1996. • For pricing purposes allow for 6.nr drop down seals, pro rata if more is required. | PC QUANT
V | Where provided Contractor to allow for isolated and reconnecting existing hold open's ensuring correct operation on completion. | Item
4 | FIRE COMPARTMENTATION WORKS
A | To the Ground Floor corridor of the single storey building adjacent to the Music Room as per appended drawings, Contractor to allow for installing plasterboard infill to provide 30 minutes compartmentation, following removal of Georgian wire glass pane. Contactor to construct bulkhead utilising 48mm MF studs, head and sole plates, with 1.nr layer of 12.5mm Fireline board either side and 50mm isover insulation between. On completion tape and joint, rub down, ready to receive decoration specified elsewhere. | Item
B | Contractor to allow Provisional Sum for any firestopping remedials to be undertaken (above and beyond firestopping to the surround of linings and new door sets etc) to be instructed by the CA. | PROV SUM | 1500
5 | WORKS TO NON FIRE RATED DOORS
A | To the existing non-fire doors, Contractor will be required to overhaul where not correctly operating with ease to ensure left in a good and operational order on completion. Contractor should allow for removing door leaf's from hinges, re-hanging, adjusting hinges to ensure they correctly close within lining/against door stop, including adjusting of overhead closers. For pricing purposes Contractor to allow for overhauling 12.nr internal non fire doors. | PC QUANT
B | Contractor to allow the provisional sum for instruction by the CA in relation to any further repairs or replacement of parts required in relation to non fire rated internal doorsets following overhaul. | PC SUM | 2500
C | To the double glazed aluminium external doorsets, the Contractor is to allow for overhauling to ensure that they are able to operate, close and lock with ease. Contractor should allow for removing door leaf's from hinges, re-hanging, adjusting hinges to ensure they correctly close within lining/against door stop, including adjusting of overhead closers. For pricing purposes Contractor to allow for overhauling 4.nr sets of external doors. | Item
D | With regards to defective push bar releases to the external doorsets, the Contractor is to allow for renewing these to 2.nr sets of doors with matching new to ensure that they operate correctly. | Item
6 | MISCELLANEOUS
A | Contractor to allow for a builders clean and sparkle clean on completion of all working areas and external areas to ensure that sufficient cleanliness is provided at handover to the Client. Contractor to also allow for thorough clean of all associated external areas in relation to site setup/access on completion. Contractor to make good all soft and hardstandings following dismantling of access and site setup to ensure in the same condition as prior to works undertaken. | Item
On completion of all works the Contractor is to make good all surrounding/landscaped areas such as existing surfaces so that areas are left tidy and presentable on completion.
Note: It is advised that the Contractor undertakes a Schedule of Condition prior to commencing works to use a reference at a later date.
B | In relation to the existing door access controls provided to the external gates, Contractor needs to allow for appointing the schools incumbent fire alarm contractor, Failsafe Alarms , in relation to patching into the fire alarm system so that in the event of activating the gates release to allow evacuation to the Muster Point. Contractor to allow for the incumbents appended quote plus OHP for appointing/managing them. | Item
C | Contractor to allow for the Contingency Sum to be expended by the Contract Administrator. | PROV | 2500
3 | SCHEDULE OF WORKS |  | £
SUMMARY
1 | STRIP OUT
2 | NEW FIRE DOORS
3 | EXISTING FIRE DOORS
4 | FIRE COMPARTMENTATION WORKS
5 | WORKS TO NON FIRE RATED DOORS
6 | MISCELLANEOUS
HOLLYMOUNT SOW TOTAL

## MALMESBURY
Hollymount Primary School & Malmesbury Primary School, LB of Merton
Fire Door Package
Contractor Pricing Document
Note: Contractor to note that the Schedule of Works, drawings and appendices take precedence over the descriptions provided in this document and as such these should be priced. This document has been provided in editable format to make it easier for the contractor to insert their costs.
Ref Nr | Item/Description | Item/PC | Cost (£)
Section 1 | Preliminaries
Section 2 | Schedule of Works |  | (price within breakdown below)
C | MALMESBURY PRIMARY SCHOOL
1 | STRIP OUT
i | Prior to works commencing the Contractor is to allow for isolating all services to the working areas to minimise hazards. | Item
ii | Following suitable access being provided, Contractor is to allow for stripping and disposing of all existing doorsets due to be renewed as per the appended door schedule and drawings, allowing to appropriately dispose of doorsets. | Item
iii | Contractor to allow for carefully stripping out existing doorsets ensuring no damage to adjoining surfaces is caused. | Item
iv | Contractor to allow for carefully removing, carting away and appropriately disposing of non fire rated glazed screens and bulkheads, as per the appended drawings, ensuring no damage is caused to the adjacent surfaces. | Item
v | A copy of the Asbestos Register has been included within the tender pack. It not believed that any asbestos will be present behind door linings however for the avoidance of doubt, should sampling and any subsequent asbestos removal be required, the CA will instruct utilising PC SUM. Contractor to allow for the following Provisional Sum as part of their submission. | PC SUM | 2000
2 | NEW FIRE DOORS
New Fire Doors
NOTE: All new doorsets are shown in red on the appended proposals and detailed within the Door Schedule per room
A | As directed by the appended Door Schedule and proposed drawings, Contractor to supply and install new FD30s rated timber doorsets (double doors) finished in to match existing doorsets to this area of the building. The doorsets will incorporate fire rated impact resistant vision panels as shown in the appended drawing. Internal door set to match the existing doors to this area of the building as per the Door Schedule complete with linings, architrave and stops. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. | Item
Include for routing out and installation of smoke seals and intumescent strips to new doors inc thresholds, linings and fire rated vision panels to BS EN 1634 & BS 476. Doors made to measure to suit existing and new structural openings. Allow for adjustment to suit existing openings. Doors to be self-closing and to achieve ½ hour fire resistance in accordance with Building Regulations.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Supply and install overhead door closers in polished chrome to new doors inc chrome plate fire door signage as depicted on the proposed plans.
Note: Where new barrel locks are requested these are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
Dorguard and links to fire alarm to be provided where stated within the door schedule.
B | As directed by the Door Schedule and appended proposed drawings, Contractor to supply and install new sets of FD30s rated timber internal door sets finished to match the existing to this part of the building as shown on the Door Schedule, complete with linings, architrave and stops, complete with fire rated glazed viewing panels as requested on the 'Door Schedule', to provide means of separation between areas. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. | Item
Include for routing out and installation of smoke seals and intumescent strips to new doors inc thresholds, linings and fire rated vision panels to BS EN 1634 & BS 476. Doors made to measure to suit existing and new structural openings. Allow for cutting down of doors and adjustment to suit existing openings. Doors to be self-closing and to achieve ½ hour fire resistance in accordance with Building Regulations. Allow for providing polished chrome handles to accept new Laidlaw 6 pin euro cylinder locks.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Supply and install overhead door closers in polished chrome to new doors inc chrome plate fire door signage as depicted on the proposed plans. Polished chrome lever on rose door handles to be provided to match the existing. Where provided to Classrooms thumb turn locks (50mm screw on-rose) finished in polished chrome are to be provided to allow doors to be locked from the inside, inclusive of means to open from the outside.
Note: Where new barrel locks are requested these are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
C | As directed by the Door Schedule and appended proposed drawings, Contractor to supply and install new sets of solid FD30s rated timber internal door sets finished to match the existing to this part of the building as shown on the Door Schedule, complete with linings, architrave and stops as requested on the 'Door Schedule', to provide means of separation between areas. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. | Item
Include for routing out and installation of smoke seals and intumescent strips to new doors inc thresholds and linings. Doors made to measure to suit existing and new structural openings. Allow for cutting down of doors and adjustment to suit existing openings. Doors to be self-closing and to achieve ½ hour fire resistance in accordance with Building Regulations. Allow for providing polished chrome handles to accept new Laidlaw 6 pin euro cylinder locks.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Supply and install overhead door closers in polished chrome to new doors inc chrome plate fire door signage as depicted on the proposed plans. Polished chrome lever on rose door handles to be provided to match the existing. Where provided to Classrooms or washrooms, thumb turn locks (50mm screw on-rose) finished in polished chrome are to be provided to allow doors to be locked from the inside, inclusive of means to open from the outside.
Note: Where new barrel locks are requested these are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
D | As directed by the appended Door Schedule and proposed drawings, Contractor to supply and install new FD30s rated timber doorsets (door & a half) finished in to match existing doorsets to this area of the building. The doorsets will incorporate fire rated impact resistant vision panels as shown in the appended drawing. Internal door set to match the existing doors to this area of the building as per the Door Schedule complete with linings, architrave and stops. Contractor to allow for making good and touching up decorations to surrounding surfaces on completion, inc any adjustments required to the size of openings. | Item
Include for routing out and installation of smoke seals and intumescent strips to new doors inc thresholds, linings and fire rated vision panels to BS EN 1634 & BS 476. Doors made to measure to suit existing and new structural openings. Allow for adjustment to suit existing openings. Doors to be self-closing and to achieve ½ hour fire resistance in accordance with Building Regulations.
Allow to provide Grade 13 BS EN 1935 rated brushed steel hinges to doors. Supply and install overhead door closers in polished chrome to new doors inc chrome plate fire door signage as depicted on the proposed plans.
Note: Where new barrel locks are requested these are to be suited to match the existing locks which are currently on the same suite. 2.nr keys per door are to be provided.
Dorguard and links to fire alarm to be provided where stated within the door schedule.
E | To the surround of new linings Contractor to apply Intumescent Acrylic and Acoustic mastic sealant, (Product 58) from Envirograf. | Item
F | Replacement refers to complete replacement of the doorset, the doorset product must be inclusive of conformity certification or by independent registered installer schemes, where such schemes are available such as CERTIFIRE, BRE Certification and BM TRADA. Sample of door type and finish to be provided to CA prior to order and installation. | Item
G | To the new doors except to Stores are to be provided with finger guards either side of the hinges to provide protection to children. Contractor to allow for supply and install of new Firestop Little Fingers Slimline Front Projector fingerguards, to either side of the door leaf's to cover hingers, in accordance with the manufacturers recommendations. | Item
H | Given the age of the existing hold open devices fitted to walls for corridor doors, Contractor will be required to replace all existing units with new electromagnetic fire door hold open surface mounted units in brushed steel. For pricing purposes please allow for 9.nr sets, 18 in total. Units are to be wired upto the existing wiring and should be capable of being able to hold 11kgs. | PC QUANT
3 | EXISTING FIRE DOORS
A | First Floor
i | Where existing fire doors are deemed to be of sufficient construction to provide protection and can be re-utilised, the Contractor will be required to remove door leaf's to allow thorough overhaul inc repair, replacement of defective/non compliant parts, joinery repairs, intumescent sealants, decorations etc. Contractor to price in accordance with the below re-measurable quantities; | Item
ii | Door Adjustment: Contractor is to allow for easing and adjusting (likely repair method to be re-hanging doors) door to ensure that the door shuts flush with no gaps larger then 4mm to the perimeter and a compliant base gap. Fire door is to close within time frames as stated within BS 9999:2017, BS 8214:2016. Doors must not be reduced or altered on site beyond the manufacturers guidelines as this will void certification. Please refer to Appendix B for areas and photos of affected areas. • For pricing purposes allow for 9.nr doorsets to be adjusted inc overhead closers | PC QUANT
iii | Intumescent Seals: Contractor is to allow for the replacement of missing intumescent fire seals to door. Contractor is to ensure that the door has a rebate suitable for the application of new rebated intumescent fire and smoke seals (Product 68) from Envirograf or similar approved. Contractor is to allow for works to all edges of the door. All works must be undertaken in line with manufacturer recommendations and guidelines. Please refer to Appendix B. • For pricing purposes allow for 9.nr doorsets to surround of lining • For pricing purposes allow for 9.nr doorsets for install including routing of rebate to leading edge of door leaf | PC QUANT
iv | Threshold Gaps: The threshold gap must not exceed 10mm. If it is more than 10mm then a face fixed or drop down threshold seal must be fitted. Please see ironmongery schedule on intumescent & cold smoke seals Door frame New Drop Seal: Contractor is to allow for the installation of new fire rated drop seal to suit fire rating of door set to be fitted in line with manufacture’s recommendations and guidelines. All works are to be in accordance with BS EN 1154:1997 and EN 1154:1996. • For pricing purposes allow for 9.nr drop down seals, pro rata if more is required. | PC QUANT
v | Overhead Closers: Where existing overhead door closers are identified to be not correctly functioning and beyond adjustment, repair etc, Contractor to allow for renewing with new DORMA TS71 Fire Door Closer - Power Size 3-4 - Push/Pull Mounting - Silver, ensuring on completion door self closes with ease. • For pricing purposes allow for 4.nr overhead closer replacements, pro rata if more is required. | PC QUANT
vi | To the doorset between the extension and main corridor where an MDF door lining is provided, Contractor to allow for renewing with new pre-finished FD30 rated door lining set in white. Contractor to allow for carefully removing and setting aside the existing door to be re-hung inc ironmongery, hinges and furniture etc. Contractor to secure new lining to the substrate to surround of opening utilising intumescent adhesive and sealants from Envirograf, prior to hanging the existing door set. Contractor to ease and adjust, ensuring door self closes on completion, review all gaps to surround ensuring no more than 4mm to the leading edge and head, 10mm to bottom where drop down provided/4mm without dropdown. Contractor to make good surround on completion. | Item
vii | Where provided Contractor to allow for isolated and reconnecting existing hold open's ensuring correct operation on completion. | Item
B | Ground Floor
i | Where existing fire doors are deemed to be of sufficient construction to provide protection and can be re-utilised, the Contractor will be required to remove door leaf's to allow thorough overhaul inc repair, replacement of defective/non compliant parts, joinery repairs, intumescent sealants, decorations etc. Contractor to price in accordance with the below re-measurable quantities; | Item
ii | Door Adjustment: Contractor is to allow for easing and adjusting (likely repair method to be re-hanging doors) door to ensure that the door shuts flush with no gaps larger then 4mm to the perimeter and a compliant base gap. Fire door is to close within time frames as stated within BS 9999:2017, BS 8214:2016. Doors must not be reduced or altered on site beyond the manufacturers guidelines as this will void certification. Please refer to Appendix B for areas and photos of affected areas. • For pricing purposes allow for 5.nr doorsets to be adjusted inc overhead closers | PC QUANT
iii | Intumescent Seals: Contractor is to allow for the replacement of missing intumescent fire seals to door. Contractor is to ensure that the door has a rebate suitable for the application of new rebated intumescent fire and smoke seals (Product 68) from Envirograf or similar approved. Contractor is to allow for works to all edges of the door. All works must be undertaken in line with manufacturer recommendations and guidelines. Please refer to Appendix B. • For pricing purposes allow for 5.nr doorsets to surround of lining • For pricing purposes allow for 5.nr doorsets for install including routing of rebate to leading edge of door leaf | PC QUANT
iv | Threshold Gaps: The threshold gap must not exceed 10mm. If it is more than 10mm then a face fixed or drop down threshold seal must be fitted. Please see ironmongery schedule on intumescent & cold smoke seals Door frame New Drop Seal: Contractor is to allow for the installation of new fire rated drop seal to suit fire rating of door set to be fitted in line with manufacture’s recommendations and guidelines. All works are to be in accordance with BS EN 1154:1997 and EN 1154:1996. • For pricing purposes allow for 5.nr drop down seals, pro rata if more is required. | PC QUANT
v | Overhead Closers: Where existing overhead door closers are identified to be not correctly functioning and beyond adjustment, repair etc, Contractor to allow for renewing with new DORMA TS71 Fire Door Closer - Power Size 3-4 - Push/Pull Mounting - Silver, ensuring on completion door self closes with ease. • For pricing purposes allow for 2.nr overhead closer replacements, pro rata if more is required. | PC QUANT
vi | Where provided Contractor to allow for isolated and reconnecting existing hold open's ensuring correct operation on completion. | Item
4 | FIRE COMPARTMENTATION WORKS
A | To the end of the First Floor and Ground Floor corridors in 2.nr locations and First Floor Group Room where door and a half leaf's are to be renewed with a single leaf, as per appended drawings, Contractor to allow for installing plasterboard infill to provide 30 minutes compartmentation. Contactor to construct side partition utilising 48mm MF studs, head and sole plates, with 1.nr layer of 12.5mm Fireline board either side and 50mm isover insulation between. On completion tape and joint, rub down, ready to receive decoration specified elsewhere. Allow for 3.nr to be adapted back to single doors. | PC QUANT
B | To the First Floor Hall where redundant non-fire rated door is provided to the flank wall leading onto small set of stairs, as per appended drawings, Contractor to allow for installing plasterboard infill to provide 30 minutes compartmentation. Contactor to construct infill partition utilising 48mm MF studs, head and sole plates, with 1.nr layer of 12.5mm Fireline board either side and 50mm isover insulation between. On completion tape and joint, rub down, ready to receive decoration specified elsewhere. | Item
C | Where non-fire rated bulkheads are provided to fire doors such as to the Ground Floor corridor where Georgian wire glazing provided, as per the appended drawing, the Contractor will be required to allow for installing plasterboard infill to provide 30 minutes compartmentation. Contactor to construct infill partition utilising 48mm MF studs, head and sole plates, with 1.nr layer of 12.5mm Fireline board either side and 50mm isover insulation between. On completion tape and joint, rub down, ready to receive decoration specified elsewhere. Contractor to allow for 5.nr locations. | PC QUANT
D | Contractor to allow Provisional Sum for any firestopping remedials to be undertaken (above and beyond firestopping to the surround of linings and new door sets etc) to be instructed by the CA. | PROV SUM | 1500
E | Replacement of Shutter to Canteen
i | To the existing serving hatch to Canteen, the Contractor is to design and install new 30 minute fire rated steel roller shutter with powder coated finish in white, to BS EN 16034 and BS EN 13241, inclusive of channel guides and t shaped bottom rail. New unit to include motor and surface mounted key switch incorporating battery backup pack, fixed to the wall within the Kitchen. | Item
ii | Contractor to provide new small power supply protected in surface mounted steel conduit from the nearest circuit providing fused spur at high level, suitable to operate the new shutter in accordance with the manufacturers requirements. | Item
iii | In relation to the new powered shutter to serving hatch to Canteen, Contractor needs to allow for appointing the schools incumbent fire alarm contractor, CRL Security , in relation to patching into the fire alarm system so that in the event of alarm being raised the shutters will automatically shut. Contractor to allow for the incumbents appended quote plus OHP for appointing/managing them. | Item
6 | MISCELLANEOUS
A | Contractor to allow for a builders clean and sparkle clean on completion of all working areas and external areas to ensure that sufficient cleanliness is provided at handover to the Client. Contractor to also allow for thorough clean of all associated external areas in relation to site setup/access on completion. Contractor to make good all soft and hardstandings following dismantling of access and site setup to ensure in the same condition as prior to works undertaken. | Item
On completion of all works the Contractor is to make good all surrounding/landscaped areas such as existing surfaces so that areas are left tidy and presentable on completion.
Note: It is advised that the Contractor undertakes a Schedule of Condition prior to commencing works to use a reference at a later date.
B | In relation to the existing door access controls provided to the external gates, Contractor needs to allow for appointing the schools incumbent fire alarm contractor, Failsafe Alarms , in relation to patching into the fire alarm system so that in the event of activating the gates release to allow evacuation to the Muster Point. Contractor to allow for the incumbents appended quote plus OHP for appointing/managing them. | Item
C | Contractor to allow for the Contingency Sum to be expended by the Contract Administrator. | PROV | 2500
3 | SCHEDULE OF WORKS |  | £
SUMMARY
1 | STRIP OUT
2 | NEW FIRE DOORS
3 | EXISTING FIRE DOORS
4 | FIRE COMPARTMENTATION WORKS
5 | MISCELLANEOUS
MALMESBURY SOW TOTAL
TENDER PRICING SUMMARY
1 | Preliminaries
2 | Schedule of Works (BOTH SCHOOLS COMBINED)
TOTAL