## GENERAL
Merton Park Primary School, LB of Merton
Fire Alarm Replacement
Contractor Pricing Document
Note: Contractor to note that the Schedule of Works, drawings and appendices take precedence over the descriptions provided in this document and as such these should be priced. This document has been provided in editable format to make it easier for the contractor to insert their costs.
Ref Nr | Item/Description | Item/PC | Cost (£)
Section 1 | Preliminaries
Section 2 | Schedule of Works |  | (price within breakdown below)
A
1 | GENERAL
A | Works relate to the fire alarm replacement works to be undertaken at Merton Park Primary School, on behalf of the London Borough of Merton. Works largely involve the replacement of the fire alarm system with a new Level 2 wireless system in order to improve detection and means of warning for improved evacuation. Works are expected to largely take place over the summer holidays 2025 when limited number of pupils will be onsite for summer camp.
Note: Where Named Sub-Contractors have been included, the Main Contractor is to allow for appointing them, referring back to their appended quotes, in addition to managing them throughout the process, attendance and OHP. This will include all engagement, formalising appointment, liaising with them throughout the process and through to completion of works.
Works will largely involve a small number of different trades. It is assumed that Main Contractors pricing these works will have their own internal specialist trades.
The Contractor is to note that works are expected to commence by the 11th August and complete by the 29th August 2025 prior to new school term commencing. Works post the 2nd September will need to be competed by the Contractor outside of normal working hours (post 3.30pm/Weekends) following term commencing on the 3rd September. As there will be holiday clubs present over the summer break all employees inc regular visitors to site must hold valid enhanced DBS Certificates, with proof being provided with tender submission. Failure to provide will result in tender returns being voided.
If this is not possible the Contractor is to provide an alternative achieve programme with their tender return clearly stating the programme length and any long lead-in items which may impact on this being achieved. Likewise if the Contractor believes they are able to complete within a quicker timeframe they should confirm this on the Tender Form and covering letter.
Contractor to allow for developing a sufficient Construction Phase Plan in order for the works to be executed in a safe and professional manner. The Contractor will need to allow for making safe the working areas and compound through use of herras fencing and barriers. Contractor to allow for liaising closely with the site managers of each site on a daily basis. Given scope of works it is assumed that either a floating site supervisor or working foreman will be employed.
The Contractor will need to allow for acting as Principal Contractor under the CDM Regulations 2015 and must allow for this within their pricing. Given timescales for the project it is anticipated that works will NOT be notifiable to the HSE. ` It is paramount that the Contractor allows for developing a sufficient Construction Phase Plan for the works to be executed in a safe and professional manner.
Services
B | The Contractor will be provided access to the sites water and electrical supply. Meter readings will be taken on the day of works commencing and on completion of works. Although energy will be FoC to the Contractor they will be responsible for utilising efficiently. | Item
Protection
C | All site personnel to wear appropriate PPE and the Contractor is to make an allowance for site protection / access restriction as identified by site RAMS. | Item
D | Waste Materials
| Remove all rubbish and debris from the site from time to time as it accumulates and at the completion of the contract. Leave the site neat and tidy to the satisfaction of the Contract Administrator. A skip may be placed on site in addition to a compound area, in a location to be agreed with the Contract Administrator. | Item
Cleaning
E | The Contractor is expected to leave works areas particularly external areas clean and tidy upon completion of each day’s work. Contactor to lay protection to working areas and where doors are transported across. Providing partial cover over flooring will NOT be acceptable. The Contractor is deemed to have included projection within costs. | Item
Parking/ Storage
F | The Contractor will be provided with the area highlighted on the appended logistics plan, although this may reduce once he school staff arrive on-site towards the end of August. No parking will be allowed on site from the 1st September during normal working hours. The surrounding roads to each site are largely restricted. No parking costs incurred on these roads will be reimbursed to contractors or subcontractors. The Contractor must not block vehicles movements or fire escapes at any time and must move their vehicles as necessary upon any reasonable request from the Client, other contractors or maintenance teams working on site. | Item
Access
G | The site is located in residential area of Morden in South London, with major roads and public transport network within close vicinity. The Contractor is to undertake a full photographic record at both sites of the site access, delivery and communal areas, including the route to the work site and submit to the Contract Administrator prior to commencement. | Item
Contractor to allow for developing a sufficient Construction Phase Plan in order for the works to be executed in a safe and professional manner. The Contractor will need to allow for making safe the site from the adjacent school site through use of herras fencing. Contractor to allow for liaising closely with the site manager of the adjacent school site during the school term.
The Contractor will be responsible for developing the Construction Phase Plan following appointment to detail how they will safely execute the works and manage the site.
Note: As such it is paramount that the Contractor ensures the access into the site is not obstructed at any time during the course of the works.
Note: The end-user will NOT be expected to take deliveries on behalf of the Contractor.
Handover Documents
H | The Contractor must collate all required Handover Documentation as the work proceeds, submitting to the Contract Administrator all information requested by McBains by the completion date to enable Practical Completion to be issued. | Item
| Working Hours | Item
I | As previously detailed, given the Client’s requirements for works to be completed by the 5th September and school term commencing on the 3rd September, the Contractor must allow for OOH working from the 3rd September.
Normal working hours are expected to be Monday to Friday 7.30am – 6.00pm. It is expected that the Contractor will be given keys to access the working areas/site and as such will be responsible for locking up at the end of each working day.
With regards to noisy works the Contractor will need to undertake within normal working hours Monday to Friday to ensure no disruption to adjoining properties at weekends.
Welfare Facilities
J | The Contractor will be provided with a designated toilet and breakout space within the school for their use. Note. A condition survey of the working areas will be undertaken prior to commencement by the CA for agreement by the Main Contractor, which will be reviewed on completion. Should any damage be identified the Main Contractor will be responsible for rectifying back to the condition prior to works commencing. | Item
Note: The Contractor is expected to develop the site logistics plan at tender return stage. This is to ensure that a practical and acceptable approach is provided.
The Contractor will be able to make use of existing services on site but will however be responsible for making all connections and ensuring these have been carried out safely (no trip hazards etc).
Health and Safety
K | It is considered that due to the nature of the works and anticipated contract period these works will NOT be notifiable under the CDM Regulations 2015. As such the Contractor is to allow for providing all necessary information for the compilation of the Health and Safety Folder, in addition to providing a Construction Health and Safety Plan to the satisfaction of the Principal Designer prior to works starting on site. The Contractor is to review any existing building plans/health & safety documentation prior to starting the works. Asbestos information has been appended to the tender documents. A Pre-Construction Information Document will be issued to all tendering Contractors during the tender period. | Item
During the Construction phase and as works progress, the Contractor is expected to act as Principal Contractor and supply all required method statements/obtain from sub-contractors where applicable, to the satisfaction of the Principal Designer, including collation of information from the named underpinning sub-contractor. The Principal Contractor will be responsible for amending their Construction Phase Plan if required during the progress of works and the collation and submission of Health & Safety File on completion of the works to the satisfaction of the Principal Designer. The Principal Designer will be responsible for issuing all F10 notices to the HSE and distributing to all relevant parties.
The Contractor will also be responsible for closing out the requirements under the Building Safety Act although this is envisaged to be limited following sign off from our internal BSA PD at prior to tender stage. Contractor will need to allow for closely liaising with the BCO in order to satisfy requirements.
Security
L | The Contractor shall ensure that the building is left secure at all times. Should there be any security issues during the scheme the Contractor should notify the Client. | Item
The Contractor will be responsible for ensuring the site/compound is secure throughout the duration of the works, including buildings where welfare/storage is provided and will be responsible for any loss of materials from site. As such it is advised that materials/items of value be brought to site on day of install etc.
Note: The Client will not be responsible for any loss or damage caused where utilising existing buildings for these purposes.
Preliminaries
M | Allow here for all contractors’ preliminary costs for undertaking these works. Please append a breakdown to reflect breakdown in terms of site management, contracts management, H&S supervision, welfare, IT, allowance for consumables etc. | Item
Qualifications
N | Main Contractors must be able to demonstrate experience of installing fire doors within the education sector, in addition to their registration to a relevant fire door accreditation schemes, where such schemes are available such as CERTIFIRE, BRE Certification, BWF and BM TRADA, as an installer and provide conformity certificate on completion. | Item
Sub Total | Section 1 Preliminaries | £

## HOLLYMOUNT
Merton Park Primary School, LB of Merton
Fire Alarm Replacement
Contractor Pricing Document
Note: Contractor to note that the Schedule of Works, drawings and appendices take precedence over the descriptions provided in this document and as such these should be priced. This document has been provided in editable format to make it easier for the contractor to insert their costs.
Ref Nr | Item/Description | Item/PC | Cost (£)
Section 1 | Preliminaries
Section 2 | Schedule of Works |  | (price within breakdown below)
1 | STRIP OUT
i | Prior to works commencing the Contractor is to allow for isolating all services to the working areas to minimise hazards. | Item
ii | Following suitable access being provided, Contractor is to allow for stripping and disposing of all existing equipment inc control panel and cabling including containment, ensuring that minimal damage is caused to adjoining surfaces. Any resulting damage to be made good by the Contractor at their own expense inc touching up decorations to match existing finish. | Item
iii | A copy of the Asbestos Register has been included within the tender pack. It not believed that any asbestos will be present behind door linings however for the avoidance of doubt, should sampling and any subsequent asbestos removal be required, the CA will instruct utilising PC SUM. Contractor to allow for the following Provisional Sum as part of their submission. | PC SUM | 2000
2 | DECORATIONS
A | In relation to the new CCTV cameras being installed and following removal of existing, Contractor to allow for making good any affected surfaces including where decorated to ensure acceptable finish is provided on completion. | Item
3 | MEP
A | The Contractor is responsible for the design, install and commissioning of a new addressable wireless L2 fire alarm system in order to provide a compliant and appropriate level of detection/warning to meet the end-users requirements and facilitate the build, as detailed within the proposed drawings. The new system must be compliant with BS 5839-1. This will include but not be limited to the following system; | Item
New small power and adaptions to existing small power infrastructure to suit new layout
New small power and data installations in relation to the new door access controls to be provided to the Main Reception lobby doors
Works are to be undertaken in accordance with the following standard clauses;
General Electrical Clauses
• Electrical work is to be carried out by a suitably qualified Electrical Engineer to comply with the Current edition of the IEE Regulations and BS7671:2001 • The Contractor is to allow to produce Record Drawings to record the new installations and alterations • Allow to provide Maintenance details for the Health and Safety File • Allow for all necessary fire stopping for new service runs • Allow for all required and necessary BWIC with regards to MEP works • All new electrical fittings to be supplied by either MK Electrics or Crabtree • All new electrical wiring and outlets to be surface mounted in plastic conduit for ease with flush surface fixings (power outlets/light switches etc) to be provided • In accordance with Building Bulletin’s and DFE design guidance including but not limited to the following; • Technical Annex 2G – Electrical Services, Communication, Fire and Security, Version 9
B | Following strip out of the existing fire alarm system, the Main Contractor will be required to design, supply and install a new L2 addressable wireless fire alarm system to the main building. Contractor will be responsible for developing the drawing appended to the tender pack which reflects the additional rooms to be provided with manual call points and means of detection/sounders in accordance with the recent Fire Risk Assessment provided by Standby Fire Protection This will ensure suitable means of coverage is provided to conform with BS 5839-1. For pricing purposes Contractor should price on the basis of the below itemised breakdown; | Item
i | Electrical adaptions inc new supplies in connection with new control panel, to be sited in the same location as existing, in addition to fused spurs etc as deemed required by the Main Contractor as part of the design element, to BS7671: 2018. | Item
ii | New 1 loop fire alarm addressable control panel inc of battery back-up power cell, transponder, expander, relay unit. Control panel to be suitable for taking upto 20 programmable zones, EN54 compliant and have a USB interface. | Item
iii | Supply and install of new steel conduit where cabling is exposed/surface mounted and cannot be run through voids to the main panel. | Item
iv | New wireless smoke and sounder detectors inc base and device power cell | Item
v | New wireless heat detectors inc base and device power cell | Item
vi | New wireless manual call points with resettable capability, hinged cover and power cell | Item
vii | New wireless VAD detector unit inc base and device power cell to each disabled WC | Item
viii | Blank off old bells from the current system | Item
ix | Provision of new fire alarm zonal plan to be provided within wall mounted frame adjacent to panel location | Item
x | Contractor to allow for installation of fire alarm interfaces and connection to 3rd party devices, such as; fire door hold backs, access control, MCP control panel, fans | Item
xi | Contractor to allow for all BWIC with the electrical works inc new data runs, such as penetrations, sleeving, any excavations in relation new power supplies, firestopping, sealants etc in order to complete the works to an acceptable and compliant standard. | Item
xii | On completion Contractor to allow for successfully commissioning the new system and providing a demonstration to the school and CA, including providing clear instructions for the school to refer back to. | Item
xiii | As part of the Main Contractors duties under CDM Regulations, O&M's inc H&S file to be provided on completing of the works, detailing works undertaken, maintenance regime, warranties, product data sheets, details of supply chain involved etc and any residual risks. Digital copy will be acceptable but a hard copy manual for the new panel and system should be provided. | Item
C | Should any electrical upgrades be required as part of the works Contractor to allow Provisional Sum to be expended by the CA. | PC SUM | 2000
D | Contractor to allow for firestopping around all penetrations be it existing and/or new, utilising intumescent mastic such as Product 58 from Envirograf. | Item
E | Should any further fire stopping above and beyond the above scope be required Contractor to allow Provisional Sum to be expended by the CA. | PC SUM | 1000
4 | MISCELLANEOUS
A | Contractor to allow for a builders clean and sparkle clean on completion of all working areas and external areas to ensure that sufficient cleanliness is provided at handover to the Client. Contractor to also allow for thorough clean of all associated external areas in relation to site setup/access on completion. Contractor to make good all soft and hardstandings following dismantling of access and site setup to ensure in the same condition as prior to works undertaken. | Item
On completion of all works the Contractor is to make good all surrounding/landscaped areas such as existing surfaces so that areas are left tidy and presentable on completion.
Note: It is advised that the Contractor undertakes a Schedule of Condition prior to commencing works to use a reference at a later date.
B | Contractor to allow for the Contingency Sum to be expended by the Contract Administrator. | PROV | 3000
2 | SCHEDULE OF WORKS |  | £
SUMMARY
1 | STRIP OUT
2 | DECORATIONS
3 | MEP
4 | MISCELLANEOUS
2 | MERTON PARK SOW TOTAL

## SUMMARY
Merton Park Primary School
Fire Alarm Replacement
Contractor Pricing Document
| PRICING SUMMARY | £
1 | Preliminaries
2 | Merton Park Primary School Schedule of Works
TOTAL