100

Roof Renewal

4 & 5 Highbury Road

Brandon

Schedule A.1

Specification & Schedule of Works

File Ref: PRJ000054

July 2025

| 1.0 1.1 1.2 1.3 1.4 1.5 1.6 1.7 1.8 1.9 1.10 1.11 2.0 2.1 2.2 2.3 2.4 3.0 3.1 3.2 3.3 3.4 3.5 3.6 4.0 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 4.10 4.11 4.12 4.13 4.14 4.15 4.16 4.17 4.18 4.19 5.0 5.1 5.2 5.3 5.4 5.5 5.6 5.7 5.8 5.9 5.10 6.0 6.1 6.2 | Description of Works To 2 no. vacant industrial units: Replacement of existing built-up double skin asbestos-cement roof covering, trims, gutters, downpipes and rooflights with new composite insulated panels, rooflights and valley gutter systems. Including safe disposal of all asbestos containing materials from site. Installation of single skin cladding to elevations at gable ends and insulated composite panel cladding plus single sheet profile to centre of elevations at gable ends. The works and finishes are generally to replicate that of the external fabric upgrade works to Units 1-3 Highbury Road, undertaken in 2019 and 2021. Also refer to attached documents: Invitation to Tender Annex 1 – Tender Drawings: as shown on the drawing issue sheet Annex 2 – Preliminaries Annex 3 – Asbestos Survey Annex 4 – Pre-Construction Information (to follow) Annex 5 – Safety and Environmental Requirements Annex 6 – Drainage Survey (to follow) Annex 7 – Brett Martin Xlok Ultra Standard Details Annex 8 – DigDat & UKPN Plans Annex 9 – Structural Information (to follow) Schedule A.2 Tender Schedule -A copy of the Council’s Standard Terms and Conditions may be downloaded from: http://www.westsuffolk.gov.uk/Business/Selling_to_the_Council/ index.cfm?aud=business General Conditions Supply all documentation relating to Construction (Design & Management) Regulations 2015 prior to commencement on site, including site specific Risk Assessments and Method Statements to the Contract Administrator for approval. Attention is drawn to the Council’s Safety and Environmental requirements for Contractors and Sub-contractors (included within tender package). The contractor is to provide all relevant warranty certificates under the name of ‘West Suffolk Council’. The method statement and programme are to ensure that internal elements are not exposed for longer than necessary. Allow for providing safe system of work and access to the roof i.e. nets, edge protection handrails, MEWP’s, Youngmans, scaffolding as determined by the risk assessment and for removal from site on completion. The contractor will be responsible for inspection and certification of scaffolding, with tags remaining in date for duration of works. Netting is to comprise of mansafe nets with additional debris netting on top. N.B. adjoining units will remain occupied and operational, and temporary works are to include mansafe and debris netting to underside of single roof slope adjoining Unit 3 and 6 valley gutters. Power will be available for use of the contractor on site. Water will NOT be available to the Contractor on site. The Contractor is to provide toilet and mess facilities. The Contractor will be responsible for keeping these facilities clean and tidy and stocked with consumables. Toilet facilities within the Units will NOT be available for use of the contractor on site. It is a mandatory requirement that the contractor attends site prior to tender submission to fully appreciate the extent of the works required and site constraints. See Invitation to Tender document for further information. Allow for providing safe system of protection for the public and for compound area as determined by the risk assessment and for the removal from site on completion. Fencing is to be a minimum of 1.8m high Heras type and is to remain for the duration of the works to the specified areas with appropriate signage securely affixed. Skips are to be secured when not in use. N.B. Existing yards to the rear of the units are fenced and gates can be made secure- for siting of toilet/mess facilities/materials etc. The contractor will be responsible for identifying all underground services in accordance with the risk assessments, prior to any excavation works. Refer also to DigDat/UKPN plans attached. The contractor will be responsible for measurement of all materials prior to ordering. The works are subject to Local Authority Building Control approval and the Contractor will be required to make the site available and arrange for inspections with West Suffolk Building Control at the relevant stages. (Building Regulations Application to be submitted by client). Contact details for WSC Building Control will be provided by the client. Where possible and safe to do so, waste materials are to be separated, crushed and re-used/recycled. Allow for any other contractor obligations as described in Annex 2 – Preliminaries Allow for any other contractor obligations as described in Annex 4 – Pre-Construction Information (to follow) CARRIED TO SUMMARY Asbestos Removal Practices Referring to the existing Asbestos R/D surveys, allow for the removal of asbestos containing materials. The work below shall be carried out in accordance with HSE guidelines and comprises of Licensed and Non-Licensed asbestos work. Licensable work must be notified to the enforcing authority and carried out by a Licensed Contractor. Notifiable Non-Licensed work must be notified to the enforcing authority. All waste cleared from site must be in licenced skips to authorised waste landfill sites. On completion of the removal works, a licensed contractor is to be employed to vacuum (Type H) clean all remaining debris from the unit, including high level ledges, ceilings, and purlins. Provide the client with evidence of this appointment and the relevant waste consignment notes. On completion, carry out a reassurance air test for each unit which shall be taken by an independent UKAS registered specialist, and the results handed to the client, together with copies of all waste transfer and disposal notices. CARRIED TO SUMMARY External Cladding (CONTRACTORS DESIGN PORTION) Remove and dispose of existing single skin metal cladding, metal/plasterboard built-up cladding and asbestos-cement soffits at high-level gable end walls of North and South elevations. Allow for removal and reinstatement of timber cladding to facilitate removal of AC soffits to North elevation. Supply and install Foreclad 200- F200W single skin steel cladding sheets 0.5mm thick, plastisol coated Wedgewood Blue RAL 220 50 15 BS 18C37, laid vertically and fixed to lightweight steel (top hat) sections chemically fixed to external masonry. To outer face of parapet walls of North and South elevations as shown on drawing 004. Supply and install Kingspan KS1000 FC insulated wall panels, 100mm core thickness, XL Forte RAL 9002 laid vertically and fixed to existing steel framing, with Foreclad 200- F200W single skin steel cladding sheets 0.5mm thick, plastisol coated Wedgewood Blue RAL 220 50 15 BS 18C37 affixed so profiles of gable ends are consistent. To central gable ends at North and South elevations as shown on drawing 004. Incorporate corner trims (e.g. where parapets meet central gable area) and cold formed drip flashings. All Trims to match cladding, Wedgewood blue RAL 220 50 15 BS 18C37. Supply and install new soffit flashings, Wedgewood blue RAL 220 50 15 BS 18C37 to shopfronts (replacing AC soffits) and to sectional door openings at South Elevation. Allow for additional flashings to conceal full height masonry reveals at sectional door openings, Wedgewood blue RAL 220 50 15 BS 18C37. Unless otherwise noted allow to retain all existing penetrations through external walls, applying suitable seal/flashing around and designing cladding rail system to support surrounding panels and single skin sheets. CARRIED TO SUMMARY Roof (CONTRACTORS DESIGN PORTION) Remove and dispose of full roof covering build-ups to Unit 4 & 5 including; asbestos-cement corrugated roof sheets and internal linings, rooflights, gable and ridge trims, internal plastic RWPs, high level asbestos-cement cladding to internal partitions, detached AC flue and GRP over-sheeting. Allow for repairs to existing steel truss members - Straighten any bends in the existing steel frame trusses. Re-decorate all previously painted steel trusses, purlins and framing. All members coming into contact with new sheeting to be decorated prior to fixing new roof sheets. Thoroughly clean down to remove all surface contamination. Carefully scrape back to a firm edge all areas of defective paint coatings and rub down to 'feather' the broken edges. Scrape and wire brush corroded steel to produce a clean metal surface. Rub down with a suitable abrasive and *dust off. All manually prepared surfaces should be prepared to a minimum standard of St3. BS EN ISO 8501-1: 2007 at the time of coating. Prime all bare metal with: 1 coat of Dulux Trade All Purpose Primer applied to give a minimum wet film thickness of 80 microns giving a minimum dry film thickness of 40 microns. Finishing System - 2 coats of Dulux Trade Satinwood each applied to give a minimum wet film thickness of 50 microns per coat, giving a minimum dry film thickness of 25 microns per coat. Colour BS18 B 25 Merlin Grey Supply and install new Kingspan KS1000 RW composite insulated panels in XL Forte RAL 9002 to all roof slopes as shown on Dwg 004. 115mm thick core giving U-value of 0.18 W/m2k. Junctions between the roof panel system and walls / penetrations insulated with PIR board insulation any gaps filled with Premier Sealants (01724 864 100) Firefoam (class B1 rated) or similar, fire rated gun applied canister urethane insulation. Profile fillers to be Premier Sealant Systems Limited ref:M25 or similar, type to suit cladding profile. Material: MP (Metallocene polyolefin). Colour: Black. Fixing: Seal the top, bottom and sides of each profile filler with a single line of nonsetting gun-grade, PremSeal CV or similar. Locate wherever necessary to close off corrugation cavities from the inside and outside of the building. Ensure a tight fit and leave no gaps. Supply and fix 2Nr Dektite flashings to suit existing soil and vent pipe penetrations. Supply and install Brett Martin Xlok ultra non-fragile panel glazing system glazed in 25mm structured polycarbonate Class B non-fragility to ACR[M]001:2000, to areas as shown on Dwg 004. U-value min. of 1.8 W/m2k (system achieves 1.6W/m2K) Supply and fix at 450mm centres and seal with butyl rubber tape, new external flashings at ridge, change in slope (apron flashings), verge and rooflight abutment details. RAL 9002 except verge flashing to be Wedgewood blue 10C31 RAL 220 50 15 BS 18C37. Supply and fix at 450mm centres and seal with butyl rubber tape new internal flashings at gable/roof and valley/roof and change in slope abutments. Voids filled with site applied LPCB certified PIR insulation board with minor gaps filled with fire rated canister insulation. All internal trims white to match inner lining of composite roof panels. End laps to be air sealed with butyl tape or sealant. N.B. Flashings not required at ridge/ridge due to position of existing structure. Valley Gutters – to Unit 4/5 and Unit 5/6 valleys: Cut out both ends of existing valley gutter and form openings through brickwork. Fabricate and fix in place new galvanised steel extension outlet section, complete with overflow cut-out. Extension to protrude approx. 450mm beyond external wall. Supply and fix new purpose made cold formed flashings to enclose exposed ends of gutter and turn down and fix to walls below. Wedgewood blue 10C31 RAL 220 50 15 BS 18C37 Clean out 2 no. existing asbestos-cement valley gutters, insulate with 20mm thick PIR insulation and supply and fix new plygene gutter lining system complete with outlets, clips and fixings. Clean out 1 no. existing asbestos-cement plygene-lined valley gutter (Unit 3/4), check for defects and report to client. New roof coverings to be finished with an L shaped deflector flashing where it overhangs the valley gutters to divert rainwater runoff down into the gutter. RAL 9002 to match roof coverings. Upper slope Gutters - Supply and install new Kingspan Highline double sided plastisol coated steel eaves gutters sized to suit roof area complete with 2 no. outlets. Fixed to composite panels via Kingspan gutter support arms to manufacturer’s recommendations. All RAL 9002. Downpipes- Supply and install new 150mm diameter Kingspan Highline (or similar approved) PPC aluminium downpipes where shown on plans discharging to underground drains. 2 no. downpipes to North Elevation, 2 no. downpipes to South elevation, Wedgewood blue 10C31 RAL 220 50 15 BS 18C37. 4 no. downpipes (2 no. per slope) to drop from upper roof slope to lower roof slope. All RAL 9002. CARRIED TO SUMMARY Underground drainage Allow for new and alterations to existing rainwater drainage system as follows: Overflow RWPs & Overflow RWPs – 150mm underground drain with short radius bend connected to IC2 and IC3 respectively. Push fit coupling to rainwater pipes. (Downpipes noted elsewhere). IC1 – 450mm diameter inspection chamber on 100mm granular material. Selected backfill and concrete bed and surround to cover and frame. Ductile iron lid and cast iron frame (12.5T loading). 150 dia. Drain run to existing IC1. Centre line of drain min. 1.0m from front wall of the building. IC2 - 450mm diameter inspection chamber on 100mm granular material. Selected backfill and concrete bed and surround to cover and frame. Ductile iron lid and cast iron frame (12.5T loading). Drain run to new IC2. Centre line of drain min. 1.0m from front wall of the building. RWP 3 & RWP 4 - 150mm dia. Upvc underground drains with short radius bend connected to existing underground drain runs (to soakaways) with 45degree bend and flexible couplings. Push fit couplings to rainwater pipe connection. Externally cap/plug redundant sections of drain from internal rainwater pipe outlets. Supply and install new 225mm dia. Heavy duty inspection chambers (IC3 & IC4) at connections to existing drainage runs (to soakaways) retained. Loading, materials and installation as per ICs 1 & 2. 2 no. existing rainwater pipe outlets inside the building to be broken out level with internal floor level and plugged with concrete. Seal existing internal outlets with fixed galvanised steel plate and sealing compound. All below ground drainage to be 150mm internal dia. Upvc pipes with upvc couplings laid to a minimum fall of 1:80 and to be laid as in accordance with manufacturer’s specification and recommendations. Drains to be bedded on minimum 100mm depth 10mm nominal single size granular material and sidefill with similar material. Selected backfill above in 300mm layers all well compacted. Where pipes are laid under the parking area or yard space they should have concrete paving slabs laid as bridging over pipes, with at least 100mm selected material between the top of pipe and the underside of the slab. Dig will generally be in soft ground but where it passes through tarmac paths or concrete hardstanding the trench edges should be saw cut and reinstated in similar material to the same depth as existing. CARRIED TO SUMMARY Removal of waste Provide skips as required for waste materials and clear away all debris arising from the works and unused materials and dispose of to an approved site. Sweep all floor areas internally and external working area on completion. CARRIED TO SUMMARY SUMMARY - Preliminaries & General Conditions - Asbestos Removal Practices - External Cladding - Roof - Underground drainage 6.0 Removal of waste TOTAL QUOTATION SUM |  |  |  |
| --- | --- | --- | --- | --- |