REFERENCE SPECIFICATION - T1

FIRE SAFETY RECTIFICATION WORKS

Please note all past and future amendments will supersede this specification.

Table of Contents

Title	Page

C20	Demolition	4

C90	Alterations - spot items	8

F10	Brick/ block walling	9

F30	Accessories/ sundry items for brick/ block/ stone  walling	12

G20	Carpentry/ timber framing/ first fixing	13

K10	Gypsum board dry linings/ partitions/ ceilings	19

K11	Rigid sheet flooring/ sheathing/ decking/ sarking/ linings/ casings 27

K13	Rigid sheet fine linings and panelling	29

K40	Demountable suspended ceilings	30

K45	Suspended ceiling system alterations	33

L10	Windows/ Rooflights/ Screens/ Louvres	38

L20	Doors/ shutters/ hatches	42

L40	General glazing	54

M20	Plastered/ Rendered/ Roughcast coatings	56

M60	Painting/ clear finishing	60

M61	Intumescent coatings for fire protection of steelwork	69

N10	General fixtures/ furnishings/ equipment	72

N15	Internal fire and safety signage systems	73

P10	Sundry insulation/ proofing work	74

P12	Fire stopping systems	75

P20	Unframed isolated trims/ skirtings/ sundry items	79

P21	Door/ window ironmongery	80

P31	Holes, chases, covers and supports for services	89

Q20	Granular sub-bases to roads/ pavings	91

Q25	Slab/ brick/ sett/ cobble pavings	92

Q40	Fencing	93

U90	General ventilation - domestic	95

Page 2  of  111

V90	Electrical systems - domestic	97

Z10	Purpose made joinery	102

Z11	Purpose made metalwork	103

Z20	Fixings and adhesives	105

Z21	Mortars	106

Z22	Sealants	108

Z31	Powder coatings	109

Page 3  of  111

# C20 Demolition

To be read with Preliminaries/ General conditions

## GENERAL REQUIREMENTS

110	DESK STUDY/ SURVEY

- Scope: Before starting deconstruction/ demolition work, examine available information, and carry out a survey of:

  - the structure or structures to be deconstructed/ demolished, - the site on which the structure or structures stand, and - the surrounding area.

- Report and method statements: Submit, describing:

  - Form, condition and details of the structure or structures, the site, and the surrounding area. Extent: As schedule .

  - Type, location and condition of features of historical, archaeological, geological or ecological importance.

  - Type, location and condition of adjoining or surrounding premises that might be adversely affected by removal of the structure or structures, or by noise, vibration and/ or dust generated during deconstruction/ demolition.

  - Identity and location of services above and below ground, including those required for the Contractor's use, and arrangements for their disconnection and removal.

  - Form and location of flammable, toxic or hazardous materials, including lead-based paint, and proposed methods for their removal and disposal.

  - Form and location of materials identified for reuse or recycling, and proposed methods for removal and temporary storage.

  - Proposed programme of work, including sequence and methods of deconstruction/ demolition.

  - Details of specific pre-weakening required.

  - Arrangements for protection of personnel and the general public, including exclusion of unauthorized persons.

  - Arrangements for control of site transport and traffic. - Special requirements: As schedule .

- Format of report: As schedule .

120	EXTENT OF DECONSTRUCTION/ DEMOLITION

•	General: Subject to retention requirements specified elsewhere, deconstruct/ demolish structures down to levels indicated.

130	GROUNDWORKS

- Old foundations, slabs and the like: Break out in locations and to the extents stated.

- Contaminated material: Remove, and carry out remediation required by the Enforcing Authority.

150	FEATURES TO BE RETAINED

•	General: Keep in place and protect the following: As schedule.

## SERVICES AFFECTED BY DECONSTRUCTION/ DEMOLITION

210	SERVICES REGULATIONS

•	Work carried out to or affecting new and/ or existing services: Carry out in accordance with the byelaws and/ or regulations of the relevant Statutory Authority.

220	LOCATION OF SERVICES

Services affected by deconstruction/ demolition work: Locate and mark positions.

• Mains services marking: Arrange with the appropriate authorities for services to be located and marked.

- Marking standard: In accordance with National Joint Utilities Group 'Guidelines on the positioning and colour coding of underground utilities' apparatus'.

230	SERVICES DISCONNECTION ARRANGED BY CONTRACTOR

•	General: Arrange with the appropriate authorities for disconnection of services and removal of fittings and equipment owned by those authorities prior to starting deconstruction/ demolition.

232	SERVICES DISCONNECTION ARRANGED BY EMPLOYER AND CONTRACTOR

- Responsibility: The Employer will arrange with the appropriate authorities for disconnection of services and removal of fittings and equipment owned by those authorities prior to deconstruction/ demolition, as follows: Refer to schedule.

- Disconnection of remaining services: Arrange with the appropriate authorities. Remove fittings and equipment not owned by those authorities.

- Timing: Do not start deconstruction/ demolition until disconnections are completed.

240	DISCONNECTION OF DRAINS

- General: Locate, disconnect and seal disused foul and surface water drains.

- Sealing: Permanent, and within the site.

250	LIVE FOUL AND SURFACE WATER DRAINS

- Drains and associated manholes, inspection chambers, gullies, vent pipes and fittings:

  - Protect; maintain normal flow during deconstruction/ demolition.

  - Make good any damage arising from deconstruction/ demolition work.

  - Leave clean and in working order at completion of deconstruction/ demolition work.

- Other requirements: As schedule.

260	SERVICE BYPASS CONNECTIONS

- General: Provide as necessary to maintain continuity of services to occupied areas of the site on which the deconstruction/ demolition is taking place and to adjoining sites/ properties.

- Minimum notice to adjoining owners and all affected occupiers: 72 hours, if shutdown is necessary during changeover.

270	SERVICES TO BE RETAINED

- Damage to services: Give notice, and notify relevant service authorities and/ or owner/ occupier regarding damage arising from deconstruction/ demolition.

- Repairs to services: Complete as directed, and to the satisfaction of the service authority or owner.

## DECONSTRUCTION/ DEMOLITION WORK

310	WORKMANSHIP

- Standard: Demolish structures in accordance with BS 6187.

- Operatives:

  - Appropriately skilled and experienced for the type of work.

  - Holding, or in training to obtain, relevant CITB Certificates of Competence.

- Site staff responsible for supervision and control of work: Experienced in the assessment of risks involved and methods of deconstruction/ demolition to be used.

320	GAS OR VAPOUR RISKS

•	Precautions: Prevent fire and/ or explosion caused by gas and/ or vapour from tanks, pipes, etc.

330	DUST CONTROL

General: Reduce airborne dust by periodically spraying deconstruction/ demolition works with an appropriate wetting agent. Keep public roadways and footpaths clear of mud and debris.

•	Lead dust: Submit method statement for control, containment and clean-up regimes.

340	HEALTH HAZARDS

•	Precautions: Protect site operatives and general public from hazards associated with vibration, dangerous fumes and dust arising during the course of the Works.

350	ADJOINING PROPERTY

- Temporary support and protection: Provide. Maintain and alter, as necessary, as work proceeds. Do not leave unnecessary or unstable projections.

- Defects: Report immediately on discovery.

- Damage: Minimize. Repair promptly to ensure safety, stability, weather protection and security.

- Support to foundations: Do not disturb.

360	STRUCTURES TO BE RETAINED

- Extent: As schedule.

- Parts which are to be kept in place: Protect.

- Interface between retained structures and deconstruction/ demolition: Cut away and strip out with care to minimize making good.

370	PARTLY DEMOLISHED STRUCTURES

- General: Leave in a stable condition, with adequate temporary support at each stage to prevent risk of uncontrolled collapse. Make secure outside working hours.

- Temporary works: Prevent overloading due to debris.

- Access: Prevent access by unauthorized persons.

380	DANGEROUS OPENINGS

- General: Provide guarding at all times, including outside of working hours. Illuminate during hours of darkness.

- Access: Prevent access by unauthorized persons.

- ASBESTOS-CONTAINING MATERIALS – KNOWN OCCURRENCES

  - General: Materials containing asbestos are known to be present in: Refer to asbestos survey reports supplied by employer.

  - Removal: By contractor licensed by the Health and Safety Executive, and prior to other works starting in these locations.

- ASBESTOS-CONTAINING MATERIALS – UNKNOWN OCCURRENCES

  - Discovery: Give notice immediately of suspected asbestos-containing materials when discovered during deconstruction/ demolition work. Avoid disturbing such materials.

  - Removal: Submit statutory risk assessments and details of proposed methods for safe removal.

410	UNFORESEEN HAZARDS

- Discovery: Give notice immediately when hazards such as unrecorded voids, tanks, chemicals, are discovered during deconstruction/ demolition.

- Removal: Submit details of proposed methods for filling, removal, etc.

420	OPEN BASEMENTS, ETC

- Temporary support: Leave adequate buttress walls or provide temporary support to basement retaining walls up to ground level.

- Safety: Make remaining sections of retaining and buttress walls safe and secure.

- Water movement: Make holes in basement floors to allow water drainage or penetration (depending on water table). Provide a hole for every 10 m², not less than 600 mm in diameter.

430	FILLING OF BASEMENTS, ETC

Temporary support: Leave adequate buttress walls or provide temporary support to basement retaining walls up to ground level.

- Water movement: Make holes in basement floors to allow water drainage or penetration (depending on water table). Provide a hole for every 10 m², not less than 600 mm in diameter.

- Filling: Remove organic material and soil from basements and other voids. Fill and consolidate with g ranular material in accordance with local Highway Authority requirements.

442	SITE SURFACE AT COMPLETION

- Levels: Grade the site to follow the levels of adjacent areas.

- Temporary surface: Cover the site with 100 mm thick consolidated layer of crushed hard rock in areas shown on drawings.

450	SITE CONDITION AT COMPLETION

- Debris: Clear away and leave the site in a tidy condition.

- Other requirements: As schedule.

## MATERIALS ARISING

- CONTRACTOR'S PROPERTY

  - Components and materials arising from the deconstruction/ demolition work: Property of the Contractor except where otherwise provided.

  - Action: Remove from site as work proceeds where not to be reused or recycled for site use.

- EMPLOYER'S PROPERTY

  - Components and materials to remain the property of the Employer: As schedule.

  - Protection: Maintain until these items are removed by the Employer or reused in the Works, or until the end of the Contract.

  - Special requirements: As schedule.

520	RECYCLED MATERIALS

- Materials arising from deconstruction/ demolition work: Can be recycled or reused elsewhere in the project, subject to compliance with the appropriate specification and in accordance with any site waste management plan.

- Evidence of compliance: Submit full details and supporting documentation.

- Verification: Allow adequate time in programme for verification of compliance.

# C90 Alterations - spot items

## GENERAL

110	DESCRIPTIONS

•	Location of spot item descriptions: Schedule of work.

120	EMPLOYER'S PROPERTY

- Components and materials arising from alterations that are to remain the property of the Employer: A s schedule.

- Protection: Maintain until items listed above are removed by the Employer or reused in the Works, or until the end of the Contract.

- Special requirements: As schedule.

130	RECYCLED MATERIALS

- Materials arising from alterations: May be recycled or reused elsewhere in the project, subject to compliance with the appropriate specification and in accordance with any site waste management plan.

- Evidence of compliance: Submit full details and supporting documentation.

- Verification: Allow adequate time in programme for verification of compliance.

# F10 Brick/ block walling

5	FACING BRICKWORK ABOVE DPC

- Bricks: To BS EN 771-1.

  - Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

  - Recycled content: Contractor's choice. - Special shapes: None.

- Mortar: As section Z21.

  - Standard: Not applicable.

  - Mix: 1:1:6 cement:lime:sand.

- Bond: To match existing.

- Joints: To match existing.

18	CONCRETE FACING BLOCKWORK ABOVE DPC

- Blocks: To BS EN 771-3.

  - Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

  - Configuration: Group 1.

  - Compressive strength: Not applicable.

Category: I.

  - Freeze/ thaw resistance: Not applicable.

  - Recycled content: Contractor's choice.

  - Work sizes (length x width x height): 440 x 100 x 215 mm.

Tolerance category: D1.

  - Finish/ colour: Riven.

  - Special shapes: As schedule.

  - Additional requirements: None.

- Mortar: As section Z21.

  - Standard: Not applicable.

  - Mix: 1:1:6 cement:lime:sand.

- Bond: To match existing.

- Joints: To match existing.

- Features: None.

33	CLAY COMMON BRICKWORK ABOVE DPC

- Bricks: To BS EN 771-1.

  - Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

  - Size: 215 x 102 x 65 mm.

  - Mean compressive strength (minimum): Not required.

  - Category: Not required.

  - Durability designation: F2.

  - Density: Not applicable.

  - Water absorption: Not applicable.

  - Configuration: Frogged.

  - Recycled content: Contractor's choice. - Additional requirements: None.

- Mortar: As section Z21.

  - Standard: Not applicable.

  - Mix: 1:1:6 cement:lime:sand.

- Bond: To match existing.

36	CONCRETE COMMON BLOCKWORK AS SCHEDULE

- Blocks: To BS EN 771-3.

  - Manufacturer: Contractor's choice.

  - Product reference: Contractor's choice.

  - Configuration: Group 1.

  - Compressive strength: Not applicable.

  - Category: I.

  - Freeze/ thaw resistance: Not applicable.

  - Thermal properties: Not applicable.

  - Recycled content: Contractor's choice.

  - Work sizes (length x width x height): 440 x 100 x 215  mm. Tolerance category: D1.

  - Special shapes: None.

  - Additional requirements: None.

- Mortar: As section Z21.

  - Standard: Not applicable.

  - Mix: 1:1:6 cement:lime:sand.

- Bond: To match existing.

45	ENGINEERING BRICKWORK AS SCHEDULE

- Bricks: To BS EN 771-1.

  - Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

  - Mean compressive strength: Greater than or equal to 75 N/mm².

  - Category: I.

  - Water absorption: Equal to or less than 7.5%.

  - Freeze/ thaw category: F2.

  - Active soluble salts content category: S2. - Additional requirements: None.

- Mortar: As section Z21.

  - Standard: Not applicable.

  - Mix: 1:¼:3 cement:lime:sand.

  - Additional requirements: None.

- Bond: To match existing.

- Joints: Flush.

51	BASIC WORKMANSHIP

- Bond where not specified: Half lap stretcher.

- Mortar joints: Fill all vertical joints. Lay bricks, solid and cellular blocks on a full bed.

- AAC block thin mortar adhesive and gypsum block adhesive joints: Fill vertical joints. Lay blocks on a full bed.

- Clay block joints:

  - Thin layer mortar: Lay blocks on a full bed. - Interlocking perpends: Butted.

- Quoins and advance work: Rack back.

- Locations for equal levelling of cavity wall leaves:

  - Every course containing vertical twist type ties or other rigid ties.

  - Every third tie course for double triangle/ butterfly ties. - Courses in which lintels are to be bedded.

- Lift height (maximum) for walling using cement gauged or hydraulic lime mortar: 1.2 m above any other part of work at any time.

- Daily lift height (maximum) for walling using cement gauged or hydraulic lime mortar: 1.5 m for any one leaf.

- Lift height (maximum) for walling using thin layer mortar: 1.3 m above any other part of work at any time.

55	FACEWORK

- Commencement of facework: Not less than 150 mm below finished level of adjoining ground or external works level.

- Brick/ block selection: Do not use units with damaged faces or arrises.

- Cut masonry units: Where cut faces or edges are exposed cut with table masonry saw.

- Coursing brickwork and concrete blockwork: Evenly spaced using gauge rods. To produce satisfactory junctions and joints with built-in elements and components.

60	ALTERATIONS/ EXTENSIONS

- Coursing: Line up with existing work.

- Block bonding new walls to existing: Unless agreed otherwise cut pocket requirements as follows: - Width: Full thickness of new wall.

  - Depth (minimum): 100 mm.

  - Vertical spacing: As follows:

  - Brick to brick: 4 courses high at 8 course centres.

  - Block to block: Every other course.

  - Pocket joints: Fully filled with mortar.

- New and existing facework in the same plane: Bonded together at every course to achieve continuity of bond and coursing.

- Support of existing work: Fully consolidate joint above inserted lintel or masonry with semidry mortar to support existing structure.

66	FIRE STOPPING

• Avoidance of fire and smoke penetration: Fit tightly between cavity barriers and masonry. Leave no gaps.

90	CRACKED BRICKS IN EXISTING FACEWORK

- Replacement: Prior to repointing adjacent cracked joints, cut out and replace with matching sound bricks to approval.

- Jointing mortar: As section Z21. - Standard: Not applicable.

- Mix: 1:1:6 cement:lime:sand.

95	REPOINTING

- Preparation: Cut out joints to form a rectangular recess of 15-20 mm depth. Clean and dampen joints sufficiently to control suction.

- Joint profile: To match existing .

- Mortar: As section Z21.

  - Standard: Not applicable.

  - Mix: 1:1:6 cement:lime:sand.

# F30 Accessories/ sundry items for brick/ block/ stone  walling

5	CAVITIES

- Concrete fill to base of cavity:

- Concrete generally: To BS EN 206 and BS 8500-2.

- Concrete type: Designated GEN1 or Standardized prescribed ST2 mix with high workability.

  - Extent: Maintain 75 mm between top of fill and external ground level and a minimum of 225 mm between top of fill and ground level dpc.

- Cleanliness: Keep cavity faces, ties and dpcs free from mortar and debris.

24A	CAVITY WALL TIES

- Standard: To BS EN 845-1.

- Manufacturer: Ancon.

  - Product reference: Ancon Double Triangle Wall Tie

- Length: 150 - 300 mm.

- Material: Stainless steel grade 1.4301 (304) •	Embedment length (minimum): 50 mm.

28	FIXING TIES IN MASONRY CAVITY WALLS •	Embedment in mortar beds (minimum): 50 mm.

- Placement: Sloping slightly downwards towards outer leaf without bending. Drip centred in the cavity and pointing downwards.

- Spacing: Staggered in alternate courses. - Horizontal centres: 900 mm . - Vertical centres: 450 mm .

- Provision of additional ties: Within 225 mm of reveals of unbonded openings and at the vertical reveals of unsupported masonry at not more than 300 mm centres vertically.

# G20 Carpentry/ timber framing/ first fixing

To be read with Preliminaries/ General conditions.

## GENERAL

105	TIMBER PROCUREMENT

- Timber (including timber for wood based products): Obtained from well managed forests/ plantations in accordance with:

  - The laws governing forest management in the producer country or countries.

  - International agreements such as the Convention on International Trade in Endangered Species of wild fauna and flora (CITES).

- Documentation: Provide either:

  - Documentary evidence (which has been or can be independently verified) regarding the provenance of all timber supplied, or

  - Evidence that suppliers have adopted and are implementing a formal environmental purchasing policy for timber and wood-based products.

- Certification scheme: Forest Stewardship Council (FSA). - Other evidence: None.

120	STRUCTURAL DESIGN PROVIDED

- Description: To be provided by employer where required.

- Requirements:

- Generally: As section B50/B51. - Additional requirements: None.

150	STRENGTH GRADING OF TIMBER

•	Grader: A company currently registered under a third party quality assurance scheme operated by a certification body approved by the UK Timber Grading Committee.

160	GRADING AND MARKING OF SOFTWOOD

- Timber of a target/ finished thickness less than 100 mm and not specified for wet exposure: Graded at an average moisture content not exceeding 20% with no reading being in excess of 24% and clearly marked as 'DG'.

- Timber wet graded and specified for installation at higher moisture contents: Graded at an average moisture content above 20% and unmarked.

- Structural timber members cut from large graded sections: Regraded to approval and marked accordingly.

## PRODUCTS

210	STRUCTURAL SOFTWOOD (GRADED DIRECT TO STRENGTH CLASS) AS SCHEDULE

- Grading standard: To, BS EN 14081-1 and BS 4978, or other suitable national equivalent and so marked.

- Strength class to BS EN 338: C16 unless otherwise stated.

- Treatment:

  - Preservative treatment: (Refer to schedule for requirement) Organic solvent impregnation to NBS section Z12 and Wood Protection Association Commodity Specification C8. Design service life: 40 years.

  - Flame retardant treatment: As schedule.

230	STRUCTURAL SOFTWOOD (STRENGTH CLASS NOT SPECIFIED) AS SCHEDULE

Species: Submit proposals.

- Grading standard: To the appropriate BS EN 14081-1-compliant standard. - Grade: GS to BS 4978.

- Treatment:

  - Preservative treatment: (Refer to schedule for requirement) Organic solvent impregnation to NBS section Z12 and Wood Protection Association Commodity Specification C8. Design service life: 40 years.

  - Flame retardant treatment: As schedule.

250	STRUCTURAL HARDWOOD (GRADED DIRECT TO STRENGTH CLASS) AS SCHEDULE

- Grading standard: To BS EN 14081-1 and BS 5756, or other suitable national standard and so marked.

- Strength class to BS EN 338: As schedule.

- Surface finish: Planed all round.

- Treatment:

  - Preservative treatment: (Refer to schedule for requirement) Organic solvent impregnation to NBS section Z12 and Wood.

Design service life: 40 years.

  - Flame retardant treatment: As schedule.

260	STRUCTURAL HARDWOOD (STRENGTH CLASS NOT SPECIFIED) AS SCHEDULE

- Species: Submit proposals.

- Grading standard: To the appropriate BS EN 14081-1-compliant standard.

  - Grade: As schedule.

- Surface finish: Planed all round.

- Treatment:

  - Preservative treatment: (Refer to schedule for requirement) Organic solvent impregnation to NBS section Z12 and Wood Protection Association Commodity Specification C8. Design service life: 40 years.

  - Flame retardant treatment: As schedule.

270	UNGRADED SOFTWOOD FOR INTERNAL NONSTRUCTURAL USE

- Quality of timber: Free from decay, insect attack (except pinhole borers) and with no knots wider than half the width of the section.

- Surface finish: Planed all round.

- Treatment:

  - Preservative treatment: (Refer to schedule for requirement) Organic solvent impregnation to NBS section Z12 and Wood Protection Association Commodity Specification C8. Design service life: 40 years.

  - Flame retardant treatment: As schedule.

275	WOOD TRIM FOR GENERAL USE AS SCHEDULE

- Species: Submit proposals.

- Standard: To BS 1186-3. - Class: 2.

- Treatment: (Refer to schedule for requirement) Organic solvent impregnation to NBS section Z12 and Wood Protection Association Commodity Specification C8. - Design service life: 40 years.

- Fixing: As schedule.

- Other requirements: As schedule.

311	NON-STRUCTURAL PLYWOOD AS SCHEDULE

- Standard: To an approved national standard.

- Thickness: As schedule.

- Appearance class to BS EN 635: I/II.

- Use class to BS EN 335: Use class 1.

- Bond quality to BS EN 314-2: Class 1.

- Finish: Sanded.

- Edges: Square unless otherwise specified.

- Treatment:

  - Preservative treatment: None required.

Design service life: 40 years.

  - Flame retardant treatment: As schedule.

## WORKMANSHIP GENERALLY

- CROSS SECTION DIMENSIONS OF STRUCTURAL SOFTWOOD AND HARDWOOD

  - Dimensions: Dimensions in this specification and shown on drawings are target sizes as defined in BS EN 336.

  - Tolerances: The tolerance indicators (T1) and (T2) specify the maximum permitted deviations from target sizes as stated in BS EN 336, clause 4.3:

    - Tolerance class 1 (T1) for sawn surfaces.

    - Tolerance class 2 (T2) for further processed surfaces.

- CROSS SECTION DIMENSIONS OF NON-STRUCTURAL SOFTWOOD

  - Dimensions: Dimensions in this specification and shown on drawings are finished sizes.

  - Maximum permitted deviations from finished sizes: As stated in BS EN 1313-1: - Clause 6 for sawn sections.

- CROSS SECTION DIMENSIONS OF NON-STRUCTURAL HARDWOOD

  - Dimensions: Dimensions in this specification and shown on drawings are finished sizes.

  - Maximum permitted deviations from finished sizes: As stated in BS EN 1313-2:

    - Clause 6 for sawn sections.

    - Clause NA.3 for further processed sections.

420	WARPING OF TIMBER

•	Bow, spring, twist and cup: Not greater than the limits set down in BS 4978 or BS EN 14081-1 for softwood, or BS 5756 for hardwood.

430	SELECTION AND USE OF TIMBER

•	Timber members damaged, crushed or split beyond the limits permitted by their grading: Do not use.

435	NOTCHES, HOLES AND JOINTS IN TIMBER

Notches and holes:

  - General: Avoid if possible.

  - Sizes: Minimum needed to accommodate services.

  - Position: Do not locate near knots or other defects.

  - In same joist: Minimum 100 mm apart horizontally.

  - Notches in joists:

Position: Locate at top. Form by sawing down to a drilled hole.

Depth (maximum): 0.15 x joist depth.

Distance from supports: Between 0.1 and 0.2 x span.

  - Holes in joists:

Position: Locate on neutral axis.

Diameter (maximum): 0.25 x joist depth.

Centres (minimum): 3 x diameter of largest hole.

Distance from supports: Between 0.25 and 0.4 of span.

  - Notches in roof rafters, struts and truss members: Not permitted.

  - Holes in struts and columns: Locate on neutral axis.

Diameter (maximum): 0.25 x minimum width of member.

Centres (minimum): 3 x diameter of largest hole.

Distance from ends: Between 0.25 and 0.4 of span.

•	Scarf joints, finger joints and splice plates: Do not use without approval.

440	PROCESSING TREATED TIMBER

- Cutting and machining: Carry out as much as possible before treatment.

- Extensively processed timber: Retreat timber sawn lengthways, thickness, planed, ploughed, etc.

- Surfaces exposed by minor cutting/ drilling: Treat with two flood coats of a solution recommended by main treatment solution manufacturer.

450	MOISTURE CONTENT

•	Moisture content of wood and wood based products at time of installation: Not more than:

| - Covered in generally unheated spaces: | 24%. |
| --- | --- |
| - Covered in generally heated spaces: | 20%. |
| - Internal in continuously heated spaces: | 20%. |

510	PROTECTION

- Generally: Keep timber dry and do not overstress, distort or disfigure sections or components during transit, storage, lifting, erection or fixing.

- Timber and components: Store under cover, clear of the ground and with good ventilation. Support on regularly spaced, level bearers on a dry, firm base. Open pile to ensure free movement of air through the stack.

- Trussed rafters: Keep vertical during handling and storage.

520	EXPOSED END GRAIN PROTECTION

- Components: Seal exposed end grain of the following before delivery to site:

As schedule.

- Sealer: Clear end grain sealer.

530	PAINTED FINISHES

•	Structural timber to be painted: Primed as specified before delivery to site.

540	CLEAR FINISHES

•	Structural timber to be clear finished: Keep clean and apply first coat of specified finish before delivery to site.

550	EXPOSED TIMBER

•	Planed structural timber exposed to view in completed work: Prevent damage to and marking of surfaces and arrises.

## JOINTING TIMBER

570	JOINTING/ FIXING GENERALLY

•	Generally: Where not specified precisely, select methods of jointing and fixing and types, sizes and spacings of fasteners in compliance with section Z20.

580	FRAMING ANCHORS

- Manufacturer: Submit proposals.

  - Product reference: Submit proposals.

- Material/ finish: Stainless steel.

- Fasteners: Galvanized or sherardized square twist nails.

  - Size: Not less than size recommended by anchor manufacturer.

- Fixing: Secure using not less than the number of nails recommended by anchor manufacturer.

615	BOLT/ SCREW ASSEMBLIES AS SCHEDULE.

- Designation: Stainless steel bolts to BS EN ISO 3506-1, grade A2.

- Size: As shecule.

- Coating applied by manufacturer: None.

- Nuts and washers: Material grade and finish to suit bolts.

- Washer dimensions: Diameter/ side length of washers in contact with timber faces to be minimum 3 times bolt diameter, with a thickness not less than 0.3 times bolt diameter.

630	BOLTED JOINTS

- Bolt spacings (minimum): To BS EN 1995-1-1, section 8.5.

- Holes for bolts: Located accurately and drilled to diameters as close as practical to the nominal bolt diameter and not more than 2 mm larger.

- Washers: Placed under bolt heads and nuts that would otherwise bear directly on timber. Use spring washers in locations which will be hidden or inaccessible in the completed building.

- Bolt tightening: So that washers just bite the surface of the timber. Ensure that at least one complete thread protrudes from the nut.

- Checking: At agreed regular intervals up to Completion. Tighten as necessary.

670	ANTI-CORROSION FINISHES FOR FASTENERS

- Galvanizing: To BS 7371-6, with internal threads tapped and lightly oiled following treatment.

- Sherardizing: To BS 7371-8, Class 1.

- Zinc plating: To BS EN ISO 4042 and passivated.

760	TEMPORARY BRACING

•	Provision: As necessary to maintain structural timber components in position and to ensure complete stability during construction.

770	ADDITIONAL SUPPORTS

- Provision: Position and fix additional studs, noggings and/ or battens to support edges of sheet materials, and wall/ floor/ ceiling mounted appliances, fixtures, etc. shown on drawings.

- Material properties: Additional studs, noggings and battens to be of adequate size and have the same treatment, if any, as adjacent timber supports.

784	JOISTS GENERALLY

- Centres: Equal, and not exceeding designed spacing.

- Bowed joists: Installed with positive camber.

- End joists: Positioned approximately 50 mm from masonry walls.

786	JOISTS ON HANGERS

- Hangers: Bedded directly on and hard against supporting construction. Do not use packs or bed on mortar.

- Joists: Cut to leave not more than 6 mm gap between ends of joists and back of hanger. Rebated to lie flush with underside of hangers.

- Fixing to hangers: A nail in every hole.

795	TRIMMING OPENINGS

Trimmers and trimming joists: When not specified otherwise, not less than 25 mm wider than general joists.

# K10 Gypsum board dry linings/ partitions/ ceilings

To be read with Preliminaries/ General conditions.

## TYPES OF DRY LINING

125A	TIMBER STUD PARTITION SYSTEM FIRE RESISTANCE - 30 MINUTES

- Manufacturer: British Gypsum..

  - Product reference: Non-loadbearing timber stud.

- Studs:

  - Type: CLS Profile softwood framing timber, size 63 x 38 mm.

  - Strength class to BS EN 338: C16. - Centres: 450 mm.

- Head condition: 63 x 38 mm head plate to suspended timber or concrete floor. - Deflection allowance: 10 mm.

- Insulation: Mineral wool to BS EN 13162; density not less than 30 kg/m³ .

  - Recycled content: Contractor's choice. - Thickness: 50 mm.

- Linings: 1 x 12.5 mm Gyproc FireLine to each side.

- Finishing: Taped seamless finish.

  - Primer/ Sealer: One coat of Gyproc Drywall Prime.

  - Accessories: Rigid metal beads/ stops recommended by board manufacturer.

- Other requirements: Access panels (as schedule).

130A	METAL STUD PARTITION SYSTEM FIRE RESISTANCE - 30 MINUTES

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: GypWall Classic

- Studs:

  - Type: 48 mm Gypframe 48 S 50 'C' studs.

  - Centres: 600 mm

- Head condition:

  - Type: Gypframe 50 C 50 Floor and Ceiling Channels. - Deflection allowance: 10 mm.

- Insulation:

  - Type: Isover APR 1200. - Thickness: 50 mm.

- Linings:

  - Type: 1 x 12.5 mm Gyproc FireLine to each side. - Edge: Tapered edge.

- Finishing:

  - Type: Taped seamless finish.

  - Primer/ Sealer: One coat of Gyproc Drywall Prime.

- Accessories: Rigid metal beads/ stops recommended by board manufacturer.

- Other requirements: Access panels (as schedule).

165A	WALL LINING SYSTEM (METAL FRAMING) FIRE RESISTANCE - 30 MINUTES

- Manufacturer: British Gypsum.

- Web: www.british-gypsum.com.

- Email: bgtechnical.enquiries@bpb.com.

- Product reference: GypLyner UNIVERSAL

- Wall: Masonry.

- Cavity between wall and back of lining: As schedule - 35 mm generally and 20 mm at opening reveals.

- Framing centres: 600 mm

- Bracket centres (maximum): 800 mm

- Insulation: None.

- Linings: 1 x 12.5 mm Gyproc WallBoard unless otherwise specified.

- Access units: As schedule.

- Finishing:

  - Type: Taped seamless finish.

  - Primer/ Sealer: One coat of Gyproc Drywall Primer.

- Accessories: Brackets, channels, track, connectors, rigid beads / stops - as schedule.

185A	WALL LINING SYSTEM (ADHESIVE)

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: DriLyner BASIC

- Parge coat: Gyproc SoundCoat - unless otherwise specified.

- Adhesive method: Dabs as clause 625 or Spots as clause 630 for insulated plasterboard.

- Linings: 1 x 12.5 mm Gyproc WallBoard - unless otherwise specified.

- Finishing:

  - Type: Taped seamless finish.

  - Primer/ Sealer: One coat of Gyproc Drywall Primer. - Accessories: Rigid beads/ stops.

205A	LINING ON TIMBER FIRE RESISTANCE - 30 MINUTES

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: Timber stud (Non Loadbearing and Loadbering)

- Metal resilient (acoustic) bars: As schedule - Gypframe RB1 resilient bar.

- Insulation: 50 mm Isover Acoustic Partition Roll (APR 1200) unless otherwise specified.

- Linings:

  - Type: 1 x 12.5 mm Gyproc FireLine to each side. - Fixing: British Gypsum drywall timber screws.

- Finishing:

  - Type: Taped seamless finish.

  - Primer/ Sealer: One coat of Gyproc Drywall Primer. - Accessories: Rigid beads/ stops.

- Other requirements: Access panels - as schedule.

220A	PROPRIETARY METAL FRAME SUSPENDED CEILING SYSTEM FIRE RESISTANCE - 60 MINUTES

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: CasoLine MF suspended ceiling system

- Suspension system:

  - Hanger type: Strap hangers / angles / acoustic hangers as schedule.

Top fixings: Hangers twice screwed to sides of timber joists, using Gyproc Drywall Screws unless otherwise specified within schedule.

  - Primary grid centres: 1200 mm. Hanger centres: 1200 mm.

  - Secondary grid centres: 400 mm for single layer of MultiBoard fixed to minimum 44 mm wide timber joists.

- Linings: 12.5 mm Glasroc F MultiBoard or 2 x 12.5 mm Gyproc WallBoard unless otherwise specified.

- Insulation: 100 mm Isover general purpose roll.

- Access Units: Gyproc Profilex access panels - as schedule.

- Finishing: Skim coat plaster finish.

- Primer/ Sealer:

  - Type: One coat of Gyproc Drywall Primer.

- Accessories : As schedule.

245A	CEILING LINING ON TIMBER

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: Timber joist ceilings

- Metal resilient (acoustic) bars: Gypframe RB1 resilient bars, fixed to underside of joists at 450 mm centres.

- Linings:

  - Type: 1 x 12.5 mm Glasroc F MULTIBOARD- screw fixed unless otherwise specified. - Fixings: 58 mm Glasroc F FIRECASE Screws at 150 mm centres.

- Insulation: 100 mm Isover  Acoustic Partition Roll (APR 1200) as schedule.

- Finishing:

  - Type: Skim coat plaster finish.

  - Primer/ Sealer: One coat of Gyproc Drywall Primer.

- Accessories: Gyproc Profilex Access Panels - as schedule.

- Other requirements: As schedule.

255A	ENCASEMENT SYSTEM (METAL FRAMING) STEEL COLUMNS

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: GypLyner ENCASE

- Extent of protection to structural members: Columns: Four sides.

- Fire performance: 60 minutes - unless otherwise specified.

- Framing system: Sizes and spacing of framing and fixings as recommended by British Gypsum

- Linings: 12.5 mm Gyproc FireLine - unless otherwise specified.

- Finishing:

  - Type: Taped seamless finish.

  - Primer/ sealer: One coat of Gyproc Drywall Primer. - Accessories: Rigid beads/ stops

255B	ENCASEMENT SYSTEM (METAL FRAMING) STEEL BEAMS

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: GypLyner ENCASE

- Extent of protection to structural members: Beams: Three sides.

- Fire performance: 60 minutes - unless otherwise specified.

- Framing system: Sizes and spacing of framing and fixings as recommended by British Gypsum

- Linings: 12.5 mm Gyproc FireLine - unless otherwise specified.

- Finishing:

  - Type: Taped seamless finish.

  - Primer/ sealer: One coat of Gyproc Drywall Primer.

  - Accessories: Rigid beads/ stops

265A	ENCASEMENT SYSTEM (FRAMELESS) COLUMNS

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: FireCase

- Extent of protection to structural members: Four sided protection to steel columns.

- Fire performance: 60 minutes - unless otherwise specified.

- Support system: Sizes and spacing of intermediate backing strips/ noggings/ metal angles and fixings as recommended by British Gypsum

- Linings: 15 mm Glasroc F FireCase - unless otherwise specified.

- Fixings: Gyproc Impluse staples or 40mm Glasroc F firecase Screws.

- Finishing:

  - Type: Taped seamless finish.

  - Accessories: Rigid beads/ stops.

265B	ENCASEMENT SYSTEM (FRAMELESS) BEAMS

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: FireCase

- Extent of protection to structural members: Three sided protection to steel beams incorporating steel angles.

- Fire performance: 60 minutes - unless otherwise specified.

- Support system: Sizes and spacing of intermediate backing strips/ noggings/ metal angles and fixings as recommended by British Gypsum

- Linings: 15 mm Glasroc F FireCase - unless otherwise specified.

- Fixings: Gyproc Impluse staples or 40mm Glasroc F firecase Screws.

- Finishing:

  - Type: Taped seamless finish.

  - Accessories: Rigid beads/ stops.

## INSTALLATION

305	GYPSUM BOARDS GENERALLY

•	Standard:

- Gypsum plasterboard to BS EN 520.

- Fibre reinforced gypsum board to BS EN 15283-2.

- Evidence of compliance: All sheets to be CE marked. Submit Declaration of Performance (DoP).

335	ADDITIONAL SUPPORTS

Framing: Accurately position and securely fix to give full support to:

- Partition heads running parallel with, but offset from main structural supports.

- Fixtures, fittings and service outlets. Mark framing positions clearly and accurately on linings.

- Board edges and lining perimeters, as recommended by board manufacturer to suit type and performance of lining.

375	NEW WET LAID BASES

•	Dpcs: Install under full width of partitions/ freestanding wall linings. - Material: Bituminous sheet or plastics.

435	DRY LININGS GENERALLY

- General: Use fixing, jointing, sealing and finishing materials, components and installation methods recommended by board manufacturer.

- Cutting gypsum boards: Neatly and accurately without damaging core or tearing paper facing.

- Cut edges: Minimize and position at internal angles wherever possible. Mask with bound edges of adjacent boards at external corners.

- Fixings boards: Securely and firmly to suitably prepared and accurately levelled backgrounds.

- Finishing: Neatly to give flush, smooth, flat surfaces free from bowing and abrupt changes of level.

445	CEILINGS

- Sequence: Fix boards to ceilings before installing dry lined walls and partitions.

- Orientation of boards: Fix with bound edges at right angles to supports and with ends staggered in adjacent rows.

- Two layer boarding: Stagger joints between layers.

455	METAL FRAMING FOR PARTITIONS/ WALL LININGS

- Setting out: Accurately aligned and plumb.

  - Frame/ Stud positions: Equal centres to suit specified linings, maintaining sequence across openings.

  - Additional studs: To support vertical edges of boards.

- Fixing centres at perimeters (maximum): 600 mm.

- Openings: Form accurately.

  - Doorsets: Use sleeved or boxed metal studs and/ or suitable timber framing to achieve strength grade requirements for framing assembly and adequately support weight of door. - Services penetrations: Allow for associated fire stopping.

485	SUSPENDED CEILING GRIDS

- Setting out: Accurately aligned and level.

  - Grid members and hangers: Centres to suit specified linings and imposed loads.

  - Additional grid members: Provide bracing and stiffening at upstands, partition heads, access hatches, etc.

- Fixing: Securely at perimeters, grid joints, top and bottom hanger fixings.

505	INSTALLING MINERAL WOOL INSULATION

- Fitting insulation: Closely butted joints and no gaps. Use fasteners to prevent slumping or displacement.

- Services:

- Electrical cables overlaid by insulation: Sized accordingly. - Ceilings: Cut insulation around electrical fittings, etc.

510	SEALING GAPS AND AIR PATHS

- Location of sealant: To perimeter abutments and around openings.

  - Pressurized shafts and ducts: At board-to-board and board-to-metal frame junctions.

- Application: To clean, dry and dust free surfaces as a continuous bead with no gaps.

  - Gaps greater than 6 mm between floor and underside of gypsum board: After sealing, fill with jointing compound.

530	CAVITY FIRE BARRIERS WITHIN PARTITIONS/ WALL LININGS

Metal framed systems:

  - Material: Wire reinforced mineral wool 50 mm (minimum) thick.

  - Installation: Form accurately and fix securely with no gaps to provide a complete barrier to smoke and flame.

- Adhesive fixed wall lining systems:

  - Material: Adhesive compound.

  - Installation: Form in a continuous line with no gaps to provide a complete barrier to smoke and flame.

545A	CAVITY FIRE BARRIER SYSTEM

- Manufacturer: British Gypsum.

  - Web: www.british-gypsum.com.

  - Email: bgtechnical.enquiries@bpb.com.

  - Product reference: Cavity Fire Barrier Systems

- Framework: 68 x 38 mm timber stud framework, with studs at 600 mm centres.

- Linings:

  - Type: 12.5 mm Gyproc FireLine.

  - Edges: Tapered.

  - Applied to: Each side of framework.

- Fire resistance to BS 476-20: 30 minutes integrity, 30 minutes insulation - unless otherwise ststed.

555	FIRE STOPPING AT PERIMETERS OF DRY LINING SYSTEMS

- Material: Tightly packed mineral wool or intumescent mastic/ sealant.

- Application: To perimeter abutments to provide a complete barrier to smoke and flame.

560	JOINTS BETWEEN BOARDS

- Tapered edged gypsum boards: - Bound edges: Lightly butted.

- Cut/ unbound edges: 3 mm gap.

- Square edged plasterboards: 3 mm gap.

- Square edged gypsum fibre boards: 5 mm gap.

565	VERTICAL JOINTS

•	Joints: Centre on studs.

- Partitions: Stagger joints on opposite sides of studs. - Two layer boarding: Stagger joints between layers.

570	HORIZONTAL JOINTS

- Surfaces exposed to view: Horizontal joints not permitted. Seek instructions where height of partition/ lining exceeds maximum available length of board.

- Two layer boarding: Stagger joints between layers by at least 600 mm.

- Edges of boards: Support using additional framing.

- Two layer boarding: Support edges of outer layer.

580	INSULATION BACKED PLASTERBOARD

- General: Do not damage or cut away insulation to accommodate services.

- Installation at corners: Carefully cut back insulation or plasterboard as appropriate along edges of boards to give a continuous plasterboard face, with no gaps in insulation.

590	FIXING GYPSUM BOARD TO METAL FRAMING/ FURRINGS

Partitions/ Wall linings: Fix securely and firmly at the following centres (maximum):

  - Single layer boarding: To all framing at 300 mm centres. Reduce to 200 mm centres at external angles.

  - Multi-layer boarding: Face layer at 300 mm centres, and previous layers around perimeters at 300 mm centres.

- Ceilings: 230 mm. Reduce to 150 mm at board ends and at lining perimeters.

- Position of screws from edges of boards (minimum): 10 mm.

- Screw heads: Set in a depression. Do not break paper or gypsum core.

592	FIXING INSULATION BACKED PLASTERBOARD TO METAL FURRINGS

•	Fixing to furrings: In addition to screw fixings apply continuous beads of adhesive sealant to furrings.

610	FIXING GYPSUM BOARD TO TIMBER

- Fixing to timber: Securely at the following centres (maximum):

  - Nails: 150 mm.

  - Screws to partitions/ wall linings: 300 mm. Reduce to 200 mm at external angles. - Screws to ceilings: 230 mm.

- Position of nails/ screws from edges of boards (minimum):

  - Bound edges: 10 mm.

  - Cut/ unbound edges: 13 mm.

- Position of nails/ screws from edges of timber supports (minimum): 6 mm.

620	FIXING GYPSUM BOARD WITH ADHESIVE DABS

  - Setting out boards: Accurately aligned and plumb.

  - Fixing to substrates: Securely using adhesive dabs.

  - Adhesive dab spacings for each board:

    - Horizontally: One row along top edge and one continuous dab along bottom edge.

    - Vertically: One row along each edge and thereafter at intermediate spacings to suit size of board: Thickness (mm)   	Width (mm)   	Dab centres (mm)

9.5   1200   400

9.5/12.5   	900   	450

12.5   	1200   600

•	Adhesive dab dimensions (width x length): At least 50-75 mm x 250 mm. - Position of dabs from edges/ ends of boards (minimum): 25 mm.

625	FIXING INSULATION BACKED PLASTERBOARD WITH ADHESIVE DABS

•	Fixing to substrates: In addition to adhesive dab fixings, secure boards with nailable plugs in locations recommended by board manufacturer.

630	FIXING INSULATION BACKED PLASTERBOARD WITH ADHESIVE SPOTS

- Setting out boards: Accurately aligned and plumb.

- Fixing to substrates: Securely using adhesive spots and mechanical fastenings.

- Adhesive spot spacings to each board: Four vertical rows, at 400 mm centres in each row.

- Adhesive spot diameters (minimum): 25 mm.

- Mechanical fasteners: Nailable plugs in locations recommended by board manufacturer.

## FINISHING

650	LEVEL OF DRY LINING ACROSS JOINTS

- Sudden irregularities: Not permitted.

- Joint deviations: Measure from faces of adjacent boards using methods and straightedges (450 mm long with feet/ pads) to BS 8212, clause 3.3.5.

  - Tapered edge joints:

Permissible deviation (maximum) across joints when measured with feet resting on boards: 3 mm.

  - External angles:

Permissible deviation (maximum) for both faces: 4 mm. - Internal angles:

Permissible deviation (maximum) for both faces: 5 mm.

670	SEAMLESS JOINTING TO GYPSUM BOARDS

- Cut edges of boards: Lightly sand to remove paper burrs.

- Filling and taping: Fill joints, gaps and internal angles with jointing compound and cover with continuous lengths of paper tape, fully bedded.

- Protection of edges/ corners: Reinforce external angles, stop ends, etc. with specified edge/ angle bead.

- Finishing: Apply jointing compound. Feather out each application beyond previous application to give a flush, smooth, seamless surface.

- Nail/ screw depressions: Fill with jointing compound to give a flush surface.

- Minor imperfections: Remove by light sanding.

680	SKIM COAT PLASTER FINISH

- Plaster type: As recommended by board manufacturer.. - Thickness: 2-3 mm.

- Joints: Fill and tape except where coincident with metal beads.

- Finish: Tight, matt, smooth surface with no hollows, abrupt changes of level or trowel marks.

695	INSTALLING BEADS/ STOPS

- Cutting: Neatly using mitres at return angles.

- Fixing: Securely using longest possible lengths, plumb, square and true to line and level, ensuring full contact of wings with substrate.

- Finishing: After joint compounds/ plasters have been applied, remove surplus material while still wet from surfaces of beads exposed to view.

725	REPAIRS TO EXISTING GYPSUM BOARD

- Filling small areas with broken cores: Cut away paper facing, remove loose core material and fill with jointing compound.

  - Finish: Flush, smooth surface suitable for redecoration.

- Large patch repairs: Cut out damaged area and form neat hole with rectangular sides. Replace with matching gypsum board.

  - Fixing: Use methods to suit type of dry lining, ensuring full support to all edges of existing and new gypsum board.

  - Finishing: Fill joints, tape and apply jointing compound to give a flush, smooth surface suitable for redecoration.

# K11 Rigid sheet flooring/ sheathing/ decking/ sarking/ linings/ casings

To be read with Preliminaries/ General conditions.

## TYPES OF FLOORING/ SHEATHING/ DECKING /SARKING/ LININGS/ CASINGS

110	WOOD-BASED SHEETS GENERALLY

- Standard: To BS EN 13986.

  - Evidence of compliance: All sheets to be CE marked. Submit Declaration of Performance (DoP).

325A	PARTICLEBOARD FLOORING ROOF SPACE - LOFT BOARDS

- Substrate: Timber joists at 600 mm centres. - Additional supports: As clause 930.

- Flooring: Particleboard to BS EN 312, Type P5.

  - Size: 1220 mm x 320 mm.

  - Thickness: 18 mm.

  - Fire performance: Not applicable.

  - Edges: Tongued and grooved all edges. - Recycled content: Contractor's choice.

- Setting out: Long edges running across joists. End joints central over joists and staggered.

- Fixing to joists:

  - Fasteners: 50 mm x 8 gauge chipboard screws into pilot holes.

  - Fixing centres:

  - Around floor perimeter and along edges of each board: 600 mm (maximum);

  - Along intermediate supports: 300 mm (maximum);-  Fixing distance from edges: Minimum 8 mm; and -  Fixing distance from corner: Minimum 15 mm.

- Joint treatment: Bonded with PVA adhesive to BS EN 204, Class D3.

## WORKMANSHIP

910	INSTALLATION GENERALLY

- Timing: Building to be weathertight before fixing boards internally.

- Moisture content of timber supports (maximum): 18%.

- Joints between boards: Accurately aligned, of constant width and parallel to perimeter edges.

- Methods of fixing, and fasteners: As section Z20 where not specified otherwise.

930	ADDITIONAL SUPPORTS

- Additional studs, noggings/ dwangs (Scot) and battens:

  - Provision: In accordance with board manufacturer's recommendations and as follows:

Tongue and groove jointed rigid board areas: To all unsupported perimeter edges.

Butt jointed rigid board areas: To all unsupported edges.

Size: Not less than 50 mm wide and of adequate thickness.

  - Treatment (where required): As for adjacent timber supports.

- Additional floor supports.

  - Type: Softwood noggings.

  - Acoustic batten cradles. - Counterbattens.

940	BOARD MOISTURE CONTENT AND CONDITIONING

- Moisture content of boards at time of fixing: Appropriate to end use.

- Conditioning regime: Submit proposals.

960	FIXING GENERALLY

- Boards/ sheets: Fixed securely to each support without distortion and true to line and level.

- Fasteners: Evenly spaced in straight lines and, unless otherwise recommended by board manufacturer, in pairs across joints.

- Distance from edge of board/ sheet: Sufficient to prevent damage.

- Surplus adhesive: Removed as the work proceeds.

980	OPEN JOINTS

- Perimeter joints, expansion joints and joints between boards: Free from plaster, mortar droppings and other debris.

- Temporary wedges and packings: Removed on completion of board fixing.

# K13 Rigid sheet fine linings and panelling

To be read with Preliminaries/ General conditions.

## GENERAL REQUIREMENTS

400	DOOR FRAMES

- Hardwood packing between frames and reveals: To give even joints of specified width.

  - Position of packs: Where fixings tighten frame against structure.

- Positions of frames: Accurate, plumb, level, and aligned.

  - Fixing of frames: Secure, to prevent pulling away, deflection, or other movement during use.

  - Fastener locations: 600 mm maximum centres with at least one fixing 150 mm from each end of jambs and one adjacent to each hanging point.

410	FIRE RESISTING FRAMES

•	Gaps between frames and supporting construction: Filled as necessary in accordance with requirements for certification and/ or door/ doorset manufacturer's instructions.

# K40 Demountable suspended ceilings

To be read with Preliminaries/General conditions.

## TYPES OF CEILING SYSTEM

115A	UNIT/ MODULAR SUSPENDED CEILING SYSTEM TO AREAS AS SCHEDULE

- Standard: To BS EN 13964.

- Evidence of compliance: All ceilings kits to be CE marked. Submit Declaration of Performance (DoP).

- Ceiling system manufacturer: Armstrong Ceiling Solutions.

  - Product reference: Dune eVo - unless otherwise specified.

- Ceiling:

  - Infill units: Lay-in mineral ceiling tile - textured microperforated surface.

  - Module: 600 x 600 x 15 mm.

  - Soffit height above finished floor level: As schedule.

- Grid:

  - Form: Interlocking.

  - Exposure: Exposed.

  - Spacings: As recommeded by manufacturer.

- Access: Access panels as schedule.

- Integrated services fittings: Hangers and housings for linear luminaires - as schedule.

- Other requirements: As schedule.

115B	CEILING TILES

- Manufacturer: Armstrong Ceiling Solutions.

  - Web: www.armstrongceilingsolutions.co.uk.

  - Email: ats@armstrongceilingsolutions.co.uk.

  - Product reference: Dune eVo

- Arrangement: As recommended by manufacturer.

- Edge detail: Tegular.

- Module size (w x l, nominal): 600 x 600 mm.

## COMPONENTS

245	STANDARDS

- Steel panels: To BS EN 10346.

- Aluminium sheet, strip and plate: To BS EN 485-1 and -2.

- Aluminium bars, tubes and sections: To relevant parts of BS EN 515, BS EN 573, BS EN 755 and BS EN 12020.

## EXECUTION

305	SETTING OUT

- General: Completed ceiling should present, over the whole of its surface exposed to the room below, a continuous and even surface, jointed (where applicable) at regular intervals.

- Infill and access units, integrated services: Fitted correctly and aligned.

- Edge/ perimeter infill units size (minimum): Half standard width or length.

- Corner infill units size (minimum): Half standard width and length.

- Grid: Position to suit infill unit sizes. Allow for permitted deviations from nominal sizes of infill units.

- Infill joints and exposed suspension members: Straight, aligned and parallel to walls, unless specified otherwise.

- Suitability of construction: Give notice where building elements and features to which the ceiling systems relate are not square, straight or level.

315	PROTECTION

- Loading: Do not apply loads for which the suspension system is not designed.

- Ceiling materials: When necessary, remove and replace correctly using special tools and clean gloves, etc. as appropriate.

325	INSTALLING HANGERS

- Wire hangers: Straighten and tension before use.

- Installation: Install vertical or near vertical without bends or kinks. Do not allow hangers to press against fittings, services, or insulation covering ducts/ pipes.

- Obstructions: Where obstructions prevent vertical installation, either brace diagonal hangers against lateral movement, or hang ceiling system on an appropriate rigid sub-grid bridging across obstructions and supported to prevent lateral movement.

- Extra hangers: Provide as necessary to carry additional loads.

- Fixing:

- Wire hangers: Tie securely at top with tight bends to loops to prevent vertical movement. - Angle/ Strap hangers: Do not use rivets for top fixing.

- Spacings: As recommeded by ceiling system manufacturer.

335	INSTALLING PERIMETER TRIMS

- Jointing: Neat and accurate, without lipping or twisting.

- External and internal corners: Mitre joints generally. Overlap joints at internal corners are not acceptable.

  - Intermediate butt joints: Minimize. Use longest available lengths of trim. Align adjacent lengths.

- Fixing: Fix firmly to perimeter wall, edge battens or other building structure. - Fasteners: As recommeded by ceiling system manufacturer.

  - Fixing centres: As recommeded by ceiling system manufacturer.

375	BOARD CEILING SYSTEMS

- Cut boards: Neat and accurate.

- Fixing to grid:

  - Board edges: Fully support. Screw to grid members. Set heads of screws below surface of boards and fill flush with surface.

  - Boards applied in two or more layers: Stagger joints.

- Movement joints: Provide as appropriate for the area of ceiling system and/ or to coincide with movement joints in surrounding structure.

390	OPENINGS IN CEILING MATERIALS

•	General: Neat and accurate. To suit sizes and edge details of fittings. Do not distort ceiling system.

395	INTEGRATED SERVICES

- General: Position services accurately, support adequately. Align and level in relation to the ceiling and suspension system. Do not diminish performance of ceiling system.

- Small fittings: Support with rigid backing boards or other suitable means. Do not damage or distort the ceiling.

  - Surface spread of flame rating of additional supporting material: Not less than ceiling material.

- Services outlets:

  - Supported by ceiling system: Provide additional hangers.

  - Independently supported: Provide flanges to support ceiling system.

401	CEILING-MOUNTED LUMINAIRES

Support:   By ceiling system.

  - Independently supported luminaires: Suspension adjusted to line and level of ceiling.

  - Ceiling supported luminaires: Modifications and/ or extra support required: To each luminaire as schedule.

- Surface mounted luminaires: Units installed so that in event of a fire the designed grid expansion provision is not affected.

- Modular fluorescent recessed luminaires: Compatible with ceiling module. Extension boxes must not foul ceiling system.

- Recessed rows of luminaires: Provide flanges for support of grid and infill units, unless mounted above grid flanges. Retain in position with lateral restraint.

- Fire protecting/ resisting ceiling systems: Luminaires must not diminish protection integrity of ceiling system.

- Access: Provide access for maintenance of luminaires.

411	MECHANICAL SERVICES

- Fan coil units:

  - Inlet and outlet grilles: Trim ceiling grid and infill units to suit.

  - Space beneath: Sufficient for ceiling system components.

  - Suspension and connections: Permit accurate setting out and levelling of fan coil units.

- Air grilles and diffusers:

  - Setting out: Accurate and level.

  - Linear air diffusers: Retain in place with lateral restraint. Provide flanges for support of grid and infill units.

  - Grille/ diffuser ceiling joints: Provide smudge rings and edge seals.

- Smoke detectors and PA speakers:

  - Ceiling infill units: Scribe and trim to suit.

  - Independent suspension: As schedule. - Flexible connections: Required.

- Sprinkler heads: Carefully set out and level.

415	INSTALLING INSULATION

- Fitting: Fit accurately and firmly with butted joints and no gaps.

- Insulation within individual infill units: Fit closely. Secure to prevent displacement when infill units are installed or subsequently lifted.

- Dustproof sleeving: Reseal, if cut.

- Width: Lay insulation in the widest practical widths to suit grid member spacings.

- Services: Do not cover electrical cables that have not been sized accordingly. Cut insulation carefully around electrical fittings, etc. Do not lay insulation over luminaires.

- Sloping and vertical areas of ceiling system: Fasten insulation to prevent displacement.

425	INSTALLING CAVITY FIRE BARRIERS

- Maximum ceiling void dimension in any direction: As schedule.

- Fixing: Secure barrier at head and base using proprietary angle support system and Fix angle support system to timber framework with No. 10 woodscrews at 450 mm centres.

  - General: Fix battens securely to channels or angles at abutments to building structure.

  - At perimeters and joints: Provide permanent stability and continuity with no gaps to form a complete barrier to smoke and flame.

- Joints: Form to preserve integrity in fire.

- Service penetrations: Cut barriers neatly to accommodate services. Fit fire resistant sleeves around flexible materials. Fill gaps around services to fire barrier manufacturer's recommendations to maintain barrier integrity. Adequately support services passing through the barrier.

- Ceiling systems intended for fire protection: Do not impair fire resisting performance of ceiling system.

- Ceiling systems not intended for fire protection: Do not mechanically interlink barriers with ceiling system.

# K45 Suspended ceiling system alterations

To be read with Preliminaries/ General conditions.

## GENERAL

110	DEFINITIONS

- Ceiling: Items collectively constituting the ceiling surface, including infill units, boards, stretched fabric, access units and grid.

- Ceiling system: Ceiling plus suspension components and integrated services fittings.

120	EXISTING SUSPENDED CEILING SYSTEM TO AREAS AS SCHEDULE

- Structure over: As schedule.

- Ceiling type: Exposed grid with mineral fibre infill units.

  - Manufacturer: Determine on site.

Product reference: Determine on site.

  - Ceiling height above floor: Determine on site. - Ceiling void: Determine on site.

130	UNIT SUSPENDED CEILING SYSTEM ALTERATIONS TO AREAS AS SCHEDULE

- Manufacturer: Submit proposals.

- Product reference: Submit proposals.

- Suspension type: As existing.

- Grid: As existing.

- Infill units: As existing.

- Access units: Rectangular, hinged, fire rated - as schedule.

- Accessories: As existing.

- Integrated services fittings: As existing .

- Void barriers: As schedule.

- Acoustic Insulation: No alterations proposed .

- Performance: Maintain fire performance.

160	BOARD SUSPENDED CEILING SYSTEM ALTERATIONS TO AREAS AS SCHEDULE

- Manufacturer: Submit proposals.

- Product reference: Submit proposals.

- Suspension type: As existing.

- Grid: As existing.

- Boards: As existing .

- Access units: Rectangular Hinged Fire rated - As schedule.

- Accessories: As existing.

- Integrated services fittings: As existing .

- Void barriers: As schedule

- Acoustic insulation: No alterations proposed .

- Performance: Maintain fire performance.

## PRODUCTS

310	PRODUCTS GENERALLY

•	Ceiling systems and components: To BS EN 13964.

315	SUSPENSION SYSTEM - EXPOSED GRID TO CEILINGS AS SCHEDULE

Scope: Include all hangers, fixings, main runners, cross members, primary channels, perimeter clips, splines, noggins, clips, bracing, bridging etc. necessary to complete the ceiling and, where applicable, achieve specified performance.

- Manufacturer: Submit proposals.

  - Product reference: Submit proposals.

- Hangers: Wire - unless otherwise specified.

  - Material: Galvanized steel.

  - Top fixings: Anchor bolts - or as recommeded by system manufacturer.

- Grid:

  - Module: 600 x 600 mm.

  - Type: T section.

  - Size: 25 mm.

  - Material: Steel.

  - Finish: baked polyester paint.

  - Colour: White RAL 9010 or to match existing.

350	BOARDS TO MATCH EXISTING - AS SCHEDULE

- Manufacturer: Submit proposals.

  - Product reference: Submit proposals.

- Recycled content: Submit proposals.

- Size: As existing.

- Thickness: As existing.

- Fillets and cover strips: As existing.

  - Finish: Match textured plastics coating. - Colour: White RAL 9010 or as existing.

370	INFILL UNITS  TO MATCH EXISTING - AS SCHEDULE

- Manufacturer: Submit proposals.

  - Product reference: Submit proposals.

- Material: Mineral fibre.

- Recycled content: Submit proposals.

- Size: 600 x 600 mm.

- Edge profile: As existing.

- Finish: As existing.

  - Colour: White RAL 9010 oir as existing.

390	ACCESS UNITS - FIRE RATED AS SCHEUDULE

- Manufacturer: As schedule.

  - Product reference: As schedule.

- Size: As schedule.

- Finish: Prefinished.

  - Colour: White RAL 9010 or as existing.

405	TIMBER EDGE BATTENS AS SCHEDULE

- Type: Planed softwood to BS EN 942, class J10.

- Moisture content at time of fixing: 15% ± 2%.

- Finished size: 21 x 44 mm.

415	CAVITY FIRE BARRIERS

- Manufacturer: Submit proposals.

  - Product reference: Submit proposals.

- Ceiling system void subdivision (maximum): 20 m - unless otherwise specified.

- Fire:

  - Reaction to fire (minimum): Class 1 to BS 476-7.

  - Resistance to fire (minimum): 30/30 minutes to BS 476-20.

- Material: Wire reinforced mineral wool.

## EXECUTION

610	PREPARATION

- Documentation: Obtain available documentation of the existing ceiling system and services, including record drawings and maintenance manual. Check on site.

- Discrepancies: Give notice.

620	EXECUTION GENERALLY

- Workmanship: In accordance with BS EN 13964 Annex A.

- Designated ceiling system components: Remove carefully without affecting surrounding areas.

- Disposal of removed components: Remove from site.

- Retained components: Do not distort or damage retained components.

- Reuse of ceiling system components:

  - Condition: Undamaged, free from distortion, clean.

  - Units and boards: Match adjacent areas where appropriate.

- Cutting units, boards and components: Cut neatly and accurately. Maintain edge profiles. - Openings: Suit sizes and edge details of fittings.

650	SETTING OUT

- General: Maintain ceiling system accurately, continuous, even, and jointed at regular intervals.

Provide level soffits free from undulations, lipping and distortions in grid members.

- Infill units, access units, integrated services: Fit and align correctly.

- Minimum size for edge and perimeter infill units half standard width or length where practicable.

- Grid: Position to suit infill unit sizes. Allow for permitted deviations from nominal sizes.

- Infill joints and exposed suspension members: Straight, aligned and parallel to walls or setting out lines. Where building elements and features to which the ceiling system relates are not square, straight or level, give notice.

670	INSTALLING SUSPENSION

- Fixing:

  - Angle or strap hangers: Do not rivet for top fixing.

  - Wire hangers: Tie securely with tight bends to loops to prevent vertical movement.

- Installation:

  - Alignment Vertical or near vertical.

  - Maintain straight, with suitable tension and without bends or kinks.

  - Do not allow hangers to press against fittings, services and insulation covering ducts and pipes.

- Obstructions: Where obstructions prevent vertical installation, either:

  - brace diagonal hangers against lateral movement; or

  - hang ceiling system on an appropriate rigid sub-grid bridging across obstructions and supported to prevent lateral movement.

- Extra hangers: Provide as required to carry additional loads.

675	INSTALLING PERIMETER TRIMS

- Jointing: Neat and accurate, without lipping or twisting.

  - External and internal corners: Mitre joints.

  - Intermediate butt joints: Minimize. Use longest available lengths of trim. Align adjacent lengths, with matching joints.

- Fixing: Fix firmly to perimeter wall or other building structure.

  - Fixing centres: As existing.

- Finish: Apply before ceiling grid is installed.

  - Prime new timber edge battens with undercoat and final coat to visible surfaces.

680	INSTALLING BOARDS

Fixing boards to grids: Screw boards securely and firmly to grid members.

- Surface: Provide a flat surface free from bowing and lipping. Set heads of screws below surface of boards and fill flush with surface.

- Movement joints: Provide as appropriate for the area of ceiling and align with movement joints in surrounding structure.

- Boards applied in two or more layers: Stagger joints.

- Board edges: Fully support. Screw to grid members.

700	COORDINATION WITH SERVICES

- Preparation: Check existing position of services against proposed alterations.

- Clashes between services and ceiling system: Give notice.

- Coordination: Programme works to minimise impact.

- Services disconnection: Give notice.

710	INTEGRATED SERVICES

- General: Position services accurately, support adequately. Align and level in relation to the ceiling. Alterations must not diminish performance of ceiling system.

- Surface spread of flame rating of additional supporting material: Match ceiling material.

- Services outlets:

  - Supported by ceiling system: Provide additional hangers.

  - Independently supported: Provide flanges to support altered ceiling system.

715	LUMINAIRES

- Independently support luminaires: Adjust suspension to line and level of ceiling as necessary.

- Surface mounted luminaires: Do not inhibit designed grid expansion in fire.

- Modular fluorescent recessed luminaires: Compatible with ceiling module. Extension boxes must not foul ceiling system.

- Continuous recessed rows of luminaires: Provide flanges for support of grid and infill units, unless mounted above grid flanges. Retain in place with lateral restraint.

- Fire protecting and resisting ceiling systems: Luminaires must maintain protection integrity of ceiling system.

- Access: Provide access for maintenance of luminaires.

720	MECHANICAL SERVICES

- Fan coil units:

  - Inlet and outlet grilles: Trim ceiling grid and infill units to suit.

  - Void clearance beneath: Sufficient for ceiling system and fan coil components.

  - Suspension and connections: Permit accurate setting out and levelling of fan coil units.

- Air grilles and diffusers:

  - Linear air diffusers: Provide flanges for support of grid and infill units. Provide for displacement of ceiling grid. Retain in place with lateral restraint.

  - Grille and diffuser ceiling joints: Provide smudge rings and edge seals.

725	OTHER SERVICES

- Smoke detectors and PA speakers:

  - Infill units: Scribe to suit.

  - Flexible connections: Required.

- Sprinkler heads: Carefully set out and level.

730	INSTALLING INSULATION

- Fitting: Fit accurately and firmly with closely butted joints and no gaps.

- Insulation within individual infill units: Fit closely. Secure to prevent displacement when infill units are installed or subsequently lifted. Reseal cut dustproof sleeving.

- Width: Lay insulation in the widest practical widths to suit grid member spacings.

- Services: Do not cover electrical cables not sized accordingly. Cut insulation carefully around electrical fittings, etc. Do not lay insulation over luminaires.

- Sloping and vertical areas of ceiling system: Fasten insulation to prevent displacement.

735	INSTALLING CAVITY FIRE BARRIERS

- Fixing:

  - General: Fix firmly to channels or angles at abutments to building structure.

  - At perimeters and joints: Secure. Provide permanent stability and continuity with no gaps. Provide a complete barrier to smoke and flame.

- Joints: Form to preserve integrity in fire.

- Service penetrations: Cut and pack to maintain barrier integrity. Sleeve flexible materials. Adequately support services passing through the barrier.

  - Ceiling systems intended for fire protection: Do not impair fire resisting performance of ceiling system.

  - Ceiling systems not intended for fire protection: Do not mechanically interlink barriers with ceiling system.

# L10 Windows/ Rooflights/ Screens/ Louvres

To be read with Preliminaries/ General conditions.

## GENERAL

110	EVIDENCE OF PERFORMANCE

•	Certification: Provide independently certified evidence that all incorporated components comply with specified performance requirements.

115	TIMBER PROCUREMENT

- Timber (including timber for wood based products): Obtained from well managed forests and/ or plantations in accordance with:

  - The laws governing forest management in the producer country or countries.

  - International agreements such as the Convention on International Trade in Endangered Species of wild fauna and flora (CITES).

- Documentation: Provide either:

  - Documentary evidence (which has been or can be independently verified) regarding the provenance of all timber supplied.

  - Evidence that suppliers have adopted and are implementing a formal environmental purchasing policy for timber and wood based products.

- Certification scheme: Forest Stewardship Council (FSA). - Other evidence: None.

120	PRECONSTRUCTION SURVEY

- Procedure: Before starting work on designated items take site dimensions, record on shop drawings and use to ensure accurate fabrication.

- Designated items: Wood overpanels and sidescreens.

- Primary support structure: Carry out survey sufficient to verify that required accuracy and security of erection can be achieved.

- Timing: Before fabrication.

## PRODUCTS

560A	GLAZED OVERPANELS AND SCREENS: 30 MINUTES FIRE RESISTANCE

- Location: As schedule.

- Manufacturer: Contractor's choice.

  - Product reference: Contractor's choice.

- Screen height: As schedule, maximum floor to ceiling (2700 mm).

- Fire classification of complete system:

  - Fire resistance: To BS 476-22.

Rating: 30 minutes' integrity and 30 minutes' insulation.

- Sound insulation rating: Rw 40 dB.

- Frame:

  - Material: Softwood / hardwood, 510 kg/m³ minimum density.

  - Section size: Minimum 70 x 32 mm.

  - Frame fixing: Plugged and screwed as section Z20; spacings as clause 780A and; sealing to supporting construction.

  - Frame member requirements:

  - Joints: Frame joints mortice and tenoned, mitred, half lapped or butted and with no gaps.

  - Joint fixing: All jointing methods require mechanical fixing with the appropriate size ring shank nails or screws. Butt joints must be additionally bonded with urea formaldehyde adhesive.

- Glazing:

  - Glass type: Clear fire-resisting glazing, as manufacturers standard..

- Glazing bead:

  - Type: Propriety intumescent glazing system, as section manufacturers standard.

  - Dimensions: As schedule.

  - Fixing: As manufacurers instructions.

- Solid panels: Overpanels and sidescreens: - Type: Flamebreak 430 FD30 door blank.

  - Finish and colour: As section M60.

  - Joint treatment: Screw fixing through rear of frame using steel screws passing at least 30 mm into the centre line of the overpanel.

  - Intumescent seals: Intumescent seals provided at jambs, fitted within frame reveal within machined grooves, as manufacurers standard.

  - Frame to overpanel junction: 2 mm maximum gap tolerance permitted when intumescent seals are provided to all edges.

  - Fixing spacings: 100mm from each corner maximum and 250mm centres maximum.

- Architraves, skirtings, sills:

  - Dimensions:  45 x 19 mm..

  - Material: Sustainable softwood, primed for site painting. - Finish: As section M60.

- Other requirements: Sealing of frame to supporting wall structure, as schedule and section P12.

560B	GLAZED OVERPANELS AND SCREENS: 60 MINUTES FIRE RESISTANCE

- Location: As schedule.

- Manufacturer: Contractor's choice.

  - Product reference: Contractor's choice.

- Screen height: As schedule, maximum floor to ceiling (2700 mm).

- Fire classification of complete system:

  - Fire resistance: To BS 476-22.

Rating: 60 minutes' integrity and 60 minutes' insulation.

- Sound insulation rating: Rw 40 dB.

- Frame:

  - Material: Hardwood, 640 kg/m³ minimum density.

  - Section size: Minimum 70 x 44 mm.

  - Frame fixing: Plugged and screwed as section Z20; spacings as clause 780A and; sealing to supporting construction.

  - Frame member requirements:

  - Joints: Frame joints mortice and tenoned, mitred, half lapped or butted and with no gaps.

  - Joint fixing: All jointing methods require mechanical fixing with the appropriate size ring shank nails or screws. Butt joints must be additionally bonded with urea formaldehyde adhesive.

- Glazing:

  - Glass type: Clear fire-resisting glazing, as manufacturers standard..

- Glazing bead:

  - Type: Propriety intumescent glazing system, as section manufacturers standard.

  - Dimensions: As schedule.

  - Fixing: As manufacurers instructions.

- Solid panels: Overpanels and sidescreens:

  - Type: Flamebreak Flamebreak 660 FD60 door blank.

  - Finish and colour: As section M60.

  - Joint treatment: Screw fixing through rear of frame using steel screws passing at least 30 mm into the centre line of the overpanel.

  - Intumescent seals: Intumescent seals provided at jambs, fitted within frame reveal within machined grooves, as manufacurers standard.

  - Frame to overpanel junction: 2 mm maximum gap tolerance permitted when intumescent seals are provided to all edges.

  - Fixing spacings: 100mm from each corner maximum and 250mm centres maximum.

- Architraves, skirtings, sills:

  - Dimensions:  45 x 19 mm..

  - Material: Sustainable softwood, primed for site painting. - Finish: As section M60.

- Other requirements: Sealing of frame to supporting wall structure, as schedule and section P12.

## EXECUTION

710	PROTECTION OF COMPONENTS

- General: Do not deliver to site components that cannot be installed immediately or placed in clean, dry floored and covered storage.

- Stored components: Stack vertical or near vertical on level bearers, separated with spacers to prevent damage by and to projecting ironmongery, beads, etc.

730	PRIMING/ SEALING

•	Wood surfaces inaccessible after installation: Prime or seal as specified before fixing components.

750	BUILDING IN

- General: Not permitted unless indicated on drawings.

  - Brace and protect components to prevent distortion and damage during construction of adjacent structure.

780A	FIXING OF WOOD FRAMES

- Standard: As section Z20.

- Fasteners: Stainless steel wood screws.

  - Spacing: When not predrilled or specified otherwise, position fasteners not more than 100 mm from ends of each jamb, adjacent to each hanging point of opening lights, and at maximum 450 mm centres.

790	FIRE RESISTING FRAMES

•	Gap between back of frame and reveal: Completely fill with tightly packed mineral wool or proprietary fire stopping material.

810	SEALANT JOINTS

•	Sealant:

- Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

- Colour: To match existing.

- Application: As section Z22 to prepared joints. Finish triangular fillets to a flat or slightly convex profile.

820	IRONMONGERY

- Fixing: In accordance with any third party certification conditions applicable. Assemble and fix carefully and accurately using fasteners with matching finish supplied by ironmongery manufacturer. Do not damage ironmongery and adjacent surfaces.

- Checking/ Adjusting/ Lubricating: Carry out at completion and ensure correct functioning.

# L20 Doors/ shutters/ hatches

To be read with Preliminaries/ General conditions.

## GENERAL

110	EVIDENCE OF PERFORMANCE

•	Certification: Provide independently certified evidence that all incorporated components comply with specified performance requirements.

112	TIMBER PROCUREMENT

- Timber (including timber for wood-based products): Obtained from well-managed forests and/ or plantations in accordance with:

  - The laws governing forest management in the producer country or countries.

  - International agreements such as the Convention on International Trade in Endangered Species of wild fauna and flora (CITES).

- Documentation: Provide either:

  - Documentary evidence (which has been or can be independently verified) regarding the provenance of all timber supplied.

  - Evidence that suppliers have adopted and are implementing a formal environmental purchasing policy for timber and wood-based products.

- Certification scheme: Forest Stewardship Council (FSA). - Other evidence: None.

115	FIRE RESISTING AND SMOKE CONTROL PEDESTRIAN DOORS/ DOOR ASSEMBLIES/ DOORSETS

- CE marked fire resisting doorsets: To BS EN 16034 and in conjunction with BS EN 13241 and BS EN 14351-1 (and eventually prEN 14351-2).

- Door products: As defined in BS EN 12519.

- Evidence of fire performance: Provide certified evidence, in the form of a product conformity certificate, directly relevant fire test report or engineering assessment, that each door/ door assembly/ doorset supplied will comply with the specified requirements for fire resisting and/ or smoke control if tested to BS 476-22, BS EN 1634-1, BS EN 1634-3 or is CE marked to BS EN 16034. Such certification must cover door and frame materials, glass and glazing materials and their installation, essential and ancillary ironmongery, hinges and seals.

- Components and assemblies will be marked to the relevant CE marking European product standard (hEN), national product standard and/ or third party certification rating.

118A	GLOBAL FIRE RESISTANCE ASSESSMENT FOR DOORS/ DOOR ASSEMBLIES/ DOORSETS

- Installation of doors/ door assemblies/ doorsets: In strict accordance with respective manufacturers Global Fire Resistance Assessment.

- Aspects of design, installation assembly covered by assessment listed below in brief. For comprehensive information refer to global assessment report document.

  - The use of overpanels and how to install them.

  - Acceptable increases in leaf dimensions (height and width).

  - Acceptable changes in doorset configurations (single leaf, double leaf, single acting, double acting).

  - The use of and installation of glazing and the option to use various glass types.

  - Door frame variations

  - Ironmongery components

  - Fire, smoke and acoustic control requirements

- Global Fire Resistance Assessment Documents:

  - Appendix 9b: Flamebreak FD30-FEAF98164 rev.M.

  - Appendix 9c: Flamebreak FD60-FEA2FF02141 rev.J.

120	NON-FIRE RESISTING PEDESTRIAN DOORS/ DOOR ASSEMBLIES/ DOORSETS

- Provide certified evidence, in the form of a product conformity certificate or engineering assessment, that each pedestrian door/ doorset/ assembly supplied will comply with the specified requirements to BS EN 14351-1. Such certification must cover door and frame materials, glass and glazing materials and their installation, essential and ancillary ironmongery, hinges and seals.

- Components and assemblies will be marked to the relevant CE marking Euopean product standard, national product standard and/ or third party certification rating.

150	SITE DIMENSIONS

- Procedure: Before starting work on designated items take site dimensions, record on shop drawings and use to ensure accurate fabrication.

- Designated items: As schedule.

## PRODUCTS

230A	WOOD FLUSH DOORS FD30 FIRE RESISTING

- Standard: To BS 476-22.

- Approvals:

  - FSC®: Chain Of Custody certified.

  - PEFC: Chain Of Custody certified.

  - BM TRADA: Q Mark certification. - PAS 23/ 24 .

- Manufacturer: Contractor's choice.

  - Product reference: Flamebreak 430 Exterior Glue Lipped FD30.

- Door leaf:

  - Core: 3-layer laminated hardwood lumber.

  - Thickness: 44 mm.

  - Facings: 4 mm hardwood plywood.

  - Lippings: Exposed hardwood lippings to all edges.

  - Finish as delivered: Prepared and primed, as section M60.

- Glazing/ Infill details: Clear fire-resisting glazing, as manufacturers standard.

  - Style: As schedule.

  - Manifestation: Not required.

  - Beading: Hardwood, as manufacturers standard.

- Glazing system: As manufacturers standard.

- Thermal performance (U-value maximum): 1.2 W/m²K.

- Sizes: As schedule.

  - 1981 x 686 / 762 / 838 / 915 / 1050 / 1060 mm. - 2032 x 813 mm.

  - 2040 x 626 / 726 / 826 / 926 / 1026 / 1060 mm.

  - 2058 x 838 mm.

  - 2083 x 864 mm.

  - 2135 x 915 mm.

230B	WOOD FLUSH DOORS FD60 FIRE RESISTING

- Standard: To BS 476-22.

- Approvals:

  - FSC®: Chain Of Custody certified.

  - PEFC: Chain Of Custody certified.

  - BM TRADA: Q Mark certification. - PAS 23/ 24 .

- Manufacturer: Contractor's choice.

  - Product reference: Flamebreak 660 Exterior Glue Lipped FD60.

- Door leaf:

  - Core: 3-layer laminated hardwood lumber.

  - Thickness: 54 mm.

  - Facings: 6 mm hardwood plywood.

  - Lippings: Exposed hardwood lippings to all edges.

  - Finish as delivered: Prepared and primed, as section M60.

- Glazing/ Infill details: Clear fire-resisting glazing, as manufacturers standard.

  - Style: As schedule

  - Manifestation: Not required.

  - Beading: Hardwood, as manufacturers standard.

- Glazing system: As manufacturers standard.

- Thermal performance (U-value maximum): 1.2 W/m²K.

- Sizes: As schedule.

  - 1981 x 762 / 838 / 1060

  - 2040 x 726 / 826 / 926 / 1026 / 1060

  - 2135 x 915

230C	WOOD PANELLED DOORS FD30 FIRE RESISTING

- Standard: To BS 476-22.

- Approvals:

  - Certifire approved.

  - FSC®: Chain Of Custody certified. - PEFC: Chain Of Custody certified.

- Manufacturer: Contractor's choice.

  - Product reference: Contractor's choice.

- Door leaf:

  - Core: Particle board.

  - Thickness: 44 mm.

  - Facings: Moulded and embossed hardboard (woodgrain finish).

  - Lippings/ frame: Concealed softwood perimeter frame.

  - Finish as delivered: Prepared and primed, as section M60.

- Thermal performance (U-value maximum): Manufacturer's standard.

- Sizes: As schedule.

230D	WOOD PANELLED DOORS FD60 FIRE RESISTING

- Standard: To BS 476-22.

- Approvals:

  - Certifire approved.

  - FSC®: Chain Of Custody certified. - PEFC: Chain Of Custody certified.

- Manufacturer: Contractor's choice.

  - Product reference: Contractor's choice.

- Door leaf:

  - Core: Particle board.

  - Thickness: 54 mm.

  - Facings: Moulded and embossed hardboard (woodgrain finish).

  - Lippings/ frame: Concealed hardwood perimeter frame.

  - Finish as delivered: Prepared and primed, as section M60.

- Thermal performance (U-value maximum): Manufacturer's standard.

- Sizes: As schedule.

235A	GLAZING SYSTEM: 30 MINUTES FIRE RESISTANCE

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: Lorient Fire Resistant Glazing System, System 36/6 PLUS.

- Type: System 36/6 flexible U-shaped intumscent gasket for use with 6–7 mm fire rated glass, suitable for screens and doors.

- Channel dimensions: 15 x 12 mm, in 60 m coil, Ref: LG1512.

- Liner: Intumescent liner.

- Timber glazing beads:

  - Type: 21.5 x 13 mm, Ref: LG1321.

  - Finish: Oak.

  - Fixing: Pinned using 40 mm panel pins at 200 mm nominal centres.

235B	GLAZING SYSTEM: 60 MINUTES FIRE RESISTANCE

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: Lorient Fire Resistant Glazing System, System 36/10 PLUS.

Type: System 36/10 flexible U-shaped intumescent gasket for use with 9 - 11 mm fire rated glass, suitable for screens and doors.

- Liner: Intumescent liner.

- Timber glazing beads:

  - Type: 18.5 x 15 mm, Ref: LG1521.

  - Finish: Oak.

  - Fixing: Screwed using No. 8 x 45 mm countersunk head screws at 200 mm nominal centres.

330A	WOOD DOOR FRAMES (SOFTWOOD) FD30s FIRE RESISTING AND SMOKE CONTROL

- Materials: Generally to BS EN 942.

  - Species / density: Softwood, 450 kg/m³ minimum density.

  - Section size: Minimum 70 x 32 mm.

  - Rebated stops: Minimum 12 mm depth.

  - Appearance class: Straight grained, joinery quality, free from knots, splits and checks..

- Assembly:

  - Adhesive: PVAC to BS EN 204, Class D4.

  - Frame joints: Mortice and tenoned, mitred, half lapped or butted. All jointing methods require mechanical fixing with the appropriate size ring shank nails or screws. - Joinery workmanship: As section Z10.

- Preservative treatment: Not required.

- Moisture content on delivery: 12-16%.

- Finish as delivered: Prepared and primed, as section M60.

- Perimeter seals: Fire and smoke seal.

- Thermal performance: Not applicable.

- Fixing: Plugged and screwed as section Z20; spacings as clause 790A and; sealing to supporting construction as clause 810.

- Architraves / trims: As section P20.

330B	WOOD DOOR FRAMES (HARDWOOD) FD60s FIRE RESISTING AND SMOKE CONTROL

- Materials: Generally to BS EN 942.

  - Species / density: Hardwood, 640 kg/m³ minimum density.

  - Section size: Minimum 70 x 32 mm.

  - Rebated stops: Minimum 12 mm depth.

  - Appearance class: Straight grained, joinery quality, free from knots, splits and checks..

- Assembly:

  - Adhesive: PVAC to BS EN 204, Class D4.

  - Frame joints: Mortice and tenoned, mitred, half lapped or butted. All jointing methods require mechanical fixing with the appropriate size ring shank nails or screws. - Joinery workmanship: As section Z10.

- Preservative treatment: Not required.

- Moisture content on delivery: 12-16%.

- Finish as delivered: Prepared and primed, as section M60.

- Perimeter seals: Fire and smoke seal.

- Thermal performance: Not applicable.

- Fixing: Plugged and screwed as section Z20; spacings as clause 790A and; sealing to supporting construction as clause 810.

- Architraves / trims: As section P20.

340A	COMBINED INTUMESCENT FIRE AND SMOKE SEAL (BRUSH PILE): 30 MINUTES FIRE RESISTANCE

- Standard: Fire / Smoke to BS 476-22. and BS 476-31.1, Acoustic to BS EN ISO 10140-2.

  - Durability: 100 000 cycles.

- Approvals: Certifire: CF330, CF341. IFC: Certificate: FRPP454.

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: LP1504SS Fire and Smoke Door Seal - 15 x 4 mm.

- Type: Polyvinyl chloride (PVC) encased sodium silicate and polypropylene brush pile.

- Location:  [Head and jambs, single and double leaf door frames]. Height: Brush pile: 4 mm, total: 8 mm.

Fixed location: Within grooves in door frame or door edges.

  - Gap size:  [3-4 mm at door edge].

Fixing:  [Self adhesive within grooves of door frame or door edges].

- Length: 1000 mm and 2100 mm.

- Colour/ Finish:

  - Seal colour: Standard colour range, as schedule. - Brush pile colour: Blck or grey, as schedule.

340B	COMBINED INTUMESCENT FIRE AND SMOKE SEAL (BRUSH PILE): 60 MINUTES FIRE RESISTANCE

- Standard: Fire / Smoke to BS 476-22. and BS 476-31.1, Acoustic to BS EN ISO 10140-2.

  - Durability: 100 000 cycles.

- Approvals: Certifire: CF330, CF341. IFC: Certificate: FRPP454.

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: LP2004SS Fire and Smoke Door Seal - 20 x 4 mm.

- Type: Polyvinyl chloride (PVC) encased sodium silicate and polypropylene brush pile.

- Location:  [Head and jambs, single and double leaf door frames]. Height: Brush pile: 4 mm, total: 8 mm.

Fixed location: Within grooves in door frame or door edges.

  - Gap size:  [3-4 mm at door edge].

Fixing:  [Self adhesive within grooves of door frame or door edges].

- Length: 1000 mm and 2100 mm.

- Colour/ Finish:

  - Seal colour: Standard colour range, as schedule. - Brush pile colour: Blck or grey, as schedule. 345A	INTUMESCENT FIRE SEAL: 30 MINUTES FIRE RESISTANCE

- Standard: Fire: BS EN 1634-1: 2008 & BS 476-22: 1987. - Durability: 1 million cycles.

- Approvals: Certifire: CF330/CF341, BBA: 92/2841, IFC: FRPP454.

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: Intumescent Fire Seal Ref: LP1504 - 15 x 4 mm. - Resistance to fire: 30 minutes.

- Length: 1000 mm and 2100 mm.

- Colour:

  - Standard range: As schedule.

  - Superluxe Woodgrain finish: Not required. - Superluxe metallic finishes: Not required.

345B	INTUMESCENT FIRE SEAL: 60 MINUTES FIRE RESISTANCE

- Standard: Fire: BS EN 1634-1: 2008 & BS 476-22: 1987.

  - Durability: 1 million cycles.

- Approvals: Certifire: CF330/CF341,  BBA: BBA: 92/2841, IFC: FRPP454.

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: Intumescent Fire Seal Ref: LP2004 - 20 x 4 mm. - Resistance to fire: 60 minutes.

- Length: 1000 mm and 2100 mm.

- Colour:

  - Standard range: As schedule.

  - Superluxe Woodgrain finish: Not required. - Superluxe metallic finishes: Not required.

350A	SMOKE AND ACOUSTIC PERIMETER SEAL

- Standard: Smoke: BS 476-31.1.

- Performance: Meets smoke requirement: BS 9999: 2017. Protects against sound, smoke, draught and light.

  - Acoustic: BS EN ISO 10140-2: 2010 (up to Rw 44dB).Sound reduction up to 55dBRw - Durability: minimum of 100,000 cycles.

- Approvals: Certifire: CF629 (incl. NOR710, NOR720 & NOR810) Smoke performance of seals.

- Manufacturer: Norseal Limited.

  - Product reference: NOR710 Perimeter Seal.

- Type: Co-extruded rigid base with flexible fins.

- Location: Head and jambs, single and double leaf door frames.

- Length: 2100 mm and 3000 mm.

- Colour: As schedule.

- Fixed location: Corner seal, suitable for application against door stop and frame.

  - Minimum gap size: 3 mm at door edge.

- Fixing: Self adhesive to door frame or stop.

410A	WOOD FLUSH DOORSETS FD30s FIRE RESISTING AND SMOKE CONTROL

- Standard: To BS 476-22.

- Approvals:

  - FSC®: Chain Of Custody certified.

  - PEFC: Chain Of Custody certified.

  - BM TRADA: Q Mark certification. - PAS 23/ 24 .

- Manufacturer: Contractor's choice.

  - Product reference: Flamebreak 430 Exterior Glue Lipped FD30.

- Door leaf:

- Core: 3-layer laminated hardwood lumber.

- Thickness: 44 mm.

  - Facings: 4 mm hardwood plywood.

  - Lippings: Exposed hardwood lippings to all edges.

  - Finish as delivered: Prepared and primed, as section M60.

- Frame and architraves:

  - Type: Softwood as clause 330A.

  - Wood species / density: Submit proposals, 450 kg/m³ minimum density.

  - Section size: Minimum 70 x 32 mm.

  - Planted stops: Minimum 12 mm depth.

  - Appearance class: Straight grained, joinery quality, free from knots, splits and checks.

  - Architrave / trims: As section P20.

  - Finish as delivered: Prepared and primed, as section M60.

- Preservative treatment: Not required.

- Glazing/ Infill details: Clear fire-resisting glazing, as section L40. - Style: As schedule, refer to FD detail drawing no. 001 - Manifestation: Not required.

  - Beading: Hardwood, as section L40.

- Glazing system: As clause 235A.

- Ironmongery: As section P21 and schedule.

- Perimeter seals: Fire seals as clause 345A, acoustic smoke seals as clause 350A.

- Thermal performance (U-value maximum): 1.2 W/m²K.

- Other requirements: None.

- Fixing: Plugged and screwed.

- Door sizes: As schedule.

  - 1981 x 686 / 762 / 838 / 915 / 1050 / 1060 mm. - 2032 x 813 mm.

  - 2040 x 626 / 726 / 826 / 926 / 1026 / 1060 mm.

  - 2058 x 838 mm.

  - 2083 x 864 mm.

  - 2135 x 915 mm.

410B	WOOD FLUSH DOORSETS FD60s FIRE RESISTING AND SMOKE CONTROL

- Standard: To BS 476-22.

- Approvals:

  - FSC®: Chain Of Custody certified.

  - PEFC: Chain Of Custody certified.

  - BM TRADA: Q Mark certification. - PAS 23/ 24 .

- Manufacturer: Contractor's choice.

  - Product reference: Flamebreak 660 Exterior Glue Lipped FD60.

- Door leaf:

- Core: 3-layer laminated hardwood lumber.

- Thickness: 54 mm.

  - Facings: 6 mm hardwood plywood.

  - Lippings: Exposed hardwood lippings to all edges.

  - Finish as delivered: Prepared and primed, as section M60.

- Frame and architraves:

  - Type: Hardwood as clause 330B.

  - Wood species / density: Submit proposals, 640 kg/m³ minimum density.

  - Section size: Minimum 70 x 32 mm.

  - Planted stops: Minimum 12 mm depth.

  - Appearance class: Straight grained, joinery quality, free from knots, splits and checks.

  - Architrave / trims: As section P20.

  - Finish as delivered: Prepared and primed, as section M60.

- Preservative treatment: Not required.

- Glazing/ Infill details: Clear fire-resisting glazing, as section L40. - Style: As schedule, refer to FD detail drawing no. 001 - Manifestation: Not required.

  - Beading: Hardwood, as section L40.

- Glazing system: As clause 235B.

- Ironmongery: As section P21 and schedule.

- Perimeter seals: Fire seals as clause 345B, acoustic smoke seals as clause 350A.

- Thermal performance (U-value maximum): 1.2 W/m²K.

- Other requirements: None.

- Fixing: Plugged and screwed.

- Door sizes: As schedule.

  - 1981 x 762 / 838 / 1060 mm.

  - 2040 x 726 / 826 / 926 / 1026 / 1060 mm. - 2135 x 915 mm.

410C	WOOD PANELLED DOORSETS FD30s FIRE RESISTING AND SMOKE CONTROL

- Standard: To BS 476-22.

- Approvals:

  - Certifire approved.

  - FSC®: Chain Of Custody certified. - PEFC: Chain Of Custody certified.

- Manufacturer: Contractor's choice.

  - Product reference: Contractor's choice.

- Door leaf:

- Core: Particleboard.

- Thickness: 44 mm.

  - Facings: Moulded and embossed hardboard (woodgrain finish.

  - Lippings/ frame: Concealed softwood perimeter frame.

  - Finish as delivered: Prepared and primed, as section M60.

- Frame and architraves:

  - Type: Softwood as clause 330A.

  - Wood species / density: Submit proposals, 450 kg/m³ minimum density.

  - Section size: Minimum 70 x 32 mm.

  - Planted stops: Minimum 12 mm depth..

  - Appearance class: Straight grained, joinery quality, free from knots, splits and checks.

  - Architrave / trims: As section P20.

  - Finish as delivered: Prepared and primed, as section M60.

- Preservative treatment: Not required.

- Ironmongery: As section P21 and schedule.

- Perimeter seals: Fire and smoke seal.

- Thermal performance (U-value maximum): Manufacturer's standard.

- Other requirements: None.

- Fixing: Plugged and screwed.

- Door sizes: As schedule.

410D	WOOD PANELLED DOORSETS FD60s FIRE RESISTING AND SMOKE CONTROL

- Standard: To BS 476-22.

- Approvals:

  - Certifire approved.

  - FSC®: Chain Of Custody certified. - PEFC: Chain Of Custody certified.

- Manufacturer: Contractor's choice.

  - Product reference: Contractor's choice.

- Door leaf:

- Core: Particleboard.

- Thickness: 54 mm.

  - Facings: Moulded and embossed hardboard (woodgrain finish.

  - Lippings/ frame: Concealed hardwood perimeter frame.

  - Finish as delivered: Prepared and primed, as section M60.

- Frame and architraves:

  - Type: Hardwood as clause 330B.

  - Wood species / density: Submit proposals, 640 kg/m³ minimum density.

  - Section size: Minimum 70 x 32 mm.

  - Planted stops: Minimum 12 mm depth..

  - Appearance class: Straight grained, joinery quality, free from knots, splits and checks.

  - Architrave / trims: As section P20.

  - Finish as delivered: Prepared and primed, as section M60.

- Preservative treatment: Not required.

- Ironmongery: As section P21 and schedule.

- Perimeter seals: Fire and smoke seal.

- Thermal performance (U-value maximum): Manufacturer's standard.

- Other requirements: None.

- Fixing: Plugged and screwed.

- Door sizes: As schedule.

610A	ACTIVE FIRE CURTAIN BARRIER

- Manufacturer: Coopers Fire Ltd.

  - Product reference: FireMaster®

- Size: As schedule.

- Side channels:

  - Type: As schedule: End fixed; Face fixed and Recessed fixed. - Recommended 5 mm gap between side guide and building material. - Orientation: Vertical.

- Finish: Powder coated.

- Concealment: As schedule: Flush fit / Suspended ceiling with recessed shallow gap / Suspended ceiling with patented SLAT™.

- Fixing: As schedule.

- Accessories: As schedule: Beam protection and obstruction warning; Emergency retract; Split drop delay; Visual alert system; and Voice warning.

630A	LOFT ACCESS HATCHES: FIRE AND SMOKE CONTROL

- Standard: Fire tested to BS EN 1634-1 and BS EN 1364-2; Smoke tested to BS 1634-3. - 1 Hour Fire rated robust steel panel. - Part L & NHBC compliant.

- Manufacturer: Jupiter Blue Ltd.

  - Product reference: SD Fire Rated Loft Hatch (insulated) - picture frame.

- Material / finish: Steel, powder coated.

- Colour: White RAL 9010.

- Insulation: 100 mm glass wool, achieves 0.35 "U" value.

- Hinge: Concealed, short side unless otherwise specified.

- Operation: Budget lock (tri-drive services cabinet key) or key lock - as schedule.

Size/ structural opening: As schedule.

  - 550 x 550mm / 555 x 555mm

  - 555 x 800mm / 560 x 805mm

  - 555 x 755mm*/ 555 x 755mm

  - 600 x 600mm / 605 x 605mm   - 600 x 900mm / 605 x 905mm

  - Special: manufactured to order.

*  Note actual hatch size is 536 x 736mm to fit a ceiling cut out of 555 x 755mm when lined with

9.5mm fireboard. Other sizes do not need lining with fireboard

630B	WALL ACCESS PANELS: FIRE AND SMOKE CONTROL

- Standard: Fire tested to BS EN 1634-1 and BS EN 1364-2; Smoke tested to BS 1634-3. - 1 Hour Fire rated robust steel panel.

- Manufacturer: Jupiter Blue Ltd.

  - Product reference: PFFD Fire Rated Access Panel - picture frame.

- Material / finish: Steel, powder coated.

- Colour: White RAL 9010.

- Hinge: Concealed, vertical side unless otherwise specified.

- Operation: Budget lock (square drive) or tamper proof lock - as schedule •	Size / structural opening: As schedule.

  - 150x150mm / 155x155mm

  - 200x200mm / 205x205mm

  - 300x300mm / 305x305mm

  - 350x350mm / 355x355mm

  - 450x450mm / 455x455mm

  - 550x550mm / 555x555mm

  - 600x300mm / 605x305mm

  - 600x600mm / 605x605mm

  - 900x600mm / 905x605mm

  - 1200x600mm / 1205x605mm

  - 1500x600mm /

  - Special: manufactured to order.

630C	WALL / CEILING ACCESS PANELS

- Manufacturer: Jupiter Blue Ltd.

  - Product reference: PFS Premium Access Panel - picture frame.

- Material / finish: Steel, powder coated.

- Colour: White RAL 9010.

- Hinge: Concealed, vertical side unless otherwise specified.

- Operation: Budget lock (square drive) or tamper proof lock - as schedule.

- Size / structural opening: As schedule.

  - 150x150mm / 155x155mm

  - 200x200mm / 205x205mm

  - 300x300mm / 305x305mm

  - 350x350mm / 355x355mm

  - 450x450mm / 455x455mm

  - 550x550mm / 555x555mm

  - 600x600mm / 605x605mm

  - 900x600mm / 905x605mm

  - 1200x600mm / 1205x605mm

  - Special: manufactured to order.

## EXECUTION

710	PROTECTION OF COMPONENTS

- General: Do not deliver to site components that cannot be installed immediately or placed in clean, dry, floored and covered storage.

- Stored components: Stacked on level bearers, separated with spacers to prevent damage by and to projecting ironmongery, beads, etc.

730	PRIMING/ SEALING

•	Wood surfaces inaccessible after installation: Primed or sealed as specified before fixing components.

760	BUILDING IN

•	General: Not permitted unless indicated on drawings.

770	DAMP PROOF COURSES ASSOCIATED WITH BUILT IN WOOD FRAMES

- Method of fixing: To backs of frames using galvanized clout nails.

790A	FIXING OF WOOD FRAMES

- Spacing of fixings (frames not predrilled): Maximum 100 mm from ends of each jamb and at 600 mm maximum centres.

810	FIRE RESISTING AND SMOKE CONTROL DOORS/ DOOR ASSEMBLIES/ DOORSETS/ ROLLER SHUTTERS AND CURTAINS - CONTRACTOR INSTALLED

•	Gaps between frames and supporting construction: Filled as necessary in accordance with requirements for certification and/ or door/ doorset manufacturer's instructions.

820	SEALANT JOINTS

•	Sealant:

- Manufacturer: Contractor's choice .

Product reference: Contractor's choice .

- Colour: As schedule .

- Application: As section Z22 to prepared joints. Triangular fillets finished to a flat or slightly convex profile.

830	FIXING IRONMONGERY GENERALLY

- Fasteners: Supplied by ironmongery manufacturer.

- Finish/ Corrosion resistance: To match ironmongery.

- Holes for components: No larger than required for satisfactory fit/ operation.

- Adjacent surfaces: Undamaged.

- Moving parts: Adjusted, lubricated and functioning correctly at completion.

840	FIXING IRONMONGERY TO FIRE RESISTING DOOR ASSEMBLIES

- General: All items fixed in accordance with door leaf manufacturer's recommendations ensuring that integrity of the assembly, as established by testing, is not compromised.

- Holes for through fixings and components: Accurately cut.

  - Clearances: Not more than 8 mm unless protected by intumescent paste or similar.

  - Lock/ Latch cases for fire 60 doors requiring >  60 minutes integrity performance: Coated with intumescent paint or paste before installation.

850	LOCATION OF HINGES

- Primary hinges: Where not specified otherwise, positioned with centre lines 250 mm from top and bottom of door leaf.

- Third hinge: Where specified, positioned with centre line 250 mm below centre line of top hinge .

- Hinges for fire resisting doors: Positioned in accordance with door leaf manufacturer's recommendations.

860	INSTALLATION OF EMERGENCY EXIT DEVICES

•	Standard: Unless specified otherwise, install panic bolts/ latches in accordance with BS EN 1125.

# L40 General glazing

To be read with Preliminaries/ General conditions.

## GENERAL REQUIREMENTS

150	WORKMANSHIP AND POSITIONING GENERALLY

- Glazing generally: In accordance with BS 6262 series.

- Integrity: Glazing must be wind and watertight under all conditions with full allowance made for deflections and other movements.

- Dimensional tolerances: Panes/ sheets to be within ± 2 mm of specified dimensions.

- Materials:

  - Compatibility: Glass/ plastics, surround materials, sealers, primers and paints/ clear finishes to be used together to be compatible. Avoid contact between glazing panes/ units and alkaline materials such as cement and lime.

  - Protection: Keep materials dry until fixed. Protect insulating glass units and plastics glazing sheets from the sun and other heat sources.

152	PREPARATION

•	Surrounds, rebates, grooves and beads: Clean and prepare before installing glazing; ensure compliance with any certified installation requirements.

155	GLASS GENERALLY

- Standards: To BS 952 and relevant parts of:

  - BS EN 572 for basic soda lime silicate glass.

  - BS EN 1096 for coated glass.

  - BS EN 1748-1 for borosilicate glass.

  - BS EN 1748-2 for ceramic glass.

  - BS EN 1863 for heat strengthened soda lime silicate glass.

  - BS EN 12150 for thermally toughened soda lime silicate safety glass

  - BS EN 12337 for chemically strengthened soda lime silicate glass.

  - BS EN 13024 for thermally toughened borosilicate safety glass.

  - BS EN ISO 12543 for laminated glass and laminated safety glass.

- Panes/ sheets: Clean and free from obvious scratches, bubbles, cracks, rippling, dimples and other defects.

  - Edges: Generally undamaged. Shells and chips not more than 2 mm deep and extending not more than 5 mm across the surface are acceptable if ground out.

- BEAD FIXING WITH PINS

  - Pin spacing: Regular at maximum 150 mm centres, and within 50 mm of each corner.

  - Exposed pin heads: Punched just below wood surface.

- BEAD FIXING WITH SCREWS

  - Screw spacing: Regular at maximum 225 mm centres, and within 75 mm of each corner.

## TYPES OF GLAZING

510A	FIRE RESISTANT CHANNEL GLAZING: 30 MINUTES FIRE RESISTANCE DOORS / OVERPANELS / SIDE SCREENS

- Manufacturer: Pilkington United Kingdom Limited.

  - Product reference: Pilkington Pyrodur® Plus Clear Fire Resistant

- Fire resistance:

  - Standard: To BS 476-22.

  - Rating: 30 minutes integrity, 15 minutes heat insulation. .

- Impact Safety:

  - To BS 6206, Class B.

  - To BS EN 12600, Class 2.

- Pane material: Clear laminated intumescent glass.

  - Thickness: 7 mm.

  - Marking: Each glass pane factory marked including product reference, manufacturer and applicable glass performance classification. Marking must be permenant and visible after installation.

- Frame/ Surround material: Hardwood frame.

- Fire resistant channel: As section L20. - Dimensions: As schedule.

  - Intumescent aperture lining/ filler: As section L20.

- Cover strips: Hardwood.

- Thermal performance (U-value maximum): Manufacturer's standard.

- Installation: By a firm currently registered under a UKAS certified accreditation scheme for the installation of fire resistant glazing, in accordance with glazing manufacturer's recommendations.

- Certification: Submit fire test certification for system, including any framing, installation and maintenance requirements or restrictions.

510B	FIRE RESISTANT CHANNEL GLAZING: 60 MINUTES FIRE RESISTANCE DOORS / OVERPANELS / SIDE SCREENS

- Manufacturer: Pilkington United Kingdom Limited.

  - Product reference: Pilkington Pyrodur® Clear Fire Resistant

- Fire resistance:

  - Standard: To BS 476-22.

  - Rating: 60 minutes integrity, and up to 22 minutes of heat insulation.

- Impact Safety:

  - To BS 6206, Class B.

  - To BS EN 12600, Class 2.

- Pane material: Clear laminated intumescent glass.

  - Thickness: 10 mm.

  - Marking: Each glass pane factory marked including product reference, manufacturer and applicable glass performance classification. Marking must be permenant and visible after installation.

- Frame/ Surround material: Hardwood frame.

- Fire resistant channel: As section L20. - Dimensions: As schedule.

  - Intumescent aperture lining/ filler: As section L20.

- Cover strips: Hardwood.

- Thermal performance (U-value maximum): Manufacturer's standard.

- Installation: By a firm currently registered under a UKAS certified accreditation scheme for the installation of fire resistant glazing, in accordance with glazing manufacturer's recommendations.

- Certification: Submit fire test certification for system, including any framing, installation and maintenance requirements or restrictions.

# M20 Plastered/ Rendered/ Roughcast coatings

To be read with Preliminaries/ General conditions.

## TYPES OF COATING

210	LIGHTWEIGHT GYPSUM PLASTER AS SCHEDULE

- Substrate: As schedule.

  - Preparation: Bonding agent recommended by plaster manufacturer.

- Manufacturer: Contractor's choice.

- Undercoats: To BS EN 13279-1.

  - Product reference: Contractor's choice.

  - Thickness (excluding dubbing out and keys): Two coat 13 mm overall.

- Final coat: Finish plaster to BS EN 13279-1, class B.

  - Product reference: Contractor's choice.

  - Thickness: 2-3 mm. - Finish: Smooth.

- Accessories: Beads and stops .

240	ONE COAT PROPRIETARY PLASTER AS SCHEDULE

- Substrate: As schedule.

  - Preparation: Bonding agent recommended by plaster manufacturer.

- Manufacturer: Contractor's choice.

  - Product reference: Contractor's choice.

- Thickness (excluding dubbing out and keys): As manufacturer's recommendations.

- Finish: Smooth.

- Accessories: Beads and stops .

280	GYPSUM PLASTER SKIM COAT ON PLASTERBOARD

- Plasterboard: 12.5 mm unless otherwise specified.

  - Preparation: Bonding agent recommended by plaster manufacturer.

- Plaster: Board finish/ finish plaster to BS EN 13279-1, class B.

  - Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

  - Thickness: As manufacturer's recommendations, typically 2-5 mm. - Finish: Smooth.

- Accessories: Beads and stops .

285A	SEAMLESS JOINTING PLASTERBOARD

- Plasterboard: 12.5 mm unless otherwise specified.

  - Preparation: Cut edges of boards: Lightly sand to remove paper burrs.

- Filling and taping: Fill joints, gaps and internal angles with jointing compound and cover with continuous lengths of paper tape, fully bedded.

- Protection of edges/ corners: Reinforce external angles, stop ends, etc. with specified edge/ angle bead.

- Finishing: Apply jointing compound. Feather out each application beyond previous application to give a flush, smooth, seamless surface.

- Nail/ screw depressions: Fill with jointing compound to give a flush surface.

- Minor imperfections: Remove by light sanding. - Manufacturer: Contractor's choice.

Product reference: Contractor's choice. - Accessories: Beads and stops .

## MATERIALS AND MAKING OF MORTAR

430	READY-TO-USE CEMENT GAUGED MORTARS

Time and temperature limitations: Use within limits prescribed by mortar manufacturer. - Retempering: Restore workability with water only within prescribed time limits.

497	COLD WEATHER

- General: Do not use frozen materials or apply coatings on frozen or frost bound substrates.

- External work: Avoid when air temperature is at or below 5°C and falling or below 3°C and rising. Maintain temperature of work above freezing until coatings have fully hardened.

- Internal work: Take precautions to enable internal coating work to proceed without damage when air temperature is below 3°C.

## PREPARING SUBSTRATES

510	SUITABILITY OF SUBSTRATES

- Soundness: Free from loose areas and significant cracks and gaps.

- Cutting, chasing, making good, fixing of conduits and services outlets and the like: Completed.

- Tolerances: Permitting specified flatness/ regularity of finished coatings.

- Cleanliness: Free from dirt, dust, efflorescence and mould, and other contaminants incompatible with coatings.

541	BONDING AGENT APPLICATION

• General: Apply evenly to substrate to achieve effective bond of plaster/ render coat. Protect adjacent surfaces.

566	REMOVING DEFECTIVE EXISTING PLASTER

- Plaster for removal: Detached, soft, friable, badly cracked, affected by efflorescence or otherwise damaged.

  - Hollow, detached areas: Obtain instructions.

- Stained plaster: Submit proposals.

- Removing defective plaster. Cut back to a square, sound edge.

- Faults in background (structural deficiencies, damp, etc.): Submit proposals.

- Cracks:

  - Fine hairline cracking/ crazing: Leave. - Other cracks; Obtain instructions.

- Dust and loose material: Remove from exposed substrates and edges.

568	EXISTING DAMP AFFECTED PLASTER/ RENDER

- Plaster affected by rising damp: Remove to a height of 300 mm above highest point reached by damp or 1 m above dpc, whichever is higher.

- Perished and salt contaminated masonry: - Mortar joints: Rake out.

- Masonry units: Submit proposals.

- Faults in substrate (structural deficiencies, additional sources of damp, etc.): Submit proposals.

- Drying out substrate: Established drying conditions. Leave walls to dry for as long as possible before plastering.

- Dust and loose material: Remove from exposed substrate and edges.

## BACKINGS/ BEADS/ JOINTS

610	FIXING PLASTERBOARD BACKINGS TO TIMBER BACKGROUNDS

Fixings, accessories and installation methods: As recommended by board manufacturer.

- Fixing: At the following centres (maximum):

  - Nails: 150 mm.

  - Screws to partitions/ walls: 300 mm. Reduce to 200 mm at external angles. - Screws to ceilings: 230 mm.

- Position of nails/ screws from edges of boards (minimum):

  - Bound edges: 10 mm.

  - Cut/ unbound edges: 13 mm.

- Position of nails/ screws from edges of supports (minimum): 6 mm.

- Nail/ screw heads: Set below surface. Do not break paper or gypsum core.

612	JOINTS IN PLASTERBOARD BACKINGS

- Ceilings:

  - Bound edges: At right angles to supports and with ends staggered in adjacent rows.

  - Two layer boarding: Stagger joints between layers.

- Partitions/ walls:

  - Vertical joints: Centre on studs. Stagger joints on opposite sides of studs. Two layer boarding: Stagger joints between layers.

  - Horizontal joints:

Two layer boarding: Stagger joints between layers by at least 600 mm. Support edges of outer layer.

- Joint widths (maximum): 3 mm.

630	BEADS/ STOPS FOR INTERNAL USE

- Standard: In accordance with BS EN 13914-2.

- Material: Galvanized steel to BS EN 13658-1.

640	BEADS/ STOPS GENERALLY

- Location: External angles and stop ends, except where specified otherwise.

- Corners: Neat mitres at return angles.

- Fixing: Secure, using longest possible lengths, plumb, square and true to line and level, ensuring full contact of wings with substrate.

- Beads/ stops for external render: Fix mechanically.

- Finishing: After coatings have been applied remove surplus material, while still wet, from surfaces of beads/ stops exposed to view.

646	CRACK CONTROL AT JUNCTIONS BETWEEN DISSIMILAR SOLID SUBSTRATES

- Locations: Where defined movement joints are not required. Where dissimilar solid substrates materials are in same plane and rigidly bonded or tied together.

- Crack control materials:

  - Isolating layer: Building paper to BS 1521.

  - Metal lathing: Internally: Galvanized steel plain expanded metal with spacers.

- Installation: Fix metal lathing over isolating layer. Stagger fixings along both edges of lathing.

- Width of installation over single junctions:

  - Isolating layer: 150 mm. - Lathing: 300 mm.

- Width of installation across face of dissimilar substrates material (column, beam, etc. with face width not greater than 450 mm):

  - Isolating layer: 25 mm (minimum) beyond junctions with adjacent substrates. - Lathing: 100 mm (minimum) beyond edges of isolating layer.

659	PLASTERBOARD JOINTS

• Joints and angles (except where coincident with metal beads): Reinforce with continuous lengths of jointing tape.

## INTERNAL PLASTERING

710	APPLICATION GENERALLY

Application of coatings: Firmly and in one continuous operation between angles and joints. Achieve good adhesion.

- Appearance of finished surfaces: Even and consistent. Free from rippling, hollows, ridges, cracks and crazing.

- Accuracy: Finish to a true plane, to correct line and level, with angles and corners to a right angle unless specified otherwise, and with walls and reveals plumb and square.

- Drying out: Prevent excessively rapid or localised drying out.

715	FLATNESS/ SURFACE REGULARITY

- Sudden irregularities: Not permitted.

- Deviation of plaster surface: Measure from underside of a straight edge placed anywhere on surface.

- Permissible deviation (maximum) for plaster not less than 13 mm thick: 3 mm in any consecutive length of 1800 mm.

720	DUBBING OUT

- General: Correct substrate inaccuracies.

- New smooth, dense concrete and similar surfaces: Dubbing out prohibited unless total plaster thickness is within range recommended by plaster manufacturer.

- Thickness of any one coat (maximum): 10 mm.

- Mix: As undercoat.

- Application: Achieve firm bond. Allow each coat to set sufficiently before the next is applied. Cross scratch surface of each coat.

725	UNDERCOATS GENERALLY

- General: Rule to an even surface. Cross scratch to provide a key for the next coat.

- Undercoats on metal lathing: Work well into interstices to obtain maximum key.

- Undercoats gauged with Portland cement: Do not apply next coat until drying shrinkage is substantially complete.

- SMOOTH FINISH

  - Appearance: A tight, matt, smooth surface with no hollows, abrupt changes of level or trowel marks. Avoid water brush, excessive trowelling and over polishing.

- WOOD FLOAT FINISH

  - Appearance: An even overall texture. Finish with a dry wood float as soon as wet sheen has disappeared.

# M60 Painting/ clear finishing

To be read with Preliminaries/ General conditions.

## COATING SYSTEMS

110	EMULSION PAINT CEILINGS

- Manufacturer: As clause 210A.

  - Product reference: Vinyl Matt Emulsion.

- Surfaces: Previously painted and uncoated plaster ceiling surfaces.

  - Preparation: As recommended by manufacturer.

- Initial coats:  None.

  - Number of coats n/a.

- Undercoats: Vinyl matt emulsion. - Number of coats: 1.

- Finishing coats: Vinyl matt emulsion. - Number of coats: 1.

130	GLOSS PAINT UNCOATED WOOD

- Manufacturer: As clause 210A.

  - Product reference: Water Based Gloss.

- Surfaces: Uncoated wood surfaces.

  - Preparation: Woodworks Knotting Solution, as recommended by manufacturer.

- Initial coats: Water based gloss. - Number of coats: 1.

- Undercoats: Water based undercoat. - Number of coats: 1.

- Finishing coats: Water based gloss. - Number of coats: 1.

130A	GLOSS PAINT PREVIOUSLY PAINTED WOOD

- Manufacturer: As clause 210A.

  - Product reference: Water Based Gloss.

- Surfaces: Previously painted wood surfaces.

  - Preparation: Cleaner & Degreaser, as recommended by manufacturer.

- Initial coats: None.

  - Number of coats: n/a.

- Undercoats: Water based undercoat. - Number of coats: 1.

- Finishing coats: Water based gloss. - Number of coats: 1.

150	EGGSHELL/ SATIN PAINT WALLS

- Manufacturer: As clause 210A.

  - Product reference: Acrylic Eggshell.

- Surfaces: Previously painted and uncoated plaster wall surfaces.

  - Preparation: As recommended by manufacturer.

- Initial coats: None.

  - Number of coats: n/a.

- Undercoats: Acrylic eggshell. - Number of coats: 1.

- Finishing coats: Acrylic eggshell. - Number of coats: 1.

160A	DECORATIVE WOODSTAIN VARNISH PRESERVATIVE UNCOATED INTERNAL WOOD SURFACES

- Manufacturer: As clause 210A.

  - Product reference: Satin Woodstain.

- Surfaces: Uncoated wood surfaces - as schedule.

  - Preparation: As recommended by manufacturer.

- Initial coats: Interior/exterior all purpose preserver.

  - Number of coats: 1.

- Undercoats: Satin woodstain. - Number of coats: 1.

- Finishing coats: Satin woodstain. - Number of coats: 1.

160B	DECORATIVE WOODSTAIN VARNISH PRESERVATIVE PREVIOUSLY COATED INTERNAL WOOD SURFACES

- Manufacturer: As clause 210A.

  - Product reference: Satin Woodstain.

- Surfaces: Previously coated wood surfaces - as schedule.

  - Preparation: Fat Hog Paint and Varnish Stripper, as recommended by manufacturer.

- Initial coats: Interior/exterior all purpose preserver.

  - Number of coats: 1.

- Undercoats: Satin woodstain. - Number of coats: 1.

- Finishing coats: Satin woodstain. - Number of coats: 1.

162A	DECORATIVE POLYYURETHANE VARNISH PRESERVATIVE INTERNAL WOOD SURFACES

- Manufacturer: As clause 210A.

  - Product reference: Quick Dry Polyurethane Varnish.

- Surfaces: Previously coated and uncoated wood surfaces - as schedule.

  - Preparation: Cleaner & Degreaser, as recommended by manufacturer.

- Initial coats: Quick dry polyurethane varnish. - Number of coats: 1.

- Undercoats: Quick dry polyurethane varnish. - Number of coats: 1.

- Finishing coats: Quick dry polyurethane varnish. - Number of coats: 1.

164A	FLEXIBLE GLOSS PAINT SYSTEM UNCOATED EXTERNAL WOOD SURFACES

- Manufacturer: As clause 210A.

  - Product reference: Flexible Gloss.

- Surfaces: Uncoated wood surfaces - as schedule.

  - Preparation: Interior/Exterior all purpose preserver, knotting solution and filler, as recommended by manufacturer.

- Initial coats: Flexible Primer Undercoat. - Number of coats: 1.

- Undercoats: Flexible Primer Undercoat. - Number of coats: 1.

- Finishing coats: Flexible Gloss. - Number of coats: 1.

164B	FLEXIBLE GLOSS PAINT SYSTEM PREVIOUSLY COATED EXTERNAL WOOD SURFACES

- Manufacturer: As clause 210A.

  - Product reference: Flexible Gloss.

- Surfaces: Previously coated wood surfaces - as schedule.

  - Preparation: Cleaner & degreaser with surfaces sanded smooth as recommended by manufacturer.

- Initial coats: Interior/Exterior All Purpose Preserver. - Number of coats: 1.

- Undercoats: Flexible Primer Undercoat. - Number of coats: 1.

- Finishing coats: Flexible Gloss. - Number of coats: 1.

172A	FLAME-RETARDANT COATING SYSTEM PREVIOUSLY PAINTED WALL COVERINGS

- Manufacturer: Crown Trade, product of Crown Paints Ltd..

  - Product reference: Timonox Acrylic Eggshell.

- Type: Flame retardant coating system - for previously painted interior, Woodchip, Anaglypa, Lining paper.

- Reaction to fire: Euro Class B (National Class 0 surface spread of flame).

- Surfaces: Previously painted wall coverings - as schedule. - Preparation: As recommended by manufacturer.

- Base coats: Timonox Upgrade Intumescent Basecoat. - Number of coats: 1.

- Finishing coats: Timonox Acrylic Eggshell decoration. - Number of coats: 2.

- Application: As recommended by manufacturer.

  - Number of coats (total): 3.

- Colour: As schedule

- Additional requirements: Obtain site specific specification produced by manufacturer following site survey and submit to CA for approval prior to works.

- Certification: Provide manufacturers certificate of supply.

172B	FLAME-RETARDANT COATING SYSTEM PREVIOUSLY PAINTED WOOD (INTERIOR)

- Standard: To BS EN 13501.

- Manufacturer: Thermoguard UK Limited. .

  - Product reference: Timbercoat - Fire protection system for internal wood.

- Reaction to fire: Euro Class B (National Class 0 surface spread of flame).

- Surfaces: Previously painted wood - as schedule.

  - Preparation: As recommended by manufacturer.

- Base coats: Thermoguard Timbercoat Intumescent Basecoat. - Number of coats: 1.

- Finishing coats: Thermoguard Smoke & Flame Retardant Dualcoat. - Number of coats: 1

- Application: As recommended by manufacturer.

  - Number of coats (total): 2.

- Colour: As schedule.

- Certification: Provide manufacturers certificate of supply.

172C	FLAME-RETARDANT COATING SYSTEM PREVIOUSLY VARNISHED / STAINED WOOD (INTERIOR)

- Standard: To BS EN 13501.

- Manufacturer: Thermoguard UK Limited. .

  - Product reference: Fire Varnish - Fire protection system for exterior wood..

- Reaction to fire: Euro Class B (National Class 0 surface spread of flame).

- Surfaces: Previously stained or varnished wood - as schedule. - Preparation: As recommended by manufacturer.

- Base coats: Thermoguard Fire Varnish Intumescent Basecoat. - Number of coats: 1.

- Finishing coats: Thermoguard Fire Varnish Overcoat. - Number of coats: 1

- Application: As recommended by manufacturer.

  - Number of coats (total): 2.

- Colour: As schedule.

- Certification: Provide manufacturers certificate of supply.

172D	FLAME-RETARDANT COATING SYSTEM PREVIOUSLY PAINTED WOOD (EXTERIOR)

- Standard: To BS EN 13501.

- Manufacturer: Thermoguard UK Limited. .

  - Product reference: Timbercoat - Fire protection system for internal wood.

- Reaction to fire: Euro Class B (National Class 0 surface spread of flame).

- Surfaces: Previously painted wood - as schedule.

  - Preparation: As recommended by manufacturer.

- Base coats: Thermoguard Timbercoat Intumescent Basecoat. - Number of coats: 1.

- Finishing coats: Thermoguard Smoke & Flame Retardant Dualcoat. - Number of coats: 2

- Application: As recommended by manufacturer.

  - Number of coats (total): 3.

- Colour: As schedule.

- Certification: Provide manufacturers certificate of supply.

172E	FLAME-RETARDANT COATING SYSTEM PREVIOUSLY VARNISHED / STAINED WOOD (EXTERIOR)

- Standard: To BS EN 13501.

- Manufacturer: Thermoguard UK Limited. .

  - Product reference: Fire Varnish - Fire protection system for exterior wood..

- Reaction to fire: Euro Class B (National Class 0 surface spread of flame).

- Surfaces: Previously stained or varnished wood - as schedule. - Preparation: As recommended by manufacturer.

- Base coats: Thermoguard Fire Varnish Intumescent Basecoat. - Number of coats: 1.

- Finishing coats: Thermoguard Fire Varnish Overcoat. - Number of coats: 2

- Application: As recommended by manufacturer.

  - Number of coats (total): 3.

- Colour: As schedule.

- Certification: Provide manufacturers certificate of supply.

175A	PROTECTIVE COATING METAL SURFACES: INTERNAL OR EXTERNAL

- Manufacturer: As clause 210A.

  - Product reference: Water Based Gloss.

- Surfaces: Previously painted and uncoated metal surfaces - as schedule.

  - Preparation: Cleaner & Degreaser, as recommended by manufacturer.

- Initial coats: Water based metal primer. - Number of coats: 1.

- Undercoats: Waterbased undercoat. - Number of coats: 1.

- Finishing coats: Water based gloss. - Number of coats: 1.

- Application: As recommended by manufacturer. - Number of coats (total): 3.

## GENERAL

210A	COATING MATERIALS

- Manufacturer: Obtain materials from any of the following: - Johnstone's Trade Paints - a brand of PPG Industries..

- Crown Trade, product of Crown Paints Ltd. - Dulux Trade, brand of AkzoNobel.

- Selected manufacturers: Submit names before commencement of any coating work.

215	HANDLING AND STORAGE

- Coating materials: Deliver in sealed containers, labelled clearly with brand name, type of material and manufacturer's batch number.

- Materials from more than one batch: Store separately.

240	SURFACES NOT TO BE COATED

Door hinges, intumescent fire seals and smoke seals within door frames or door edges .

250	SURFACES TO BE CLEANED BUT NOT COATED

As schedule .

280	PROTECTION

•	'Wet paint' signs and barriers: Provide where necessary to protect other operatives and general public, and to prevent damage to freshly applied coatings.

## PREPARATION

400	PREPARATION GENERALLY

- Standard: In accordance with BS 6150.

- Refer to any pre-existing CDM Health and Safety File.

- Refer to CDM Construction Phase Plan where applicable.

- Suspected existing hazardous materials: Prepare risk assessments and method statements covering operations, disposal of waste, containment and reoccupation, and obtain approval before commencing work.

- Preparation materials: Types recommended by their manufacturers and the coating manufacturer for the situation and surfaces being prepared.

- Substrates: Sufficiently dry in depth to suit coating.

- Efflorescence salts: Remove.

- Dirt, grease and oil: Remove. Give notice if contamination of surfaces/ substrates has occurred.

- Surface irregularities: Remove.

- Joints, cracks, holes and other depressions: Fill flush with surface, provide smooth finish.

- Dust, particles and residues from preparation: Remove and dispose of safely.

- Water based stoppers and fillers:

  - Apply before priming unless recommended otherwise by manufacturer. - If applied after priming: Patch prime.

- Oil based stoppers and fillers: Apply after priming.

- Doors, opening windows and other moving parts:

  - Ease, if necessary, before coating. - Prime resulting bare areas.

420	FIXTURES AND FITTINGS

- Removal: Before commencing work remove: Coverplates, grilles, wall clocks, and other surface mounted fixtures .

- Replacement: Refurbishment as necessary, refit when coating is dry.

425	IRONMONGERY

- Removal: Before commencing work remove ironmongery from surfaces to be coated.

- Hinges: Do not remove.

- Replacement: Refurbish as necessary; refit when coating is dry.

430	EXISTING IRONMONGERY

•	Refurbishment: Remove old coating marks. Clean and polish.

440	PREVIOUSLY COATED SURFACES GENERALLY

- Preparation: In accordance with BS 6150, clause 11.5.

- Contaminated or hazardous surfaces: Give notice of:

  - Coatings suspected of containing lead.

  - Substrates suspected of containing asbestos or other hazardous materials.

- Suspected existing hazardous materials: Prepare risk assessments and method statements covering operations, disposal of waste, containment and reoccupation, and obtain approval before commencing work.

- Significant rot, corrosion or other degradation of substrates.

- Removing coatings: Do not damage substrate and adjacent surfaces or adversely affect subsequent coatings.

- Loose, flaking or otherwise defective areas: Carefully remove to a firm edge.

- Alkali affected coatings: Completely remove.

- Retained coatings:

  - Thoroughly clean to remove dirt, grease and contaminants. - Gloss coated surfaces: Provide key.

- Partly removed coatings:

  - Additional preparatory coats: Apply to restore original coating thicknesses. - Junctions: Provide flush surface.

- Completely stripped surfaces: Prepare as for uncoated surfaces.

456	PREVIOUSLY COATED SURFACES - BURNING OFF

Risk assessment and method statement: Prepare, and obtain approval before commencing work.

- Adjacent areas: Protect from excessive heat and falling scrapings.

- Exposed resinous areas and knots: Apply two coats of knotting.

- Removed coatings: Dispose of safely.

461	PREVIOUSLY COATED WOOD

- Degraded or weathered surface wood: Take back to provide suitable substrate.

- Degraded substrate wood: Repair with sound material of same species.

- Exposed resinous areas and knots: Apply two coats of knotting.

471	PREPRIMED WOOD

•	Areas of defective primer: Take back to bare timber.

481	UNCOATED WOOD

- General: Provide smooth, even finish with arrises and moulding edges lightly rounded or eased.

- Heads of fasteners: Countersink sufficient to hold stoppers/fillers.

- Resinous areas and knots: Apply two coats of knotting.

490	PREVIOUSLY COATED STEEL

- Defective paintwork: Remove to leave a firm edge and clean bright metal.

- Sound paintwork: Provide key for subsequent coats.

- Corrosion and loose scale: Take back to bare metal.

- Residual rust: Treat with a proprietary removal solution.

- Bare metal: Apply primer as soon as possible.

- Remaining areas: Degrease.

500	PREPRIMED STEEL

• Areas of defective primer, corrosion and loose scale: Take back to bare metal. Reprime as soon as possible.

511	GALVANIZED, SHERARDIZED AND ELECTROPLATED STEEL

- White rust: Remove.

- Pretreatment: Apply one of the following:

  - Mordant solution to blacken whole surface.

  - Etching primer recommended by coating system manufacturer.

521	UNCOATED STEEL - MANUAL CLEANING

- Oil and grease: Remove.

- Corrosion, loose scale, welding slag and spatter: Remove.

- Residual rust: Treat with a proprietary removal solution.

- Primer: Apply as soon as possible.

541	UNCOATED ALUMINIUM/ COPPER/ LEAD

- Surface corrosion: Remove and lightly key surface.

- Pretreatment: Etching primer if recommended by coating system manufacturer.

552	UNCOATED PVC-U

•	Dirt and grease: Remove. Do not abrade surface.

570	UNCOATED MASONRY/ RENDERING

•	Loose and flaking material: Remove.

580	UNCOATED PLASTER

- Nibs, trowel marks and plaster splashes: Scrape off.

- Overtrowelled 'polished' areas: Key lightly.

590	UNCOATED PLASTERBOARD

Depressions around fixings: Fill with stoppers/ fillers.

601	UNCOATED PLASTERBOARD - TO RECEIVE TEXTURED COATING

•	Joints: Fill, tape and feather out with materials recommended by textured coating manufacturer.

611	WALL COVERINGS

- Retained wall coverings: Check that they are in good condition and well adhered to substrate.

- Previously covered walls: Wash down to remove paper residues, adhesive and size.

622	ORGANIC GROWTHS

- Dead and loose growths and infected coatings: Scrape off and remove from site •	Treatment biocide: Apply appropriate solution to growth areas and surrounding surfaces.

- Residual effect biocide: Apply appropriate solution to inhibit re-establishment of growths.

645	SEALING INTERNAL MOVEMENT JOINTS

- General: To junctions of walls and ceilings with architraves, skirtings and other trims.

- Sealant: Water-borne acrylic.

  - Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

  - Preparation and application: As section Z22.

## APPLICATION

711	COATING GENERALLY

- Application standard: In accordance with BS 6150, clause 9.

- Conditions: Maintain suitable temperature, humidity and air quality during application and drying.

- Surfaces: Clean and dry at time of application.

- Thinning and intermixing of coatings: Not permitted unless recommended by manufacturer.

- Overpainting: Do not paint over intumescent strips or silicone mastics.

- Priming coats:

  - Thickness: To suit surface porosity.

  - Application: As soon as possible on same day as preparation is completed.

- Finish:

  - Even, smooth and of uniform colour.

  - Free from brush marks, sags, runs and other defects. - Cut in neatly.

- Doors, opening windows and other moving parts: Ease before coating and between coats.

- WORKSHOP COATING OF CONCEALED JOINERY SURFACES

  - General: Apply coatings to all surfaces of components.

- SITE COATING OF CONCEALED JOINERY SURFACES

  - General: After priming, apply additional coatings to surfaces that will be concealed when fixed in place.

    - Components: As schedule.

    - Additional coatings: One undercoat.

740	CONCEALED METAL SURFACES

• General: Apply additional coatings to surfaces that will be concealed when component is fixed in place.

- Components: As schedule.

- Additional coatings: Black paint to BS 1070.

751	STAINING WOOD

- Primer: Apply, if recommended by stain manufacturer.

- Application: Apply in flowing coats and brush out excess stain to produce uniform appearance.

760	VARNISHING WOOD

First coat: Thin with plant oil based thinner.

- Brush well in and lay off avoiding aeration.

•	Subsequent coats: Provide light key along the grain between coats.

770	EXTERNAL DOORS

•	Bottom edges: Prime and coat before hanging doors.

780	BEAD GLAZING TO COATED WOOD

•	Before glazing: Apply first two coats to rebates and beads.

# M61 Intumescent coatings for fire protection of steelwork

To be read with Preliminaries/General conditions

## PROTECTIVE COATING SYSTEMS

120	ON SITE COATING TO EXISTING STEEL INTERNALLY

- Use/ Location: Exposed internal faces of columns, beams and purlins, but excluding cladding rails - refer to schedule.

- Fire performance: To BS EN 13501-1 and -2, as clause 202.

- Preparation: Manual cleaning.

- Intumescent coating system:

  - Manufacturer: Submit proposals.

Product reference: Submit proposals.

  - Primer:

Type: Submit proposals.

  - Intumescent coat:

Type: Submit proposals

Finish: Non-visible areas: Basic; Visible areas: Normal decorative; and Visible areas: High decorative.

  - Top sealer coat:

Type: Submit proposals. Colour: As schedule.

- Bolt head/ Nut protection: As main steelwork.

## PERFORMANCE AND GENERAL REQUIREMENTS

203	FIRE PERFORMANCE TO BS 476

•	Fire resistance to BS 476-21: 120 minutes unless otherwise specified.

205	VALIDATION OF MATERIALS

•	Project-specific evaluation of intumescent coating materials:

- Standard: In accordance with BS EN 16623, clause 4. - Test results: Submit on request.

210	WORKING PROCEDURES

- Standard: In accordance with BS EN 16623.

- Give notice: Before commencing surface preparation and coating application.

- Quality control: Record project specific procedures for surface preparation and coating application.

215	WORKING CONDITIONS

- General: Maintain manufacturer's recommeded temperature, humidity and air quality conditions during application and drying.

- Surface condition: Clean and dry at time of coating application.

250	SPRAYED COATING APPLICATION ON SITE

- Standard: In accordance with BS EN 16623.

- Spray drift: Minimize.

- Uncoated areas of steel: As schedule.

- Masking: Protect designated adjacent surfaces. - Designated surfaces: As schedule.

270	INSPECTION

- Permit intumescent manufacturer to: - Inspect work in progress.

  - Inspect quality control records.

  - Take dry film thickness and other measurements. - Take samples of products.

- Intumescent manufacturer's inspection reports: Submit without delay.

## PREPARATION OF SURFACES

330	EXISTING STEEL - MANUAL CLEANING

- Preparation: Remove oil, grease and contaminants.

- Loose or unsound coatings: Remove to a firm edge.

- Finish: To BS EN ISO 8501-1, preparation grade St2. Leave a clean but unpolished dry surface.

- Primer: Apply as soon as possible after cleaning and before gingering or blackening appears. Remove coating edges that lift as a result of priming, and reprime.

## APPLICATION OF COATINGS

410	INTUMESCENT COATING DRY FILM THICKNESS (DFT)

- Applicable coatings: Primer, intumescent and top sealer coat.

- Required dft: Determine for every steel member to give specified period of fire resistance. Use intumescent coating manufacturer's current published loading tables.

  - Special sections and partial fire exposure conditions: Obtain required dft in writing from manufacturer.

- Schedule and drawings: Submit at least two weeks before starting work.

  - Schedule content: Member sizes, weights/ thicknesses, loading conditions, etc. showing, for each variant, the exposed perimeter/ sectional area (Hp/A) ratio and required dft.

  - Drawing content: Steelwork drawings marked in colour to show required dft for each member.

420	MEASUREMENT OF INTUMESCENT DFT

- Primer dft: Determine average dft (for deduction from total dft after application of intumescent).

- Intumescent dft: Determine at:

  - 500 mm centres along each coated plane of universal sections (8 planes), and rectangular hollow sections (4 planes).

  - 125 mm centres along coated circular hollow sections, spread evenly around circumference.

- Acceptance standard:

  - Average intumescent dft: Not less than required dft (exclusive of primer and top sealer).

  - Local intumescent dft: Not less than 80% of required dft. Areas greater than 100 mm equivalent diameter with a dft of less than 80% of required dft must be brought up to thickness.

440	BASIC FINISH

•	Definition: Reasonably smooth and even. Orange peel, other texture, minor runs and similar minor defects are acceptable.

450	NORMAL DECORATIVE FINISH

•	Definition: Good standard of cosmetic finish generally, when viewed from a distance of 5 m or more. Minor orange peel or other texture is acceptable.

460	HIGH DECORATIVE FINISH

•	Definition: High standard of evenness, smoothness and gloss when viewed from a minimum distance of 2 m.

490	TOP SEALER COAT

•	Application: To achieve dft recommended by manufacturer and to give an even, solid, opaque appearance, free from runs, sags and other visual defects.

## COMPLETION

530	RECORDS OF INTUMESCENT APPLICATION

•	On completion of intumescent work, submit:

- Accurate surface preparation, coating and intumescent application records.

- Fire resistance certificates.

- Intumescent manufacturer's recommendations for maintenance and overcoating.

# N10 General fixtures/ furnishings/ equipment

To be read with Preliminaries/General conditions.

## PRODUCTS

195A	POSTER DISPLAY FRAMES: SIZE A4 FOR FIRE ACTION NOTICES

- Manufacturer: Contractors choice.

  - Product reference: A4 Poster Snap Frame.

- Type: Wall mounted, front loading with snap action secure sprung frame..

- Poster size: 210 x 297 mm (A4).

  - Visible area size (minimum):  190 x 277 mm. - Overall size: 240 x 330 x 11 mm.

- Back panel:  Styrene.

- Frame: 25 mm, mitred corners. - Material: Aluminium.

  - Finish/ Colour: Satin silver anodized.

- Fixing:  Wall mounted through pre-drilled fixing holes, fixings to suit background. - Orientation:  Portrait.

- Accessories/ Other requirements: Complete with anti-glare UV resistant PVC poster cover.

195B	POSTER DISPLAY FRAMES: SIZE A3 FOR ZONE PLANS

- Manufacturer: Contractors choice.

  - Product reference: A3 Poster Snap Frame.

- Type: Wall mounted, front loading with snap action secure sprung frame..

- Poster size: 420 x 297 mm (A3).

  - Visible area size (minimum):  400 x 270 mm. - Overall size: 450 x 330 x 11 mm.

- Back panel:  Styrene.

- Frame: 25 mm, mitred corners. - Material: Aluminium.

  - Finish/ Colour: Satin silver anodized.

- Fixing:  Wall mounted through pre-drilled fixing holes, fixings to suit background. - Orientation:  As achedule.

- Accessories/ Other requirements: Complete with anti-glare UV resistant PVC poster cover.

# N15 Internal fire and safety signage systems

GENERAL

## SYSTEM PERFORMANCE

205	DESIGN OF INTERNAL SIGNAGE SYSTEMS FOR ESCAPE ROUTE

- Design: Complete detailed design and submit before commencing work.

- Content: Signs including facing information, components, inserts, accessories and fixings necessary to complete the system.

- Proposals: Submit drawings, schedules, technical information, calculations and manufacturer's literature before commencing work.

210	GENERAL REQUIREMENTS

- Signage and way guiding system design: determined in accordance with BS 5499-4 or BS ISO 16069.

  - For fire escape and evacuation signage: In accordance with: BS 5499-4 or BS ISO 16069.

  - For way guiding systems: In accordance with BS ISO 16069.

  - For safety signs other than escape route signage: In accordance with: BS 5499-10.

- Comply with the requirements of: Fire Risk Assessment.

220	SIGN DESIGN AND FORMAT FOR ESCAPE ROUTE

- Format: As schedule - In accordance with BS EN ISO 7010.

- Geometric shapes, colours and layout: In accordance with BS ISO 3864-1.

- Design principles for graphical symbols: In accordance with BS ISO 3864-3.

- Colorimetric and photometric properties of safety sign materials: In accordance with BS ISO 3864-4.

- Water safety: In accordance with BS ISO 20712-1.

## PRODUCTS

330	PLASTICS SHEET FOR ESCAPE ROUTE SIGNS

- Material: ABS.

- Manufacturer: Contractor's choice.

- Product reference: Submit proposals.

- Component thickness: 2 mm.

- Finish: Manufacturer's standard.

- Perimeters: Manufacturer's standard.

- Supports/ Fixings: Adhesive, screw fix, ceiling, suspended wire - refer to schedule for requirement.

- Accessories: Clip connectors to suspended ceiling grid / Magnetic hanging kit - refer to schedule for requirement.

## EXECUTION

610	FIXING SIGNS GENERALLY

- Installation:

- Secure, plumb and level.

- Fasteners and adhesives: As section Z20.

- Strength of fasteners: Sufficient to support live and dead loads.

- Fixings showing on surface of sign: Must not detract from the message being displayed.

## COMPLETION

910	DOCUMENTATION

•	Submit:

- Manufacturer's maintenance instructions.

- Guarantees, warranties, test certificates, record schedules and logbooks.

# P10 Sundry insulation/ proofing work

SUNDRY INSULATION/ PROOFING WORK

To be read with Preliminaries/ General conditions

## TYPES OF INSULATION

430A	WIRED MINERAL WOOL FLEXIBLE CAVITY BARRIERS

- Standard: to BS 476: Part 22.

  - Reaction to fire classification of A1 as defined in BS EN 13501:1. - LPCB and LUL approved.

- Manufacturer: ROCKWOOL Ltd.

  - Product reference: ROCKWOOL Fire Barrier. - Material: Wire reinforced mineral wool mats.

- Resistance to fire:

  - Integrity: As schedule.

  - Insulation: As schedule.

- Thickness: 50 mm or 60 mm - as schedule.

- Width: 1000 mm.

- Length: 3500 mm or 4000 mm.

- Facing: Plain, Foil facing 1 side or Foil facing 2 sides - as schedule.

- Mesh: 1 side or 2 sides - as schedule.

- Accessories: ROCKWOOL Fire Barrier Angle Support and Fire Barrier Clamping Plate.

- Installation requirements:

  - Vertical joints: 100 mm minimum over lapped joints, wire stitched.

  - Horizontal joints (drop height extensions): As vertical joints.

  - Fasteners: Staples at maximum 150 mm centres. Fold cavity barrier if necessary to ensure a tight fit.

  - Joints and intersections: Butted, no gaps.

# P12 Fire stopping systems

To be read with Preliminaries/ General conditions.

## GENERAL

130	FIRE STOPPING SYSTEM TO INDIVIDUAL SERVICES PENETRATIONS AS SCHEDULE

- Fire resistance: As clause 240.

- Penetration seal: As chosen system manufacturers instructions. - Size: Depth - as system manufacturers instructions.

- Gap sealer: As system manufacturers instructions.

- Capping sealant: As system manufacturers instructions. - Colour: As schedule.

160	LINEAR GAP SEALING AS SCHEDULE

- Fire resistance: As clause 240.

- Gap width or height (nominal): As schedule.

- Gap filler: MR - mineral wool, PE - polyethylene rod or FR - fire resistant foam in accordance with system manufacturers instructions.

- Capping sealant: In accordance with system manufacturers instructions. - Colour: As schedule.

## PRODUCTS

240	FIRE PERFORMANCE COMPARTMENT WALLS AND FLOORS

- Resistance to fire: To BS 476-20 and -22, minimum 60 minutes integrity and insulation unless otherwise specified.

- Reaction to fire: In accordance with Building Regulations, Class 0.

- Smoke resistance:

  - Air leakage rate (maximum): 3 m³/m²·hr.

245A	PERMISSIBLE PRODUCTS, SYSTEMS AND INSTALLATION

- Obtain materials from any of the following manufacturers systems:

  - Manufacturer / system: ROCKWOOL Ltd - ROCKWOOL FIREPRO Fire Protection Systems. - Manufacturer / system: HILTI (UK) Ltd - HILTI Firestop and Fire Protection Systems.

- Selected manufacturers: Submit names before commencement of any coating work.

- Third Party Certified Installer: As clause 610.

- Certification: Certificate of conformity to be provided upon completion of works with schedule of referenced fire stopping details.

305	PRODUCT CERTIFICATION

- Certification: For products specified generically, submit evidence of compliance with the specification.

- Acceptable evidence: Listing in LPCB Register or Agrément certificate.

330	FLEXIBLE INTUMESCENT GAP SEALER

- Manufacturer: As clause 245A.

  - Product reference: Contractor's choice .

- Strip width: Wider than joint width as manufacturers instructions.

335A	FIRESTOP FOAM: RIGID

- Manufacturer: Hilti (Gt Britain) Ltd. - Product reference: CP 620.

  - Material: Two-component polyurethane foam.

  - Description: Rigid and fast-curing firestop foam with water resistance for fire, smoke and moisture barrier around cable and mixed penetrations.

  - Suitable substrates: Drywall, concrete and masonry.

- Fire resistance: Up to three hours, dependent on substrate and application.

335B	FIRESTOP FOAM: FLEXIBLE / RE-PENETRABLE

- Manufacturer: Hilti (Gt Britain) Ltd. - Product reference: CFS-F FX.

  - Material: Two-component polyurethane foam.

  - Descripion: Flexible firestop foam for fire and smoke barrier around cable and mixed penetrations - Re-penetrable to allow future cable capacity increases. - Suitable substrates: Drywall, concrete and masonry.

- Fire resistance: Up to two hours, dependent on substrate and application.

335C	INTUMESCENT POLYURETHANE (PU) EXPANDING FOAM

- Standard: To BS 476-20 or BS EN 1366-4.

- Manufacturer: Contractor's choice .

  - Product reference: Contractor's choice .

- Application: Frame to wall joints, as schedule.

338	INTUMESCENT MASTIC

•	Manufacturer: As clause 245A.

- Product reference: Contractor's choice .

340	INTUMESCENT MORTAR

•	Manufacturer: As clause 245A.

- Product reference: Contractor's choice .

342	FIRE RESISTING MORTAR

•	Manufacturer: As clause 245A.

- Product reference: Contractor's choice .

360	MINERAL WOOL RIGID BATTS

- Standard: To BS EN 13162.

- Surface treatment: Ablative coating

- Manufacturer: As clause 245A.

  - Product reference: Contractor's choice .

- Recycled content: Contractor's choice.

370A	PIPE WRAPS/ COLLARS/ INTUMESCENT AND INSULATED SLEEVES

- Type: As schedule.

- Manufacturer: As clause 245A.

  - Product reference: Contractor's choice.

385	SEALANT BACKING MATERIAL

•	Manufacturer: As clause 245A.

- Product reference: Contractor's choice.

390	SEALANT

- Type: Contractors choice.

- Manufacturer: As clause 245A.

- Product reference: Contractor's choice.

## EXECUTION

610	THIRD PARTY CERTIFIED INSTALLER

- Certification: For the technical competency of the installer of the evidence of compliance with a third party installation certification scheme.

- Acceptable evidence: FIRAS Installer Certification, LPCB Certification and UKAS Accreditation Certificate.

620	WORKMANSHIP GENERALLY

- Gaps: Seal between building elements and services, to provide effective resistance to fire and the passage of smoke. Allow for capping sealants where required. Finish flush with surrounds.

- Adjacent surfaces: Prevent overrun of sealant or mortar on to finished surfaces.

650	INSTALLING FLEXIBLE INTUMESCENT GAP SEALER

- Fitting of strips: Compress strips and fit into gap, so that, as they decompress, the strips wedge themselves in the void.

- Shrink wrapping: As manufacturers instructions.

- Joints:

- Ends of strips: Fit intumescent 'end piece' at both ends of run of stop laminate. - Joints between strips: Fit two intumescent 'end pieces' at each butt joint.

660	APPLYING INTUMESCENT FOAM

- New joints: Remove builder's debris, mortar droppings, grease, and other contaminants.

- Old joints: Clean and remove existing sealant from each joint.

- Priming: Lightly moisten substrate with water.

- Application: Fill joint to approximately half its depth, and allow foam to expand to face of joint.

- Trimming: Trim excess foam to give a neat, flush appearance.

670	APPLYING INTUMESCENT MORTAR

- Sequence: Install mortar after services are permanently installed.

- Loose dust and combustible materials: Remove from the opening.

- Shuttering: Install suitable shuttering panels to the faces of the opening.

- Temperature: Do not apply mortar when it could be damaged by frost.

- Powder:water ratio: As manufacturers instructions.

- Mortar cure: Do not disturb mortar before final set has taken place.

- Shuttering: Remove after mortar has cured.

710	INSTALLING MINERAL WOOL BATTS

- Installing batts: Fit tight into void between the penetrating services and the surrounding construction to form a solid barrier.

- Brackets: As manufacturers instructions.

Bracket fixing: As manufacturers instructions.

- Face of batts: Flush with the surface of wall, floor or soffit.

- Joints between batts: Close butt joints; seal with acoustic intumescent sealant or as manufacturers instructions.

- Gaps between services and barrier: Seal with fire resisting sealant.

730	FIXING PIPE COLLARS

- Collar fixing: Plugged and screwed as recommended by manufacturer.

- Gap around collar: Seal with gap filler and sealant.

- Length of wraps: Project 50 mm from each side of the element or as manufacturers instructions.

740	INSERTING SEALANT BACKING MATERIAL

- Preparation: Removed debris from service penetration.

- Installation: Insert joint filler to depth as manufacturers instructions leaving sufficient depth to apply sealant.

745	APPLYING SEALANTS GENERALLY

•	Application: As section Z22.

750	APPLYING CAPPING SEALANT

- Preparation: As manufacturers instructions.

- Priming: Primer recommended by sealant manufacturer.

- Depth of sealant: As manufacturers instructions.

- Temperature: Do not apply water based sealants when they could be damaged by frost.

## COMPLETION

910	CLEANING

- Masking tapes: Remove.

- Cleaning: Clean off splashes and droppings. Wipe down finishes.

920	INSPECTION

•	Notice for inspection (minimum): 3 working days .

# P20 Unframed isolated trims/ skirtings/ sundry items

To be read with Preliminaries/General conditions

110A	SOFTWOOD ARCHITRAVE FOR FIRE DOOR FRAME / WALL JOINTS

- Quality of wood and fixing: To BS 1186-3.

  - Species: Contractor's choice. - Class: CSH.

- Moisture content at time of fixing: 9-13%.

- Preservative treatment: Not required - unless otherwise specified.

- Fire rating: Not applicable.

- Profile: To match existing or chamfered.

  - Finished size: 19 x 70 x 15 mm unless otherwise specified.

  - Architraves to be minimum 15 mm thick with 15 mm overlap on frame and wall.

- Finish as delivered: Prepared and primed as M60.

- Fixing: Pneumatically fired pins 200 mm nominal centres.

115A	SOFTWOOD SKIRTINGS GENERALLY

- Quality of wood and fixing: To BS 1186-3.

  - Species: Contractor's choice. - Class: CSH.

- Moisture content at time of fixing: 9-13%.

- Preservative treatment: Not required - unless otherwise specified.

- Fire rating: Not applicable.

- Profile: To match existing or chamfered.

  - Finished size: 19 x 95 x 15 mm unless otherwise specified.

- Finish as delivered: Prepared and primed as M60.

- Fixing: Adhesive as section Z20.

120	HARDWOOD QUADRANT FOR FIRE DOOR FRAME / WALL JOINTS

- Quality of wood and fixing: To BS 1186-3.

  - Species:   Contractors choice. - Class: CSH.

- Moisture content at time of fixing: 9-13%.

- Preservative treatment: Not required - unless otherwise specified.

- Fire rating: Not applicable.

- Profile: Quadrant.

  - Finished size: As schedule, minimum 15 mm.

- Finish as delivered: Sanded.

- Fixing: Pneumatically fired pins 200 mm nominal centres.

# P21 Door/ window ironmongery

To be read with Preliminaries/ General conditions.

## PRE-TENDER

10	QUANTITIES AND LOCATIONS

- Quantities and locations of ironmongery are given in the schedules .

- Fixing: As sections L10 and L20.

## GENERAL

170	IRONMONGERY FOR FIRE DOORS

- Relevant products: Ironmongery fixed to, or morticed into, the component parts of a fire resisting door assembly.

- Compliance: Ironmongery included in successful tests to BS 476-22 or BS EN 1634-1 on door assemblies similar to those proposed.

- Certification: Submit CERTIFIRE certificates .

- Melting point of components (except decorative non functional parts): 800°C minimum.

## DOOR HANGING DEVICES

310A	SINGLE AXIS DOOR HINGES FIRE RESISTING DOORS AS SCHEDULE: FD30 & FD60

- Standard: To BS EN 1935.

  - Hinges to doors on escape routes and fire/ smoke control doors: CE marked.

  - Tested to BS EN 1935: 2002, grade 13 to 200,000 cycles on 120kg door mass.  Also cycle tested to 500,000 cycles.

  - Fire tested to BS EN 1634-1 with assessment for use on timber fire doors with intumescent protection up to FD30 and FD60 provided they are fitted in accordance with the guidelines detailed in IFCA/06252

  - Approvals: Certifire CF5291.

- Manufacturer: ASSA ABLOY Opening Solutions UK & Ireland . - Product reference: UNION PowerLOAD 603 .

- Type: Double ball bearing butt, square corner - unless otherwise stated .

- Size: 102 x 88 mm .

- Material/ finish: 1.4301 (304) stainless steel .

- Hinge grade: 13 .

- Other requirements: Intumescent kit J-603-IK suitable for 30 and 60 minute timber fire doors - ordered as a separate item .

## DOOR OPERATING DEVICES

410A	OVERHEAD DOOR CLOSERS FLAT ENTRANCE DOORS AND DOORS ON ESCAPE ROUTES

- Standard: To BS EN 1154.

  - Door closing devices to fire/ smoke control doors: CE marked.

  - Fire tested to EN1634 on timber doors to achieve a 2 hour fire rating. - Approvals: Certifire CF5291.

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: Briton 2300 Series - Closer with backcheck; all-over softline cover..

- Type: CAM action slide arm.

- Fixing: Door mounted (body) - Pull side/ Push side, as schedule.

- Power size: Adjustable 2-4.

- Other functions: Back check.

- Finish: SSS Satin stainless steel.

- Operational adjustment:

  - Variable power: Matched to size, weight and location of doors.

  - Latched doors: Override latches and/ or door seals when fitted.

  - Unlatched doors: Hold shut under normal working conditions. - Closing against smoke seals of fire doors: Positive. No gaps.

471A	ELECTROMAGNETIC HOLD OPEN DEVICES FIRE RESISTING DOORS AS SHEDULE

- Standard: To BS EN 1155.

  - Electromagnetic devices to fire/ smoke control doors: CE marked.

  - Fire tested to EN 1634 for use on fire doors up to 2hr timber / 4hr steel. - Approvals: Certifire CF388.

- Manufacturer: Allegion (UK) Ltd..

  - Product reference: Briton 2700 Series Electromagnetic hold open closer with softline cover.

- Type: Electromagnetic track arm closer with integral hold open.

- Fixing: Door mounted (body) - Pull side/ Push side, as schedule.

- Material/ finish: SSS - Satin stainless steel.

- Power size: Adjustable spring power 3-4.

- Electric supply: 24 volts.

- Means of release: Alarm system and/ or failure of power supply.

- Test switch:  Integrated test switch simulates fire condition to check operation.

- Manual release: Manual override allows door to be pulled closed.

- Operational adjustment of integral closer:

  - Variable power: Matched to size, weight and location of doors.

  - Latched doors: Override latches and/ or door seals when fitted. - Unlatched doors: Hold shut under normal working conditions.

471B	ELECTRO-MAGNETIC HOLD-OPEN/ SWING-FREE  DEVICES

- Standard: To BS EN 1154, BS EN 1155 and the requirements of Building Regulations, Approved Document B: Fire Safety.

  - Electromagnetic devices to fire/ smoke control doors: CE marked.

- Manufacturer: dormakaba UK & Ireland.

  - Product reference: DORMA TS 73 EMF.

- Closer:

  - Spring strength: EN 4.

- Arm type: Free-swing.

- Mounting : Door leaf fixing.

- Finish: 01 – Silver.

- Accessories: Mounting backplate/ upstand bracket, and test switch as schedule.

## DOOR SECURING DEVICES

515A	EURO PROFILE MORTICE DEADLOCK FIRE DOORS AS SCHEDULE

- Standard: To BS EN 12209.

  - Locks to doors on escape routes and fire/ smoke control doors: CE marked.

  - To BS EN 1634--1 for 60 minutes timber fire doors and 4 hour steel fire doors. - Approvals: Certifire CF741

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: 5510.60.S - Mortice euro profile cylinder deadlock with square forend..

- Material / finish: SSS Satin stainless steel forend and strike plate.

- Backset: 60 mm.

- Deadbolt: 22 mm deadbolt throw (single turn of key or cylinder turn).

- Accessories: As schedule - Box strike / 13 mm rebate kit / 25 mm rebate kit.

- Intumescent protection:  [When instaled to fire doors, fit with lock protection kit to BS 476-22, 60 minute resistance to fire].

515B	EURO PROFILE MORTICE SASHLOCK FIRE DOORS AS SCHEDULE

- Standard: To BS EN 12209.

  - Locks to doors on escape routes and fire/ smoke control doors: CE marked.

  - To BS EN 1634--1 for 60 minutes timber fire doors and 4 hour steel fire doors. - Approvals: Certifire CF741

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: 5520.60.S - Mortice euro profile cylinder sashlock with square forend..

- Finish: SSS Satin stainless steel forend and strike plate.

- Backset / centres: 60 mm backset, 72 mm centres.

- Deadbolt: 22 mm deadbolt throw (single turn of key or cylinder turn).

- Lever furniture: Suitable for unsprung lever operation.

- Accessories: As schedule - Box strike / 13 mm rebate kit / 25 mm rebate kit.

- Intumescent protection:  [When instaled to fire doors, fit with lock protection kit to BS 476-22, 60 minute resistance to fire].

515C	EURO PROFILE MORTICE NIGHTLATCH FIRE DOORS AS SCHEDULE

- Standard: To BS EN 12209.

  - Locks to doors on escape routes and fire/ smoke control doors: CE marked.

  - To BS EN 1634--1 for 60 minutes timber fire doors and 4 hour steel fire doors. - Approvals: Certifire CF741.

- Operation: Nightlatch function operated by a half set of lever handles - internal lever retracts latchbolt; external single cylinder retracts latchbolt with use of key.

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: 5550.60.S - Euro profile cylinder nightlatch with radius forend and hold-back..

- Finish: SSS Satin stainless steel forend and strike plate.

- Backset / centres: 60 mm backset, 72 mm centres.

- Snib: Integral holdback snib.

- Lever furniture: Suitable for unsprung lever operation.

- Accessories: As schedule - Box strike / 13 mm rebate kit / 25 mm rebate kit.

- Intumescent protection:  [When instaled to fire doors, fit with lock protection kit to BS 476-22, 60 minute resistance to fire].

515D	MORTICE LATCH FIRE DOORS AS SCHEDULE

- Standard: To BS EN 12209.

  - Locks to doors on escape routes and fire/ smoke control doors: CE marked.

  - To BS EN 1634--1 for 60 minutes timber fire doors and 4 hour steel fire doors. - Approvals: Certifire CF741.

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: 5540.60.S - Mortice latch with square forend.

- Finish: SSS Satin stainless steel forend and strike plate.

- Backset: 60 mm.

- Lever furniture: Suitable for unsprung lever operation.

- Accessories: As schedule - Box strike / 13 mm rebate kit / 25 mm rebate kit.

- Intumescent protection:  [When instaled to fire doors, fit with lock protection kit to BS 476-22, 60 minute resistance to fire].

520A	EURO PROFILE CYLINDER DEADLOCK / SASHLOCK / NIGHTLATCH LOCKCASES

- Standard: To EN 1303.

  - Key security: grade 4: (movable pins: 5).

  - Fire resistance:  [Grade 1 - suitable for use on fire/smoke resisting assemblies]

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: Briton C2000.

- Type: Single cylinder / Double cylinder / Cylinder and turn.

- Keying: Keyed to differ (KD) or keyed alike (KA) - refer to schedule.

- Number of keys: 3 supplied as standard - refer to schedule

530A	MULTIPOINT LOCKING SYSTEM FLAT ENTRANCE DOORS

- Standard: To PAS 24.

  - Endurance tested to 200,000 cycles

  - Tested to BS EN 1670 Grade 4  (240 hours Natural Salt Spray)

  - 10 year mechanical guarantee

- Manufacturer: ASSA ABLOY Opening Solutions UK & Ireland.

  - Product reference: YALE AutoSecure multi-point locking system.

- Type: TBC - option i.e. YASL-3H45PL18W THREE HOOK, 45MM BACKSET, PL18 20MM FACEPLATE.

- Backset: TBC - 35 or 45 mm backset options.

- Follower: Single (not split).

- Material / finish: Stainless steel faceplate/ locking plates.

- Snib: Integral holdback snib.

- Intumescent protection:  [Fit with lock protection kit to BS 476-22, 60 minute resistance to fire].

535A	EURO PROFILE CYLINDER MULTIPOINT LOCKING SYSTEMS

Standard: BS EN 1303.

  - To BS 3621:2007 and PAS 24.

  - BSI Kitemark Approved - KM532920.

  - TS007 - 1 Star Cylinder.

  - Approvals: Secured by Design.

  - Key security: grade 6: (effective differs 100,000 / movable pins: 6).

  - Attack resistance: grade 2.

  - 10 year guarantee.

Manufacturer: ASSA ABLOY Opening Solutions UK & Ireland

  - Product reference: YALE KM Superior 1 Star Euro Profile Cylinder

  - Product option: TBC - i.e. KMT3030-NP - KM SUPERIOR EURO TURN - 30:10:30 (70mm) NICKEL

- Type: Euro cylinder and turn.

- Keying: Keyed to differ (KD).

- Number of keys: 3 supplied as standard.

571A	PUSH PAD EMERGENCY EXIT LATCH

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: Briton 581.BM Push Pad.

- Outside access device: Briton 1413E/LE - Lever variant, non-handed. -  Supplied with euro-profile cylinder as standard.

- Material:

  - Painted aluminium alloy/ aluminium cover. - Chrome aluminium alloy latch bolt.

- Accessories: As schedule:

  - Briton 574.AS.L additional side Pullman latch kit. - For LH doors.

  - Briton 574.AS.R additional side Pullman latch kit. - For RH doors.

  - Briton 574.S two side Pullman latched. - Non-handed.

  - Briton 574.S three side Pullman latched. - Non-handed.

  - Briton 574.V upper and lower Pullman latches. - Non-handed.

  - Briton 574.VS.L one upper and one side Pullman. - For LH doors.

  - Briton 574.VS.R one upper and one side Pullman latches. - For RH doors.

577A	PUSHBAR PANIC EXIT DEVICES

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: Briton 574.V two point locking rod kit for panic device with upper and lower pullmans.

- Finish: (BM) Black.

- Outside access device: Briton 1413E/LE.

- Accessories: Easy clean socket 574.STE.

582A	LEVER ACTION FLUSH BOLTS

- Standard: To BS EN 12051.

- Fire resistance:  [Grade 1 - suitable for use on fire/smoke resisting assemblies]

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: Lever action flush bolts.

- Type: 4735.S.20.202 - SS Lever action flush bolt, 202 x 20 mm.

- Keep plates: Fix flat shoot plates provided.

- Fixing: Fix using screws supplied.

- Material / finish: Satin stainless steel.

- Intumescent protection:  [When instaled to fire doors, fit with flush bolt protection kit to BS 476-22, 60 minute resistance to fire].

582B	SURFACE BOLTS

- Standard: To BS EN 12051.

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: Flat section surface bolt with extruded keep.

- Type:

  - AQ81 - 102mm Bolt Casing, Bolt Shoot Length - 25mm

  - AQ82 - 150mm Bolt Casing, Bolt Shoot Length - 25mm

  - AQ83 - 202mm Bolt Casing, Bolt Shoot Length - 25mm

  - AQ84 - 254mm Bolt Casing, Bolt Shoot Length - 25mm

- Operation / fixing: Flat slide bolt with integral ball an spring mechanism for positive location of bolt, fix horizonally with screws supplied.

- Fixing: Fix using screws provided.

- Material / finish: Brass, satin chrome finish.

## DOOR FURNITURE

610A	LEVER HANDLES ON BACKPLATE FLAT ENTRANCE DOORS

- Standard: To BS EN 1906.

  - TS007 2 star PAS 24.

  - Corrosion tested to BS EN 1670. Tested to 50,000 cycles (conforms to BS1906). Abusive load tested to BS 6462.

  - 10 year guarantee.

Manufacturer: Trojan Hardware & Design Limited .

  - Product reference: TROJAN TS007 2 Star Composite Lever Handle .

- Type: Flat pattern .

- Size: Backplate size 240 x 30mm .

- Material/ finish: Stainless steel, grade 1.4301 (304), chrome finish .

- Mounting: Rectangular sprung plate with hidden screw fixing .

610B	LEVER HANDLES ON ROSE FIRE DOORS AS SCHEDULE

- Standard: To BS EN 1906, Grade 3 category of use.

  - BS EN 1906 - Grade 7 durability (200,000 cycles).

  - BS EN 1670 Grade 3 corrosion resistance.

  - To BS EN 1634 on timber doors to achieve a 90 minute fire rating / 4 hour for metal doors. - Conforms to dimensional recommendations of BS 8300.

- Manufacturer: Allegion (UK) Ltd. .

  - Product reference: 4201.19.SS - Lever handle on rose, round bar return to door .

- Type: Round pattern (tubular) with return to door .

- Size: 19 mm diameter .

- Material/ finish: Satin stainless steel, grade 1.4301 (304) .

- Mounting: Sprung rose with bolt through fixing .

641	PULL HANDLES FIRE DOORS AS SCHEDULE

- Manufacturer: Allegion (UK) Ltd..

  - Product reference: D pull handle - Round bar section - 4721.20.300.

- Standard: To BS 8424. Shape: D handle .

- Diameter: 20 mm .

- Distance between centres: 300 mm .

- Material/ finish: Satin stainless steel, grade 1.4401 (316) .

- Mounting: Bolt through .

- Additional requirements: None .

641A	PULL HANDLES FIRE DOORS AS SCHEDULE

- Manufacturer: Allegion (UK) Ltd..

  - Product reference: D pull handle - Round bar section - 4721.20.200.

- Standard: To BS 8424. Shape: D handle .

- Diameter: 20 mm .

- Distance between centres: 200 mm .

- Material/ finish: Satin stainless steel, grade 1.4401 (316) .

- Mounting: Bolt through .

- Additional requirements: None .

670	PUSH PLATES FIRE DOORS AS SCHEDULE

- Manufacturer: Allegion (UK) Ltd. .

- Product reference: 4731.75.375 Push plate, egraved 'PUSH' .

- Size: 325 x 75 mm .

- Material/ finish: Satin stainless steel, grade 304 .

- Mounting: Face fix using SS CSK screws supplied .

- Additional requirements: Rounded edges and radiused corners, screw heads colour matched to plate .

690	KICK PLATES FIRE DOORS AS SCHEDULE

Manufacturer: Allegion (UK) Ltd. .

- Product reference: 4760.304 - Kick plate 1.2 mm thick .

- Size: Width and height - as schedule .

- Material/ finish: Satin stainless steel, grade 304 .

- Mounting: Face fix using SS CSK screws supplied .

- Additional requirements: Rounded edges and 5 mm radiused corners .

695A	STAINLESS STEEL PLATE FIRE DOOR SIGNS FIRE DOOR KEEP SHUT / LOCKED

- Standard: BS 5499.

  - Mandatory fire safety instruction notice (white text / blue background).

- Manufacturer: Allegion (UK) Ltd.

  - Product reference: 4750.10 - Fire door keep shut.

  - Product reference: 4750.11 - Fire door keep locked.

- Type: Circular 76 mm dia. x 1.5 mm stainless steel sign.

- Fixing: Face fix using SS CSK screws supplied.

700A	DOOR NUMERALS FLAT ENTRANCE DOORS

- Manufacturer: Trojan Hardware & Design Limited

  - Product reference: TROJAN polished chrome door numerals. - Size: 75 mm.

- Fixing: Face fix using SS CSK screws supplied.

710A	ESCUTCHEONS EURO PROFILE FIRE DOORS AS SCHEDULE

- Manufacturer: Allegion (UK) Ltd. .

  - Product reference: 4713.4 - Euro profile cylinder escutcheon .

- Material / finish: Satin stainless steel .

- Keyhole type: Euro profile cylinder .

- Fixing: 52 mm diameter x 4mm with snap on cover (pair). Bolt through fixings supplied as standard suitable for doors 44mm-54mm.

- Usage: To cylinder locks where no handle backplate is specified to be fitted .

710B	ESCUTCHEONS BLANK FIRE DOORS AS SCHEDULE

- Manufacturer: Allegion (UK) Ltd. .

  - Product reference: 4715.4 - Blank escutcheon .

- Material/ finish: Satin stainless steel .

- Usage: To cylinder locks where no handle backplate is specified to be fitted .

710C	CYLINDER PULL EURO PROFILE FIRE DOORS AS SCHEDULE

- Manufacturer: Allegion (UK) Ltd. .

  - Product reference: 4733 - Cylinder pull with aperture for euro profile cylinder .

- Material/ finish: Satin stainless steel .

- Usage: As schedule .

720A	DOOR STOPS

- Manufacturer: Häfele UK Ltd.

  - Product reference: Door Stops - wall mounted.

- Type: 937.10.702 - 60 mm satin stainless steel wall stop, black rubber buffer.

Usage: To doors opening against walls other than those fitted with closers with a back check facility.

- Operating clearance / positioning: Door must open freely to minimum 90° opening arc without obstruction from surface fixed door closer and / or handles.

- Additional requirements: Submit proposals for alternative size door stop if required to achieve required operating clearance.

730A	FIRE AND SMOKE RESISTANT LETTERPLATES FIRE RESISTANCE: 30 MINUTES

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: Firemaster Fire and Smoke Resistant Letterplate Ref: LRJS 29063.

- Finish: Silver anodized aluminium.

- Dimensions: 304 x 70 mm.

- Door aperture size: 285 x 55 mm.

- Security: Security Cowl.

730B	FIRE AND SMOKE RESISTANT LETTERPLATES FIRE RESISTANCE: 60 MINUTES

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: High Performance Fire, Smoke and Security Letterplate Ref: LRJ 8042S.

  - Minimum / maximum door thickness: LRJ 8042S: 42 mm / 47 mm.

Dimensions: 312 x 80 mm.

Door aperture size: 270 x 60 mm.

- Finish: Brushed stainless steel.

- Security: Security Cowl.

730C	SECURITY AND FIRE RESISTANT LETTERPLATE FIRE RESISTANCE: 60 MINUTES

- Standard: To BS 476-22: Up to 60 minutes (when combined with an FD60 door).

  - Security: PAS 24:2016.

  - Classified to TS 008:2015

  - Approvals: Certificate: CF5688 and Secured by Design

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: RJ008 Fire and Security Letterplate.

- Door thickness: 44 mm / 54 mm - as schedule.

- Colour/ Finish: Silver anodized aluminium.

855A	DROP SEAL: MORTISED

- Standard: To BS 9999, smoke leakage performanbce forr sealing the threshold of door assemblies against leakage of ambient temperature smoke, as defined in BS 476: Part 31.1: 1983.

  - Suitable for use on timber fire doors for up to 60 minutes under conditions of BS 476: Pt.20/22: 1987 and BS EN 1634-1: 2014.

  - Tested for reliability, the seal completed 1 000 000 cycles without failure. - Tested for acoustic performance with BS EN ISO 10140-2: 2010.

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: LAS8001 si Drop Seal.

- Type: Mortised / concealed.

- Dimensions:

  - 35 mm high (excluding seal in dropped position) x 14 mm wide.

- Minimum/ maximum gap size:

  - 1 mm/ 13 mm.

Use with: Any perimeter seal, any thresh plate.

- Finish: Silver anodized aluminium with silver end plates, and grey silicone rubber gasket.

- Length: As schedule. 335 mm.

435 mm.

535 mm.

635 mm.

735 mm.

835 mm.

935 mm.

1035 mm.

1135 mm.

1235 mm.

890	DOOR VIEWERS FLAT ENTRANCE DOORS

Manufacturer: Lorient Polyproducts Ltd. .

- Product reference: Fire Resisting Wide Angle Door Viewer Ref: LRJ3745 .

- Angle of vision: 160° .

- Material/ finish: Chrome plated .

- Viewer body diameter: 37 x 69 mm .

- Door thickness: As schedule .

896A	DOOR MOUNTED FIRE RESISTING AIR TRANSFER GRILLES 30 MINUTE

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: Lorient intumescent fire damper, non-vision style Ref: LVN20.

- Fire resistance: 30 minutes.

- Size: 200 x 200 mm - unless otherwise stated.

- Finish: Silver.

- Flanges:

  - Type: Integral. - Finish: Steel.

- Fitting: Screwed and bedded in Lorient intumescent mastic.:

  - Mastic colour: Silver.

- Smoke control system: Not required.

896C	DOOR MOUNTED FIRE RESISTING AIR TRANSFER GRILLES 60 MINUTE

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: Lorient intumescent fire damper, non-vision style Ref: LVN25.

- Fire resistance: 60 minutes.

- Size: 200 x 200 mm - unless otherwise stated.

- Finish: Silver.

- Flanges:

  - Type: Integral. - Finish: Steel.

- Fitting: Screwed and bedded in Lorient intumescent mastic.:

  - Mastic colour: Silver.

- Smoke control system: Not required.

# P31 Holes, chases, covers and supports for services

To be read with Preliminaries/General conditions.

400A	METER BOX CABINETS: FIRE AND SMOKE RESISTANT •	Standard: To BS EN 1366-3 and BS EN 1363-1 - Resistance to fire: 60 minutes.

- Manufacturer: Ritherdon and Co. Limited.

  - Product reference: FireSeal - Fire Rated Access Panel.

- Type: Surface mounted.

- Material / finish: Steel, powder coated.

- Operation: Budget lock (tri-drive services cabinet key).

- Fixing: Screw fix as recommended by manufacturer.

- Size: As schedule.

  - Standard: 710 x 510 x 50 mm (H x W x D)

  - Special - manufactured to order: 283 x 201 x 52 mm to 1500 x 1000 x 152 mm.

## EXECUTION

620	HOLES, RECESSES AND CHASES IN IN SITU CONCRETE

- Cast in: Holes larger than 10 mm diameter, recesses and chases.

- Cutting and drilling:

  - Permitted for holes not larger than 10 mm diameter.

  - Not permitted for holes larger than 10 mm diameter except as indicated on drawings.

640	HOLES IN STRUCTURAL STEELWORK

•	Cutting and drilling: Not permitted except as indicated on drawings.

650	HOLES, RECESSES AND CHASES IN MASONRY

- Locations: To maintain integrity of strength, stability and sound resistance of construction.

- Sizes: Minimum needed to accommodate services. - Holes (maximum): 300 mm².

- Walls of hollow or cellular blocks: Do not chase.

- Walls of other materials:

  - Vertical chases: No deeper than one third of single leaf thickness, excluding finishes.

  - Horizontal or raking chases: No longer than 1 m. No deeper than one sixth of the single leaf thickness, excluding finishes.

- Chases and recesses: Do not set back to back. Offset by a clear distance at least equal to the wall thickness.

- Cutting: Do not cut until mortar is fully set. Cut carefully and neatly. Avoid spalling, cracking and other damage to surrounding structure.

670	NOTCHES AND HOLES IN STRUCTURAL TIMBER

General: Avoid if possible.

- Sizes: Minimum needed to accommodate services.

- Position: Do not locate near knots or other defects.

- Notches and holes in the same joist: Minimum 100 mm apart horizontally.

- Notches in joists:

  - Position: Locate at top. Form by sawing down to a drilled hole.

  - Depth (maximum): 0.15 x joist depth.

  - Distance from supports: Between 0.1 and 0.2 x span.

- Holes in joists:

  - Position: Locate on neutral axis.

  - Diameter (maximum): 0.25 x joist depth.

  - Centres (minimum): 3 x diameter of largest hole.

  - Distance from supports: Between 0.25 and 0.4 of span.

- Notches in roof rafters, struts and truss members: Not permitted.

- Holes in struts and columns: Locate on neutral axis.

  - Diameter (maximum): 0.25 x minimum width of member.

  - Centres (minimum): 3 x diameter of largest hole.

  - Distance from ends: Between 0.25 and 0.4 of span.

690	INSTALLING PIPE SLEEVES

- Sleeves: Fit to pipes passing through building fabric.

- Material: Match pipeline.

- Size: One or two sizes larger than pipe to allow clearance.

- Finish: Install sleeves flush with building finish. In areas where floors are washed down, install protruding 100 mm above floor finish.

- Masking plates: Fit at visible penetrations, including through false ceilings of occupied rooms.

740	INSTALLING METER CABINETS

- Fixing: Screw fixed to suit background as recommeded by manufacturer.

- Keys: Hand over to Employer at completion.

# Q20 Granular sub-bases to roads/ pavings

10	THICKNESSES OF SUB-BASES

•	Thicknesses: As specified in the relevant paving section.

30	EXCAVATION AND COMPACTION OF SUBGRADES

- Final excavation to formation level: Carry out immediately before compaction of subgrade.

- Soft spots and voids: Give notice.

- Old drainage and service trenches: Give notice.

- Wet conditions: Do not excavate or compact when the subgrade may be damaged or destabilized.

- Compaction: Thoroughly, by roller or other suitable means, adequate to resist subsidence or deformation of the subgrade during construction and of the completed roads/ pavings when in use. Take particular care to compact fully at intrusions, perimeters and where local excavation and backfilling has taken place.

40	SUB-BASES

•	Granular material: Of a known suitability for use in sub-bases, free from ice, harmful matter and excessive dust or clay, well graded, all pieces less than 75 mm in any direction, and selected from one of the following:

- Crushed rock (other than argillaceous rock) or quarry waste.

- Crushed concrete, crushed brick or tile, free from plaster, timber and metal.

- Gravel or hoggin with not more clay content than is required to bind the material together, and with no large lumps of clay.

- Natural sand or gravel.

45	LAYING AND COMPACTING SUB-BASES

- Subgrade: Not frozen and free from loose soil, rubbish and standing water.

- Structures, membranes and buried services: Ensure stability and avoid damage.

- General: Spread and level in layers.

- Compaction:

  - Timing: As soon as possible after laying.

  - Method: By roller or other suitable means, adequate to resist subsidence or deformation of the sub -base during construction and of the completed paving when in use. Take particular care to compact fully at intrusions, perimeters and where local excavation and backfilling has taken place.

50	ACCURACY

•	Permissible deviation from required levels, falls and cambers (maximum):

- Subgrade:    ± 20 mm. - Sub-base:    ± 12 mm.

60	SURFACES TO RECEIVE SAND BEDDING FOR PAVING

- Blind surface: As necessary before compaction to ensure that surface is tight and dense enough to prevent laying course sand being lost into it during construction or use.

- Material: Sand or PFA.

70	PROTECTION

- Sub-bases: As soon as practicable, cover with subsequent layers, specified elsewhere.

- Subgrades and sub-bases: Prevent degradation by construction traffic, construction operations and inclement weather.

# Q25 Slab/ brick/ sett/ cobble pavings

11	LAYING PAVINGS

- Cutting: Cleanly and accurately, without spalling, to give neat junctions with edgings and adjoining finishes.

- Lines and levels of finished surface: Smooth and even with falls to prevent ponding.

- Bedding of units: Firm so that rocking or subsidence does not occur or develop.

- Appearance: Even and regular with even joint widths and free of mortar and sand stains.

16	LEVELS OF PAVING

- Permissible deviation from specified levels (generally):

± 6 mm.

- Regularity of paved surfaces

  - Maximum undulations in the surface of pavings (except tactile paving surfaces) under a 1 m straight edge placed anywhere on the surface (where appropriate in relation to the geometry of the surface): 3 mm.

  - Joints between paving units or utility access covers:

Joints flush with the surface: difference in level between adjacent units to be no more than twice the joint width (with a 5 mm max difference in level).

Recessed, filled joints: difference in level between adjacent units to be no greater than 2 mm; the recess to be no deeper than 5 mm.

Unfilled joints: difference in level between adjacent units to be no greater than 2 mm.

- Sudden irregularities: Not permitted.

21	PROTECTION FROM TRAFFIC

- Mortar bedded pavings: Keep free from pedestrian traffic for 4 days and vehicular traffic for 10 days after laying.

- Access: Restrict access to paved areas to prevent damage from site traffic and plant.

31	CONCRETE FLAG PAVING AS SCHEDULE

- Granular sub-base: Granular material, as section Q20.

  - Thickness: 100 mm unless otherwise specified.

- Laying and jointing: Bound construction - on mortar, site category IV, to BS 7533-4.

- Laying course: Full mortar bed, nominal thickness after compaction: 15-25 mm.

  - Mortar: As section Z21, mix 1:3 cement:sand.

- Slabs: To BS EN 1339.

  - Manufacturer: Submit proposals Product reference: Submit proposals.

  - Recycled content: Contractor's choice.

  - Colour/ Finish: Natural/ textured, to match existing.

  - Sizes: 600 x 600 x 35 mm, Square edge unless otherwise specified.

- Jointing: Mortar filled.

  - Width: 5-10 mm.

  - Mortar: As section Z21, mix: 1:4 cement:sand.

# Q40 Fencing

To be read with Preliminaries/ General conditions.

## FENCING SYSTEMS

310A	CLOSE BOARDED FENCING

- Manufacturer: Contractor's choice.

  - Product reference: Contractor's choice.

- Standard: To BS 1722-5.

- Height: 1800 mm.

- Wood: Softwood.

  - Treatment: To provide a 30-year service life. - Finish: Surface coating not required.

- Boards/ rails: Softwood feather edged boards on arris rails.

- Posts: Wood.

- Centres of posts (maximum): 1.8 m.

- Method of setting posts: 300 mm square or round holes, 600 mm deep filled to not less than half the depth with concrete .

- Accessories: Twice weathered capping for boards.

- Conformity: Submit manufacturer's and installer's certificates, to BS 1722-5.

## GATES AND GATE POSTS

550A	WOOD GATES AND POSTS.

- Manufacturer: Contractor's choice.

- Standard: To BS 5709.

- Wood: Contractor's choice.

- Treatment: As section Z12 and Wood Protection Association Commodity Specification C3.

  - Type: To provide a 30-year service life. - Finish: Surface coatings not required.

- Adhesive: Synthetic resin to BS EN 301, type 1.

- Workmanship: As section Z10.

- Fittings: Two hook and band hinges, return spring and a heavy duty automatic latch.

  - Finish: Hot-dip galvanized to BS EN ISO 1461 and Polyester powder-coated, as section Z31, black.

- Method of fixing: Concrete foundation, 450 mm square x 600 mm deep.

- Accessories: As required.

## EXECUTION

710	INSTALLATION GENERALLY

•	Set out and erect:

- Alignment: Straight lines or smoothly flowing curves.

- Tops of posts: Following profile of the ground.

- Setting posts: Rigid, plumb and to specified depth, or greater where necessary to ensure adequate support.

- Fixings: All components securely fixed.

720	SETTING POSTS IN CONCRETE

Standard: To BS 8500-2.

- Mix: Designated concrete not less than GEN1 or Standard prescribed concrete not less than ST2.

- Admixtures: Do not use.

- Holes: Excavate neatly and with vertical sides.

- Filling: Position post/ strut and fill hole with concrete to not less than the specified depth, well rammed as filling proceeds and consolidated.

- Backfilling of holes not completely filled with concrete: Excavated material, well rammed and consolidated.

730	EXPOSED CONCRETE FOUNDATIONS

- Filling: Compact until air bubbles cease to appear on the upper surface.

- Finishing: Weathered to shed water and trowelled smooth.

740	SETTING POSTS IN EARTH

- Holes: Excavated neatly, with vertical sides and as small as practicable to allow refilling.

- Filling: Position posts/ struts and replace excavated material, well rammed as filling proceeds.

750	DRIVEN POSTS

•	Damage to heads: Minimize.

- Repair: Neatly finish post tops after installation.

760	NAILED WOOD RAILS

- Length (minimum): Two bays, with joints in adjacent rails staggered.

- Fixing: Nail each length of rail to each post with two 100 mm galvanized nails.

- Rails with split ends: Replace.

- CLEFT WOOD RAILS

  - Length (maximum): 3.05 m.

  - Fixing: Rail end section shaped to adequately fill the post mortice. Nail each rail to each prick post with two galvanized nails.

  - Rails with split ends: Replace.

- ARRIS RAILS

  - Fixing:

    - Rail end section: Shaped to adequately fill the post mortice or recess.

    - Recessed posts: Rails bolted to each post.

    - Top rails: Fixed at both ends using One 8 mm diameter bolt.

  - Rails with split ends: Replace.

770	SITE CUTTING OF WOOD

- General: Kept to a minimum.

- Below or near ground level: Cutting prohibited.

- Treatment of surfaces exposed by minor cutting and drilling: Two flood coats of solution recommended for the purpose by main treatment solution manufacturer.

780	MAKING GOOD GALVANIZED SURFACES

- Treatment of minor damage (including on fasteners and fittings): Low melting point zinc alloy repair rods or powders made for this purpose, or at least two coats of zinc-rich paint to BS 4652.

- Thickness: Apply sufficient material to provide a zinc coating at least equal in thickness to the original layer.

# U90 General ventilation - domestic

## PRODUCTS

34A	VENTILATION DUCTS IN EXTERNAL WALLING: CORE VENTILATOR

Standard: To BS 5250.

- Manufacturer: Rytons Building Products Ltd.

  - Product reference: AC7HPTCWL - Terracotta Cowl/ External Grille.

- Type: Circular telescopic duct, with external cowl, and push/ pull or tilt action ventilation control.

- Components: - Cowl.

  - External grille.

  - Tube.

  - LookRyt® panel.

- Size:

  - Cowl: 217 x 210 x 93 mm (l x h x d).

  - External Grille: 166 x 160 mm (l x h).

  - Tube: 358 x 127 mm (l x diameter).

  - LookRyt® Panel: 172 x 172 mm (l x h).

- Additonal requirements: Core drilling of external masonry wall to form duct aperture.

36A	AIR TRANSFER GRILLES: FIRE RESISTANT

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: Lorient High Performance intumescent fire damper Ref: LVH44. Applications: Doors, walls (solid/ partition), ducts, floors and ceilings.

- Fire resistance: 60 minutes, minimum.

- Diameter: Not required.

- Size: As schedule. - 200 x 200 mm. - 300 x 300 m].

  - 400 x 400 mm.

  - 450 x 450 mm.

  - 500 x 500 mm.

  - 600 x 600 mm.

- Cover:

  - Grille: Required.

Material: Pressed steel. Finish: As schedule.

- Fitting: Screwed and bedded in Lorient intumescent mastic.:

  - Mastic colour: Silver/ White as schedule.

- Smoke control system: Not required.

36B	AIR TRANSFER GRILLES: FIRE AND SMOKE DAMPER

Manufacturer: Lorient Polyproducts Ltd.

- Product reference: Lorient High Performance cassette type intumescent fire and smoke damper Ref: LVH44S.

- Applications:  [Doors, walls (solid/ partition), ducts, floors and ceilings].

- Fire resistance: 60 minutes, minimum.

- Diameter: Not required.

- Size: As schedule. - 200 x 200 mm. - 300 x 300 m].

  - 400 x 400 mm.

  - 450 x 450 mm.

  - 500 x 500 mm.

  - 600 x 600 mm.

- Cover:

  - Grille: Required.

Material: Pressed steel. Finish: As schedule.

- Fitting: Screwed and bedded in Lorient intumescent mastic.:

  - Mastic colour: Silver/ white as schedule.

- Smoke control system: Talkback.

50B	DAMPER: FIRE - AUTOMATIC SMOKE CONTROL SYSTEM

- Manufacturer: Lorient Polyproducts Ltd.

  - Product reference: Talkback Damper-Shutter Control System

## EXECUTION

86	RIGID DUCTWORK GENERALLY

- Joints: Seal. Provide a robust airtight installation.

- Support: Do not distort ductwork or reduce cross-sectional area. Do not strain joints.

- Falls: Fall away from fans, dampers and other in-line accessories.

- Sleeves: Locate where ducts pass through building fabric. Bed solidly to the surrounding construction. Leave a gap of 10-20 mm between sleeve and duct and fill completely.

## COMPLETION

- COMMISSIONING

  - Ventilation system: Balance airflow using methods recommended by the system manufacturer.

- Performance: Provide slight positive pressure generally throughout the building, with airflow from 'dry' to 'wet' spaces..

  - Operation: Examine ductwork for leakage. Test the operation of fans, equipment, controls and sensors. Verify correct operation. Submit report.

- OPERATION AND MAINTENANCE

  - Operating and maintenance instructions: Submit copies of manufacturers' operating and maintenance instructions for equipment and controls.

  - Tools: Supply tools for operation, maintenance and cleaning purposes, including keys for valves and vents.

# V90 Electrical systems - domestic

To be read with Preliminaries/General conditions.

## SYSTEM PERFORMANCE

210	DESIGN OF LOW VOLTAGE ELECTRICAL INSTALLATION GENERALLY

- Design and detailing: Complete for the electrical installation.

- Standards: In accordance with BS 7671 and the requirements of the electricity distributor.

- Proposals: Submit drawings, technical information, calculations and manufacturers' literature.

240	DESIGN OF GENERAL LIGHTING SYSTEM

- Purpose: As schedule.

- Design and detailing: Complete for the general lighting system.

- Standard: To SLL 'Code for lighting'.

- Room: As schedule.

  - Maintained average illuminance: As schedule.

  - Glare index: As schedule. - Controls: As schedule.

- Maintenance: Submit proposals for the maintenance/ relamping regime.

250	DESIGN OF EMERGENCY LIGHTING SYSTEM

- Purpose: As schedule.

- Design and detailing: Complete for the emergency lighting system.

- Standards:

  - Emergency escape lighting: In accordance with BS 5266-1.

  - Escape route, open area, high risk task area and standby lighting: To BS EN 1838 and BS EN 50172.

- System classification: X - self-contained.

- Method of testing: Central hidden-key switches.

260	DESIGN OF EXTERNAL LIGHTING SYSTEM AS SCHEDULE

- Purpose: As schedule.

- Design and detailing: Complete for the external lighting system.

- Standards: To SLL 'Code for lighting', CIBSE Lighting Guide 6 and BS 5489-1.

  - Maintained average illuminance: Submit proposals.

  - Minimum illuminance at any point: Submit proposals. - Uniformity: Submit proposals.

265	DESIGN AND LIGHTING CALCULATIONS

- Proposals: Submit drawings, technical information, calculations and manufacturers' literature.

- Lighting calculations:

  - Type: Computer generated point calculations.

- Submit the following:

  - Luminaire layout drawings.

  - Luminaire photometric data including flux fraction ratios and polar intensity curves.

  - Lamp technical information.

  - Maintenance factor calculations, including proposals for luminaire maintenance and lamp replacement.

  - Reflectance values used for all wall, ceiling and floor surfaces.

  - Isolux contour plots for all relevant working planes, horizontal and vertical.

  - Schedule of design and calculated maintained average illuminance values. - Schedule of design and calculated uniformity values.

280	EARTHING AND BONDING DESIGN

Design: Complete the design of the earthing and bonding systems.

- Earthing, main bonding, supplementary bonding and protective conductors: In accordance with BS 7430.

- Requirements: Submit proposals.

## PRODUCTS

310	PRODUCTS GENERALLY

- Standard: In accordance with BS 7671.

- CE Marking: Required.

370	INTUMESCENT LINEAR GAP SEALS

- Standard: To BS EN 1366-4.

- Manufacturer: As schedule.

- Product reference: As schedule.

410	CABLES GENERALLY

- Approval: British Approvals Service for Cables (BASEC) certified.

- Cable sizes not stated: Submit proposals and calculations.

530A	SELF-CONTAINED EMERGENCY LUMINAIRES EMERGENCY AND NON-EMERGENCY CIRCULAR BULKHEAD

- Standards: To BS EN 60598-1 and BS EN 60598-2-22.

- Manufacturer: Lumineux Limited..

  - Product reference: BH200 LED Anti-Tamper Bulkhead with Microwave Occupancy Sensor MW - Emergency gear M3 included for fittings as required for lighting design.

- Third party product certification: ICEL 1001.

- Luminaire type: Ceiling and / or wall surface.

- Lamp: Light emitting diodes (LEDs). - Wattage: Submit proposals.

- Type: X self contained.

- Mode of operation: 2 (combined non-maintained)

- Facilities: Submit proposals.

- Duration of emergency mode: 180 (3 hour duration).

- Indicators:

  - Charging: Green light emitting diodes.

  - Fault: Flashing red light emitting diodes.

- Test in progress: Flashing green light emitting diodes.

  - Position within luminaire: Readily visible. Fix to luminaire body.

- Batteries: Manufacturers standard.

- Material: Polycarbonate.

- Colour: White.

  - Labelling: Indelibly mark with year of manufacture and installation.

- Legend: As schedule.

530B	SELF-CONTAINED EMERGENCY LUMINAIRES EMERGENCY RECTANGULAR BULKHEAD

- Standards: To BS EN 60598-1 and BS EN 60598-2-22.

- Manufacturer: Lumineux Limited.

  - Product reference: LE200 Series Emergency Bulkhead Slim.

- Third party product certification: ICEL 1001.

- Luminaire type: Ceiling and / or wall surface.

- Lamp: Light emitting diodes (LEDs). - Wattage: Submit proposals.

- Type: X self contained.

- Mode of operation: 0 (non-maintained)

- Facilities: Submit proposals.

- Duration of emergency mode: 180 (3 hour duration).

- Indicators:

  - Charging: Green light emitting diodes.

  - Fault: Flashing red light emitting diodes.

- Test in progress: Flashing green light emitting diodes.

  - Position within luminaire: Readily visible. Fix to luminaire body.

- Batteries: Manufacturers standard.

- Material: Polycarbonate.

- Colour: White.

  - Labelling: Indelibly mark with year of manufacture and installation.

- Legend: As schedule.

560A	EXTERNAL LUMINAIRES EMERGENCY CIRCULAR BULKHEAD

- Standards: Standards: To BS EN 60598-1 and BS EN 60598-2-22..

- Approval: Kitemark certified.

- Manufacturer: Lumineux Limited.

  - Product reference: BH1000 Multi Bulkhead with Emergancy M3 and Dusk to Dawn sensor DD. - Bezel Option / colour: Eyelid bezel, black

- Mounting: Wall - as schedule.

- Ingress protection to BS EN 60529: IP66.

- Lamp: Light emitting diodes (LEDs). - Wattage: 16.

  - Colour temperature: Manufacurers standard.

- Material: Polycarbonate.

- Colour: Black.

## EXECUTION

610	ELECTRICAL INSTALLATION GENERALLY

•	Standard: In accordance with BS 7671.

680	CABLE ROUTES

- Cables generally: Conceal wherever possible.

  - Concealed cable runs to wall switches and outlets: Align vertically or horizontally with the accessory.

- Exposed cable runs: Submit proposals.

  - Orientation: Straight, vertical and/ or horizontal and parallel to walls.

- Distance from other services running parallel: 150 mm minimum. - Heating pipes: Position cables below.

685	INSTALLING CABLES

- General: Install cables neatly and securely. Protect against accidental damage, adverse environmental conditions, mechanical stress and deleterious substances.

- Timing: Do not start internal cabling until building enclosure provides permanently dry conditions.

- Jointing: At equipment and terminal fittings only.

- Cables passing through walls: Sleeve with conduit bushed at both ends.

- Cables surrounded or covered by thermal insulation: Derate accordingly.

690	INSTALLING CABLES IN PLASTER

Protection: Cover with galvanized steel channel nailed to substrate.

695	INSTALLING CABLES IN VERTICAL TRUNKING/ DUCTS

- Support: Pin racks or cleats at each floor level or at 5 m vertical centres, whichever is less.

- Heat barrier centres (maximum): 5 m.

- Heat barriers: Required except where fire resisting barriers are not provided.

700	INSTALLING CABLES IN ACCESSIBLE ROOF SPACES

•	Cables running across ceiling joists: Fix to timber battens which are secured to joists.

705	INSTALLING ARMOURED CABLE

- Temperature: Do not start installation if cable or ambient temperature is below 0°C, or has been below 0°C during the previous 24 hours.

- Galvanized steel guards: Fit where cables are vulnerable to mechanical damage.

- Earthing: Bond armour to equipment and main earthing system.

- Connections to apparatus: Moisture proof, sealed glands and shrouds.

735	INSTALLING LUMINAIRES

- Location: As schedule.

- Orientation: Parallel with ceiling.

- Supports: Adequate for weight of luminaire.

740	INSTALLING EMERGENCY LUMINAIRES

- Permanent electrical supplies: Derive from adjacent local lighting circuit.

- Charge indicator: Position in a conspicuous location.

745	INSTALLING EXTERNAL LUMINAIRES

- Locations: Submit proposals.

- Seals: Check for particle ingress and clean.

760	EQUIPMENT LABELLING

- Electrical equipment: Install labels indicating purpose.

- Voltage warning notices:

  - Location: Apply to equipment in a position where it can be seen prior to gaining access to live parts when the voltage within exceeds 230 V.

  - Format: To BS EN ISO 7010, functional reference number, W012, include warnings of the voltage present.

- Distribution boards and consumer units: Card circuit chart within a reusable clear plastic cover. Fit to the inside of each unit. Include typed information identifying the outgoing circuit references, their device rating, cable type, size, circuit location and details. Label each outgoing way corresponding to the circuit chart.

- Sub-main cables: Label at both ends with circuit reference using proprietary cable marker sleeves.

765	ENGRAVING

- Metal and plastic accessories: Engrave, indicating their purpose.

- Emergency lighting test key switches: Describe their function.

- Multigang light switches: Describe the luminaire arrangement.

## COMPLETION

810	FINAL FIX

•	Accessory faceplates, luminaires and other equipment: Fit after completion of building painting.

820	CLEANING

- Electrical equipment: Clean immediately before handover.

- Equipment not supplied but installed and electrically connected: Clean immediately before handover.

830	INSPECTION AND TESTING GENERALLY

- Standard: In accordance with BS 7671.

- Notice before commencing tests (minimum): 24 hours.

- Labels and signs: Fix securely before system is tested.

- Certificates: Submit.

- Number of copies: As schedule .

860	INSPECTION AND TESTING OF EMERGENCY LIGHTING SYSTEMS

- Standard: In accordance with BS 5266-1.

- Certificate of testing: Submit.

  - Standard: To BS 5266-1, Annex F.

  - Number of copies: Submit proposals.

- System log book: To BS 5266-1.

870	INSPECTION AND TESTING OF EXTERNAL LIGHTING SYSTEMS

- Switching: Check correct operation of photoelectric control units, time switches and other switching devices over at least one switching cycle.

- Orientation: Adjust luminaires to achieve optimal performance.

- Additional requirements: As schedule.

880	DOCUMENTATION

- Timing: Submit at practical completion.

- Contents:

  - Full technical description of each system installed.

  - Manufacturers' operating and maintenance instructions for fittings and apparatus including relamping instructions for luminaire types. Identify hazardous lamps that require specialist disposal.

  - Recommended frequency of testing and inspection, both for electrical safety and for matters such as the corrosion and security of lighting columns and luminaire fixings.

  - Manufacturers' guarantees and warranties.

  - As-installed drawings showing circuits and their ratings and locations of fittings and apparatus.

  - List of normal consumable items.

890	MAINTENANCE

•	Servicing and maintenance: Undertake.

- Duration: Until 12 months after Practical Completion.

# Z10 Purpose made joinery

10	FABRICATION

- Standard: To BS 1186-2.

- Sections: Accurate in profile and length, and free from twist and bowing. Formed out of solid unless shown otherwise.

- Machined surfaces: Smooth and free from tearing, wooliness, chip bruising and other machining defects.

- Joints: Tight and close fitting.

- Assembled components: Rigid. Free from distortion.

- Screws: Provide pilot holes. Heads of countersunk screws sunk at least 2 mm below surfaces visible in completed work.

- Adhesives: Compatible with wood preservatives applied and end uses of timber.

20	CROSS SECTION DIMENSIONS OF TIMBER

- General: Dimensions on drawings are finished sizes.

- Maximum permitted deviations from finished sizes: - Softwood sections: To BS EN 1313-1.

- Hardwood sections: To BS EN 1313-2.

30	PRESERVATIVE TREATED WOOD

- Cutting and machining: Completed as far as possible before treatment.

- Extensively processed timber: Retreat timber sawn lengthways, thicknessed, planed, ploughed, etc.

- Surfaces exposed by minor cutting and/ or drilling: Treat as recommended by main treatment solution manufacturer.

40	MOISTURE CONTENT

•	Wood and wood based products: Maintained within range specified for the component during manufacture and storage.

50	FINISHING

- Surfaces: Smooth, even and suitable to receive finishes.

- Arrises: Eased unless shown otherwise on drawings.

- End grain in external components: Sealed with primer or sealer as section M60 and allowed to dry before assembly.

# Z11 Purpose made metalwork

To be read with Preliminaries/ General conditions.

## PRODUCTS

310	MATERIALS GENERALLY

- Grades of metals, section dimensions and properties: To appropriate British Standards. When not specified, select grades and sections appropriate for the purpose.

- Prefinished metal: May be used if methods of fabrication do not damage or alter appearance of finish, and finish is adequately protected.

- Fasteners: To appropriate British Standards and, unless specified otherwise, of same metal as component being fastened, with matching coating or finish.

## FABRICATION

515	FABRICATION GENERALLY

- Contact between dissimilar metals in components: Avoid.

- Finished components: Rigid and free from distortion, cracks, burrs and sharp arrises.

- Moving parts: Free moving without binding.

- Corner junctions of identical sections: Mitre.

520	COLD FORMED WORK

•	Profiles: Accurate, with straight arrises.

527	WELDING AS SCHEDULE.

- Welding procedures:

  - Method and standard: As schedule - Metal arc welding to BS EN 1011-1 and -2 (suitable for welding steel).

  - Welding Procedure Specification (WPS): Not required.

- Preparation:

  - Joint preparation: Clean thoroughly.

  - Surfaces of materials that will be self-finished and visible in the completed work: protect from weld splatter.

- Jointing:

  - Joints: Fully bond parent and filler metal throughout with no inclusions, holes, porosity or cracks.

  - Dissimilar metals: Not applicable.

  - Strength requirements: Welds to achieve design loads.

  - Heat straightening: Submit proposals.

  - Complex assemblies: Agree priority for welding members to minimize distortion caused by subsequent welds.

  - Tack welds: Use only for temporary attachment.

  - Jigs: Provide to support and restrain members during welding.

  - Filler plates: Submit proposals.

  - Lap joints: Minimum 5 x metal thickness or 25 mm, whichever is greater.

  - Weld terminations: Clean and sound.

## FINISHING

710	FINISHING WELDED AND BRAZED JOINTS VISIBLE IN COMPLETE WORK

- Standard: To BS EN ISO 8501-3.

- Preparation grade: Submit proposals.

- Butt joints: Smooth, and flush with adjacent surfaces.

- Fillet joints: Neat.

- Grinding: Grind smooth where indicated on drawings.

745	PREPARATION FOR APPLICATION OF COATINGS

- General: Complete fabrication, and drill fixing holes before applying coatings.

- Paint, grease, flux, rust, burrs and sharp arrises: Remove.

780	GALVANIZING

- Standard: To BS EN ISO 1461.

- Preparation:

  - Vent and drain holes: Provide in accordance with BS EN 14713-1 and -2. Seal after sections have been drained and cooled.

  - Components subjected to cold working stresses: Heat treat to relieve stresses before galvanizing.

  - Welding slag: Remove.

  - Component cleaning: To BS EN ISO 8501-3. - Grade: Submit proposals.

# Z20 Fixings and adhesives

10	FIXINGS AND FASTENERS GENERALLY

- Integrity of supported components: Select types, sizes, quantities and spacings of fixings, fasteners and packings to retain supported components without distortion or loss of support.

- Components, substrates, fixings and fasteners of dissimilar metals: Isolate with washers or sleeves to avoid bimetallic corrosion.

- General usage: To recommendations of fastener manufacturers and/ or manufacturers of components, products or materials fixed and fixed to.

- Fixings: To be in straight lines, at regular centres.

25	FASTENER DURABILITY

- Materials: To have:

- Bimetallic corrosion resistance appropriate to items being fixed. - Atmospheric corrosion resistance appropriate to fixing location.

- Appearance: Submit samples on request.

30	FIXINGS THROUGH FINISHES

•	Penetration of fasteners and plugs into substrate: To achieve a secure fixing.

35	PACKINGS

•	Materials: Noncompressible, corrosion proof. •	Area of packings: Sufficient to transfer loads.

40	CRAMP FIXINGS

- Fasteners: Fix cramps to frames with screws of same material as cramps.

- Fixings in masonry work: Fully bed in mortar.

50	PELLETED COUNTERSUNK SCREW FIXINGS

- Finished level of countersunk screw heads: Minimum 6 mm below timber surface.

- Pellets: Cut from matching timber, grain matched, glued in to full depth of hole.

- Finished level of pellets: Flush with surface.

55	PLUGGED COUNTERSUNK SCREW FIXING

- Finished level of countersunk screw heads: Minimum 6 mm below timber surface.

- Plugs: Glue in to full depth of hole.

- Finished level of plugs: Projecting above surface.

60	APPLYING ADHESIVES

- Surfaces: Clean. Regularity and texture to suit bonding and gap filling characteristics of adhesive.

- Support and clamping during setting: Provide as necessary. Do not mark surfaces of or distort components being fixed.

- Finished adhesive joints: Fully bonded. Free of surplus adhesive.

# Z21 Mortars

To be read with Preliminaries/ General conditions.

## CEMENT GAUGED MORTARS

110	CEMENT GAUGED MORTAR MIXES

•	Specification: Proportions and additional requirements for mortar materials are specified elsewhere.

120	SAND FOR SITE MADE CEMENT GAUGED MASONRY MORTARS

- Standard: To BS EN 13139.

- Grading: 0/2 (FP or MP).

- Fines content where the proportion of sand in a mortar mix is specified as a range (e.g. 1:1: 5-6):

Lower proportion of sand: Use category 3 fines.

Higher proportion of sand: Use category 2 fines.

- Sand for facework mortar: Maintain consistent colour and texture. Obtain from one source.

131	READY-MIXED LIME:SAND FOR CEMENT GAUGED MASONRY MORTARS

- Standard: To BS EN 998-2.

- Lime: Nonhydraulic to BS EN 459-1. - Type: CL 90S.

- Pigments for coloured mortars: To BS EN 12878.

135	SITE MADE LIME:SAND FOR CEMENT GAUGED MASONRY MORTARS

- Permitted use: Where a special colour is not required and in lieu of factory made ready-mixed material.

- Lime: Nonhydraulic to BS EN 459-1.

- Type: CL 90S.

- Mixing: Thoroughly mix lime with sand, in the dry state. Add water and mix again. Allow to stand, without drying out, for at least 16 hours before using.

160	CEMENTS FOR MORTARS

- Cement: To BS EN 197-1 and CE marked.

  - Types:   	Portland cement, CEM I.

Portland limestone cement, CEM ll/A-L or CEM ll/A-LL.

Portland slag cement, CEM II/B-S.

Portland fly ash cement, CEM II/B-V. - Strength class: 32.5, 42.5 or 52.5.

- White cement: To BS EN 197-1 and CE marked.

  - Type: Portland cement, CEM I. - Strength class: 52.5.

- Sulfate resisting Portland cement:

  - Types:   	To BS EN 197-1 Sulfate resisting Portland cement, CEM I/SR and CE marked. To BS EN 197-1 fly ash cement, CEM ll/B-V and CE marked. - Strength class: 32.5, 42.5 or 52.5.

- Masonry cement: To BS EN 413-1 and CE marked. - Class: MC 12.5.

180	ADMIXTURES FOR SITE MADE CEMENT GAUGED MORTARS

- Air entraining (plasticizing) admixtures: To BS EN 934-3 and compatible with other mortar constituents.

- Other admixtures: Submit proposals.

- Prohibited admixtures: Calcium chloride, ethylene glygol and any admixture containing calcium chloride.

190	RETARDED READY TO USE CEMENT GAUGED MASONRY MORTARS

- Standard: BS EN 998-2.

- Lime for cement:lime:sand mortars: Nonhydraulic to BS EN 459-1. - Type: CL 90S.

- Pigments for coloured mortars: To BS EN 12878.

- Time and temperature limitations: Use within limits prescribed by mortar manufacturer. - Retempering: Restore workability with water only within prescribed time limits.

210	MAKING CEMENT GAUGED MORTARS

- Batching: By volume. Use clean and accurate gauge boxes or buckets. - Mix proportions: Based on dry sand. Allow for bulking of damp sand.

- Mixing: Mix materials thoroughly to uniform consistency, free from lumps.

- Mortars containing air entraining admixtures: Mix mechanically. Do not overmix.

- Working time (maximum): Two hours at normal temperatures.

- Contamination: Prevent intermixing with other materials.

# Z22 Sealants

31	JOINTS AS SCHEDULE

•	Primer, backing strip, bond breaker: Types recommended by sealant manufacturer.

## EXECUTION

- SUITABILITY OF JOINTS

  - Presealing checks:

    - Joint dimensions: Within limits specified for the sealant.

    - Substrate quality: Surfaces regular, undamaged and stable.

  - Joints not fit to receive sealant: Submit proposals for rectification.

- PREPARING JOINTS

  - Surfaces to which sealant must adhere:

    - Remove temporary coatings, tapes, loosely adhering material, dust, oil, grease, surface water and contaminants that may affect bond.

    - Clean using materials and methods recommended by sealant manufacturer.

  - Vulnerable surfaces adjacent to joints: Mask to prevent staining or smearing with primer or sealant.

  - Backing strip and/ or bond breaker installation: Insert into joint to correct depth, without stretching or twisting, leaving no gaps.

  - Protection: Keep joints clean and protect from damage until sealant is applied.

- APPLYING SEALANTS

  - Substrate: Dry (unless recommended otherwise) and unaffected by frost, ice or snow.

  - Environmental conditions: Do not dry or raise temperature of joints by heating.

  - Sealant application: Fill joints completely and neatly, ensuring firm adhesion to substrates.

  - Sealant profiles:

    - Butt and lap joints: Slightly concave. - Fillet joints: Flat or slightly convex.

  - Protection: Protect finished joints from contamination or damage until sealant has cured.

# Z31 Powder coatings

To be read with Preliminaries/ General conditions.

120	POWDER COATING MATERIALS

- Manufacturer: Obtain from one only of the following: Contractor's choice..

- Selected manufacturer: Submit details before commencement of powder coating including:

  - Name and contact details.

  - Details of accreditation schemes.

  - Technical data of product including current Agrément certificates.

210	WORKING PROCEDURES

•	Comply with the follow following standards.

- Aluminium components: To BS 6496 or BS EN 12206-1.

- Steel components: To BS EN 13438.

- Safety standards: To British Coatings Federation 'Code of safe practice: Powder coating. Application of coating powders by electrostatic spraying'.

- Health and safety guidance: Health and Safety Executive 'Reducing risk associated with using coating powders - employers' web page.

220	POWDER COATING APPLICATORS

•	Applicator requirements:

- Approved by powder coating manufacturer.

- Currently certified to BS EN ISO 9001.

- Comply with quality procedures, guarantee conditions, standards and tests required by powder coating manufacturer.

- Selected applicator: Submit details before commencement of powder coating including:

Name and contact details.

Details of accreditation schemes.

225	GUARANTEES

•	Powder coating manufacturer and applicator guarantees:

- Submit sample copies before commencement of powder coating. - Submit signed project specific copies on completion of work.

310	PRETREATMENT OF ALUMINIUM COMPONENTS

- Condition of components to be pretreated:

  - Free from corrosion and damage.

  - All welding and jointing completed and finish off as specified.

  - Free from impurities including soil, grease and oil.

  - Suitable for and compatible with the pretreatment process.

- Conversion coating requirements:

  - Chromate system: To BS 6496 or BS EN 12206-1.

  - Chromate-free system: To BS EN 12206-1. Submit details before using.

- Rinsing requirements: Use demineralized water. Drain and dry.

320	PRETREATMENT OF STEEL COMPONENTS

- Condition of components to be pretreated:

  - Free from corrosion and damage.

  - All welding and jointing completed and finish off as specified.

  - Free from impurities including soil, grease and oil.

  - Suitable for and compatible with the pretreatment process.

- Conversion coating requirements: To BS EN 13438.

- Rinsing requirements: Use demineralized water. Drain and dry.

330	PRETREATMENT FOR PROTECTION IN AGGRESSIVE ENVIRONMENTS

- Minimum thickness of 60 microns across significant and/ or primary surfaces.

- Minimum thickness of 25 microns on non-significant and/ or secondary faces, ensuring a coherent film layer.

- All cut edges, drilled holes and mitres to be fully sealed.

- Cleaning and maintenance: Carried out once every three to twelve months (dependent on proximity to pollutant).

430	EXTENT OF POWDER COATINGS

•	Application: To visible component surfaces, and concealed surfaces requiring protection. Coated surfaces will be deemed 'significant surfaces' for relevant BS 6496/ BS EN 13438 performance requirements.

435	APPLICATION OF POWDER COATINGS

- Surfaces to receive powder coatings: Free from dust or powder deposits.

- Powder colours: Obtain from one batch of one manufacturer.

- Commencement of powder coatings: To be continuous from pretreatment.

- Components to be installed on site in order of application.

- Jig points: Not visible on coated components.

- Curing: Controlled to attain metal temperatures and hold periods recommended by powder coating manufacturer.

- Stripping and recoating of components: Only acceptable by prior agreement of powder coating manufacturer. Stripping, pretreatment and powder coating are to be in accordance with manufacturer's requirements.

- Overcoating of components: Not acceptable.

440	PERFORMANCE AND APPEARANCE OF POWDER COATINGS

- For aluminium components:

  - Standard: To BS 6496 or BS EN 12206-1.

- For steel components:

  - Standard: To BS EN 13438.

- Visual inspection after powder coating: Significant surface viewing distances to be as specified in the relevant Standard, unless specified otherwise.

- Colour and gloss levels: To conform with approved samples.

450	ALUMINIUM ALLOY FABRICATIONS

- Units may be assembled:

  - Before powder coating.

  - From components powder coated after cutting to size.

  - Where approved, from components powder coated before cutting to size.

- Exposure of uncoated background metal: Not acceptable.

- Assembly sealants: Compatible with powder coatings. Obtain approval of colour if sealants are visible after fabrication.

460	STEEL FABRICATIONS

- Unit assembly: Wherever practical, before powder coating.

- Exposure of uncoated background metal: Not acceptable.

- Assembly sealants: Compatible with powder coatings. Obtain approval of colour if sealants are visible after fabrication.

470	FIXINGS

•	Exposed metal fixings: Powder coat together with components, or coat with matching repair paint system applied in accordance with the powder coating manufacturer's recommendations.

480	DAMAGED COMPONENTS - REPAIR OR REPLACEMENT

- Before delivery to site: Check all components for damage to powder coatings. Replace damaged components.

- Site damage: Submit proposals for repair or replacement.

510	PROTECTION

- Powder coated surfaces of components: Protect from damage during handling and installation, or by subsequent site operations.

- Protective coverings must be:

  - Resistant to weather conditions.

  - Partially removable to suit building in and access to fixing points.

- Protective tapes in contact with powder coatings must be:

  - Low tack, self adhesive and light in colour.

  - Applied and removed in accordance with tape and powder coating manufacturers' recommendations. Do not use solvents to remove residues as these are detrimental to the coating.

- Inspection of protection: Carry out monthly. Promptly repair any deterioration or deficiency.

520	PROTECTION IN HAZARDOUS LOCATIONS

- Minimum thickness of 60 microns across significant and/ or primary surfaces.

- Minimum thickness of 25 microns on non-significant and/ or secondary faces ensuring a coherent film layer.

- All cut edges, drilled holes and mitres to be fully sealed.

- Cleaning: Carried out once every three to twelve months (dependent on proximity to pollutant).

535	DOCUMENTATION

• Submit the following information for each batch of powder coated components: - Supplier.

- Trade name.

- Colour.

- Type of powder.

- Method of application.

- Batch and reference number.

- Statutory requirements.

- Test certificates.

- Maintenance instructions.

540	COMPLETION

- Protection: Remove any protective coatings.

- Cleaning and maintenance of powder coatings: Carry out in accordance with procedures detailed in powder coating manufacturer and applicator guarantees.