Electrical Testing & Servicing

Specification Document

Reference HISESS14072025

Closing date Monday 13th October 2025 at 12 noon

Homes in Somerset

Bridgwater House

Kings Square

BRIDGWATER

Somerset

TA6 3AR

Contents

Introduction & Overview of Contract Requirements	3

2.	Periodic servicing and inspection	4

3.	Urgent, responsive and planned maintenance works	10

4.	Emergency Repairs	11

5.	Legislative Requirement	11

6.	Contractor Qualifications	11

7.	Recording & Monitoring	11

7a - Live View, Reporting, and Management System	12

8.	Key Performance Indicators (KPI’s)	14

9.	General Contract Requirements	15

10.	Planned System Replacements and Installations	15

11.	New Technologies	16

Equipment Schedule	17

# Introduction & Overview of Contract Requirements

Homes in Somerset has approximately 4,000 properties which are a mixture of general needs, supported and extra care properties.

Currently electrical safety servicing is required to be carried out by a competent organisation to our domestic and communal buildings and are included within this contract.

This specification details the requirement for 5 yearly periodic inspection and testing of electrical installations in communal areas and domestic dwellings and properties.  In addition you may be required with notice to complete inspections and testing of void properties and properties where a mutual exchange is taking place these will require a full inspection and test before any new occupancy that adheres to current legislative requirements.

Also included are:

- Annual portable appliance testing

- Electrical repairs works – cat 1, cat 2 and cat 3 as required

# Periodic Inspection and Testing

## Periodic inspection and testing of electrical installation of domestic, communal areas and commercial properties shall not exceed five years between inspections. If requested voids properties and properties where a mutual exchange is taking place will require a full inspection and test before any new occupancy. Where a new certificate is issued, any schedule of testing should be amended to reflect the new certificate date. All inspection, testing, certification and recording shall be undertaken in accordance with the following information.

## A list of the previous test dates for all properties shall be provided to the successful contractor who shall programme the required tests each year to ensure a rolling 5-year programme of works.

Works shall consist of a full visual inspection followed by a testing process as detailed below:

## Visual inspection shall look and check for the following:

- Breakage

- Wear/Deterioration

- Signs of overheating

- Missing parts (covers, screws, etc.)

- Loose fixings

Confirm:

- Switchgear/Supply (where reasonable and practicable to do so)

- Doors of enclosure are secure.

- Adequate labelling is in place.

Operation:

- Switchgear/Supply (where reasonable and practicable to do so)

- Equipment – switch on and off.

- Operation of RCD and RCBO’s and other similar devices using the test function.

Following the visual inspection, the testing process shall be undertaken.

## Protective Conductor Continuity

The test should be undertaken between the earth terminal and distribution boards to the following exposed conductive parts:

- Socket outlet earth conductors.

- Accessible exposed conductive parts of current using equipment & accessories.

- The continuity of all protective bonded conductors and all necessary supplementary bonded conductors

- A ring circuit continuity test shall be undertaken if not previously recorded or where alteration to the circuit has taken place.

- The insulation resistance test to be carried out between the live conductors with line and neutral connected together and earth at all final boards.

- At main and sub-main distribution boards/panels with final circuit distribution boards isolated from mains.

- The Polarity and Earth Fault Loop Impedance will be checked at the origin of the installation, distribution boards, accessible socket outlets and extremity of radial circuits (lighting etc.)

- The earth electrode resistance will require testing for any TT type system or where earth rods have been fitted.  Each rod or group of rods shall be tested with test links removed and with the installation isolated from the supply source.

- Function tests will be carried out on any RCD & RCBO, followed by the operation of the functional test button.

- Function tests will be carried out on Circuit Breakers/Isolators and switching devices – manual operation to prove that the devices disconnect from the supply.

# Annual Portable Appliance Testing

## The successful contractor will undertake portable appliance testing throughout the estate in all communal and commercially used areas (offices, communal day room, corridors, etc.)

## All equipment shall be tested/calibrated in accordance current British Standards, current guidance and legislation.

## All portable appliances shall undergo a visual inspection to check the following: -

- damage to the lead including fraying, cuts or heavy scuffing, e.g. from floor box covers.

- damage to the plug, e.g. to the cover or bent pins.

- tape applied to the lead to join leads together.

- coloured wires visible where the lead joins the plug (the cable is not being gripped where it enters the plug).

- damage to the outer cover of the equipment itself, including loose parts or screws.

- signs of overheating, such as burn marks or staining on the plug, lead or piece of equipment.

- equipment that has been used or stored in unsuitable conditions, such as wet or dusty environments or where water spills are possible; and

- cables trapped under furniture or in floor boxes.

- the electrical equipment is being used in accordance with the manufacturer’s instructions.

- the equipment is suitable for the job.

- there are no signs of internal damage, overheating or water damage to the plug.

- the correct fuse is in use and it’s a proper fuse, not a piece of wire, nail etc.

- the wires including the earth, where fitted, are attached to the correct terminal (see Figure 1).

- the terminal screws are tight.

- the cord grip is holding the outer part (sheath) of the cable tightly; and

- no bare wire is visible other than at the terminals.

- extension leads, multiway adaptors and connection leads are also tested.

## Earthed Equipment

An earth connection test is required as well as the normal insulation resistance test.

## Double Insulated Equipment

No earth connect test is required but normal insulation resistance testing is required.

## Equipment Failure

Any equipment failing its continuity or insulation resistance testing must be labelled as failed and given to the caretaker, support at home co-ordinator or disabled and returned to Homes in Somerset.

## Labelling

All portable appliances shall be labelled with a unique number and dated to show when last tested.

Any items found which either not were labelled or show a date greater than 12 months should be brought to the attention of Homes in Somerset via the monthly report.

# Installation of Fire detection equipment

## The contractor will be required to install and /or replace existing fire detection equipment when a periodical inspection and test is carried out.  This will be to an agreed schedule and in accordance with industry standard requirements.

## The type of equipment used for each type of dwelling is specified below:

General needs

For all general needs properties, the minimum required standard is Cat D1, LD2 without exception.

Category 1 Sheltered

Self-contained dwellings such as bungalows & flats.

For all sheltered properties the minimum required standard is Cat D1, LD2 without exception. For properties where it is identified that sufficient fire safety standard is not met, the contractor should advise Homes in Somerset to discuss if an LD1 upgrade may be required.

Category 2 & 3 Sheltered

Dwellings that form part of a larger premises, contained under one roof, with communal spaces & facilities such as communal lounge, communal kitchens, laundries, and passenger lifts.

For all sheltered properties the minimum required standard is Cat D1, LD1 without exception. This standard represents the highest coverage available.

## Relay module may need to be linked into the existing Warden call or dispersed alarm system and may require liaison with Homes in Somerset and the current fire servicing contractor.

## The Contractor shall advise the equipment to use but final decision of the Make of system will be by Homes in Somerset.

## All installations must be installed to the current version of       BS5839-6:2019.

A Domestic Fire Detection Commissioning certificate must be filled out following the commissioning of any smoke detection system. Certificates will be subject to quality control checks, which will be carried out by Homes in Somerset’s Compliance Team.

## Electrical Connections

All permanent feeds are to be taken from the local lighting source and comply with manufacturer’s instructions.

All electrical connections must be tested in line with the current BS7671:2018 and any amendments which may come into action through the life of the contract.

The smoke detection system is to be radio-linked, tested and signed off using an appropriate commissioning certificate in every case.

Live smoke test is not permitted as these will damage the detector – Please test in-line with manufacturer instructions using the built-in test facility.

Where required notification to building control must be carried out and a copy of the certificate sent to the Homes in Somerset’s Compliance Team.

# Reactive repairs and emergency repairs

## The contractor should allow for the capacity to receive requests to carry out repairs: reactive repairs; carried out a minimum of 4 weeks from date of request. Reasonable allowance should be made to carry out any work at the soonest possible date. Emergency repairs should be carried out within 24 hours, where a repair is not feasible within that time scale, at minimum, any dangerous condition should be made safe and a report issued to the reactive and compliance teams of any action taken and further action required.

## Integration with the Homes in Somerset ‘OPEN Housing’ Data platform will be necessary to receive Repair and work requests digitally.  The successful contractor will be required to coordinate with our IT department to enable this.

# Property Portfolio

## The contractor will be provided with information on the extent of the Homes in Somerset Property Portfolio and will be asked to provide costs for a schedule of works if not using the NHF Schedule of rates for different systems types as specified. The schedule should allow for the following criteria:

- 1 Bed flat

- 2+ Bed flats

- 1-2 Bed house

- 3+ Bed House

- Block per unit cost

- Block per communal area cost

## It is envisaged that around 800 Periodic fixed wired inspections will be required annually.

## The contractor will be required to produce a rolling programme of inspections to ensure that all properties are inspected on time and in line with current legislation, guidance and best practice.

General requirements

## The Contractor must provide, on appointment, general risk assessments and method statements (RAMS) for routine and standard operation to be carried out.  Further RAMS will be required before commencement of any works outside the scope of those standard operations or when appropriate.

## The Contractor will, before final appointment, provide references from past or existing clients to comment on the standard of work and operations.

## The contractor shall not sub-let the works to a third party contractor without written consent from a member of the Property Services department.

## Work shall not commence unless Homes in Somerset has given written permission (electronic or physical) to proceed, or the contractor is in receipt of an official order.

## The order number must be quoted on all correspondence, service records and invoices.

## The contractor shall allow for review meetings to be held quarterly intervals throughout the contract, unless there are performance issues when more frequently meetings will be required.

## The contractor shall produce monthly reports detailing the number of tests carried out during the month and if these were first, second or subsequent re-visit to gain access. Number of unsafe situations found, actions taken and any trends identified. Details on any outstanding services with dates and reasons for delays. Details on any re-visit, including reasons. Number of properties to be visited in the following month.

## The contractor shall, during inspection, testing and servicing carry out minor repairs e.g. tighten a joint, replace a screw etc to ensure the integrity of equipment is maintained and appliances remain safe.

## Any Category 1 failures must immediately be notified to Homes in Somerset prior to the electrician leaving the site, who will either authorise the repair or isolation of the system/part of system until the required repair can be completed.

## All equipment used for testing must be regularly calibrated in line with manufactures instructions and calibration certificates must be provided annually to Homes in Somerset.

## All work outside of the normal contract will be charged as per the agreed rate rounded to the nearest 10 minute.

## The contractor will advise Homes in Somerset of any changes to legislation, British Standards or guidance relating to electrical.

## This contract is for servicing of installations, appliances and equipment/facilities, it is not specifically designed to embrace new works, non cat 1 repairs or installations, but may from time to time be considered for that purpose.  Any new works up to the value of £250 to be completed while on initial visit. Between 250 and £2000 by written consent only, and over the value of £2,000 will be subject to a satisfactory quotation and will, as a rule, be part of a competitive process.

# Legislative Requirements

## All work and servicing must be carried out in accordance with, and comply with the exact requirements of British Standards, other relevant standards and best practice guidance and manufacturer’s instructions.

## Specifically all work must comply with the following standards, legislation and guidance or their updated version, should they change during the life of the contract:

| Standard | Year | Description |
| --- | --- | --- |
| BS 61439 (many parts) | 2009 - 2012 | Low-voltage switchgear and control gear assemblies |
| BS 5266 Parts 1 to 10 also BS EN 50172 | 1999 - 2008 | Code of practice for emergency lighting |
| BS 5424 Parts 2 and 3, also IEC 60158 part 3 | 1985 - 1988 | Specification for low voltage control gear |
| BS EN 60422 | 2008 | Monitoring and maintenance guide for mineral insulating oils in electrical equipment |
| BS 5839 Parts 1 - 11, also PD6531:2010 | 1988 - 2010 | Fire detection & alarm systems for buildings |
| BS EN 60079-30-2 | 2007 | Electric surface heating |
| BS 6423 | 1983 | Code of practice for maintenance of electrical switchgear and control gear for voltages up to and including 1 kV |
| BS 6626 | 2010 | Code of practice for maintenance of electrical switchgear and control gear for voltages above l kV and up to and including 36 kV |
| BS EN 62305, 4 parts | 2006-2011 | Code of practice for protection of structures against lightning |
| BS 7375 | 2010 | Code of practice for distribution of electricity on construction and building sites |
| BS 7430 | 1998 | Code of practice for earthing |
| BS 7671 | 2018 | Requirements for electrical installations. IEE Wiring Regulations. Eighteenth edition |
| BS 7909 | 2008 - 2011 | Code of practice for temporary electrical systems for entertainment and related purposes. |
| BS EN 50110 Parts 1 and 2 | 2004 - 2010 | Operation of electrical installations |
| IEC 60479 Parts 1-4, also PD6519 | 1994-2005 | Guide to effects of current on human beings and livestock. |
| BS EN 60529 | 1992 | Specification for degrees of protection provided by enclosures (IP code) |
| BS EN 60947 Parts 1-8 | 2001 - 2011 | Specification for low voltage switch gear and control gear |
| BS 1362 | 1973 | Specification for general purpose fuse links for domestic and similar purposes (primarily for use in plugs) |
| BS 1363 Parts 1 -5 | 1995 - 2008 | 13 A plugs, socket-outlets and adaptors. |
| BS EN (IEC) 60309, Parts 1,2, 4 | 1999 - 2007 | Plugs, socket-outlets and couplers for industrial purposes. |
| BS EN 60320, Parts 1, 2 | 1999 - 2009 | Appliance couplers for household and similar general purposes. |
| BS EN 60335, Many parts |  | Specification for safety of household and similar electrical appliances |
| BS EN 61000-6-3,4 | 2007 - 2011 | Electromagnetic compatibility. Generic emission standard. |
| BS EN 61000-6-1,2 | 2005 - 2007 | Electromagnetic compatibility. Generic immunity standard. |
| BS EN (IEC) 60801, Part 2 | 1993 | Electromagnetic compatibility for industrial-process measurement and control equipment. Electrostatic discharge requirements |
| BS EN ISO 13850 | 2008 | Safety of machinery. Emergency stop. Principles for design. |
| BS EN 953 | 1997 - 2009 | Safety of machinery. Guards. General requirements for the design and construction of fixed and movable guards |
| BS EN 13849 | 2008 | Safety of machinery. Safety related parts of control systems. General principles for design |
| BS EN 982 | 1996 -2008 | Safety of machinery. Safety requirements for fluid power systems and their components. Hydraulics |
| BS EN 983 | 1996 -2008 | Safety of machinery. Safety requirements for fluid power systems and their components. Pneumatics |
| BS EN 1037 | 1996 -2008 | Safety of machinery. Prevention of unexpected start-up |
| BS EN ISO 12100 | 2010 | Safety of machinery. General principles for design. Risk assessment and risk reduction. |
| BS EN 1088 | 2008 | Safety of machinery. Interlocking devices associated with guards. Principles for design and selection. |
| PD 5304 | 2005 | Safe use of machinery |
| BS EN 60204 many parts |  | Safety of machinery. Electrical equipment of machines. |
| BS EN 61069, Parts 1-8 | 1991-1999 | Industrial-process measurement and control. Evaluation of system properties for the purpose of system assessment. |
| BS EN 61310, Parts 1,2,3 | 2008 | Safety of machinery. Indication, marking and actuation. |
| BS EN 61496, 3 parts | 2004 - 2008 | Safety of machinery. Electro-sensitive protective equipment. |

The Health and Safety at Work etc Act 1974 and all relevant associated regulations

The Electricity at Work Regulations 1989

The IET Wiring Regulations BS 7671:2018 as amended

The Building Act 1984 & 2000 and associated regulations.

The Control of Asbestos at Work Regulations 2012

Regulatory Reform (Fire Safety) Order 2005

And any other electrical standards regulations which become applicable during the length of the contract.

## Contractor Qualifications

## All works must be undertaken by a recognised NICEIC, NAPIT or ECA Approved Contractor using fully qualified staff in accordance with the best practice guidance found in Guidance Note 3: Inspection and Testing of BS7671:2018

- Name & Position

- Qualifications

- Safety Certificates relevant to the works undertaken (including UKATA Asbestos Awareness).

- Driving licence information

- CSCS Card (if held)

- DBS checks

The contractor must ensure that these details are passed onto Homes in Somerset as any changes or updates are made. Details must be provided prior to starting any works.

## The contractor shall provide at the beginning of the contract details on the contract staffing and their qualifications, and update this list as staff change.

## All contractor visiting staff shall undertake at the contractor’s expense an annual UKATA asbestos awareness course and provide a copy of these certificates to Homes in Somerset.

## All operatives working within the scope of this contract will provide the client with the following information, per operative;

    - Name & Position

    - Qualifications

    - Relevant Safety Certificates

    - Driving licence information

    - CSCS Card (if held)

## All contractor visiting staff shall wear identity badges and make an appointment with the tenant prior to visiting.

# Recording & Monitoring

## Periodic Inspection Report Content and Format

All reports must be written in conformation with BS7671 to the most recent standard.  Homes in Somerset expect an electronic copy to be sent to ComplianceTeam@homesinsomerset.org  within 5 working days of the inspection and a written copy to be sent to the tenant within 10 working days of the inspection.

The report must contain: -

- Description of the extent of works, including details of parts of the installation inspected and details of what the inspection and testing covered.

- Any limitations which may have been identified during the inspection and testing process.

- Details of any damage, deterioration, defects, dangerous conditions and any non-compliance with British Standards which may give rise to danger.

- Schedule of Inspection.

- Schedule of Test results.

Any Category 1 failures must be immediately notified to Homes in Somerset prior to the electrician leaving the site, who will either authorise their repair or isolation of the system/part of system until the required repair can be completed.

Payment for services will only be made once all certification has been verified as complete, and authorisation has been made by the Homes in Somerset Contract Manager.

## The contractor shall allow for review meetings to be held at monthly intervals throughout the contract.

All records must be stored in an electronic format which has been agreed with Homes in Somerset and must be accessible by Homes in Somerset Staff and their contractors.

Existing records will be provided to the winning contractor prior to the commencement of the contract.

## 7a - Live View, Reporting, and Management System

Contractors are to provide and manage a Compliance, Live View, Reporting, and Management system with client access to allow full visibility of all compliance actions.

This system must include the following criteria:

Criteria 1 - Live View/Monitoring

Real-Time Compliance Dashboard:

- Provide a visual dashboard with an at-a-glance view of the organisation’s compliance status.

- Display key performance indicators (KPIs), compliance levels, risk areas, and open tasks.

- Customisable views to suit different user needs (e.g., by department, risk category, or regulatory requirement).

Alerts & Notifications:

- Ability to set automated alerts for non-compliance, upcoming deadlines, and changes in regulations.

- Notifications via email, SMS, or in-app for urgent compliance issues.

- Live Data Feed

- Real-time risk assessment of compliance-related issues.

Reporting:

- Pre-defined and customisable report templates for audit, compliance status, risk management, and regulatory reporting.

- Automated generation of periodic reports (e.g., daily, weekly, monthly).

Compliance Audits:

- Detailed audit logs for tracking compliance activities, changes, and actions taken.

- Ability to generate audit trails for internal and external review.

Data Export:

- Export reports in various formats (e.g., PDF, Excel or CSV) for ease of sharing and analysis.

Criteria 2 - Management and Workflow

Task Management:

- Assign tasks to individuals or teams related to compliance actions.

- Track task status (pending, in-progress, completed) and deadlines.

- Provide reminders for overdue tasks.

Document Management:

- Centralised storage for compliance-related documents (e.g., policies, procedures, certificates).

- Version control and access restrictions to ensure document integrity.

Regulatory Change Management:

- A system for tracking changes in regulatory requirements and mapping them to a compliance framework.

- Notifications about changes in legislation or industry standards.

Incident Management:

- Reporting and tracking of non-compliance incidents.

- Ability to document the response and corrective actions taken.

Role-Based Access Control (RBAC):

- Customised user roles and permissions to control access to sensitive compliance data.

- Administrator, manager, and staff levels with varying degrees of access and control.

Criteria 3 - User Interface & Experience

Customisable Dashboards:

- Users should be able to personalise their dashboards to focus on the most relevant compliance data.

Criteria 4 - Integration and Compatibility

System Integration:

- Ability to integrate with other internal systems (e.g., ERP, HR, CRM) for a seamless flow of compliance data.

- API capabilities for integration with third-party tools or external data sources.

Data Security and Compliance:

- Ensure compliance with industry-standard security protocols (e.g., encryption, secure login, two-factor authentication).

- Compliance with data protection regulations such as GDPR for user data.

Criteria 5 - Data Analytics & Insights

Trend Analysis:

- Built-in analytics to help identify trends in compliance, risk areas, and overall organisational performance over time.

Predictive Analytics:

- Ability to use historical data to predict potential compliance risks.

Custom Reports & Dashboards:

- Allow users to create custom reports and dashboards based on specific needs, with drag-and-drop functionality.

Criteria 6 - Audit and Compliance History

Audit Trails:

- Automatic tracking of all compliance activities with time-stamps and responsible individuals.

- Ability to access historical compliance data for audits, internal reviews, and benchmarking.

Training and Support

- Access to training materials (videos, user manuals, FAQ) for on boarding and ongoing education.

- Help Desk Support

Criteria 7 - Scalability & Flexibility

Scalability:

- The software should support scalability to accommodate existing remote managed systems currently used by Homes in Somerset

- The software should support scalability to accommodate growing organisations or changes in regulatory environments.

Flexible Configuration:

- Ability to easily configure the software to reflect changes in compliance requirements, reporting formats, or workflows.

Criteria 8 - Compliance Monitoring & Continuous Improvement

Continuous Monitoring:

- Continuous tracking of compliance status and quick detection of new non-compliance incidents.

Performance Analytics:

- Performance analytics to gauge the effectiveness of compliance processes and suggest improvements.

Criteria 9 - Cost & Licensing

Pricing Model:

- Clear definition of any additional costs for add-ons, integrations, or support services.

Details of the Service Providers proposed system, and how this complies with the above criteria will be discussed with HIS at tender stage.

# Key Performance Indicators (KPI’s)

In order to ensure that the contract is meeting the standards required a number of KPI’s will be included within the contract.

KPI’s will be reported on a monthly basis and relate to inspections due during that month. At the end of each month a new list of premises to be inspected will be submitted to Homes in Somerset detailing the type of inspection due in the following month.

Access to most sites will be made either with the Caretaker, Homes Check co-ordinator or Site Manager. Clarifications and assistance regarding communal access can be obtained by contacting the Homes in Somerset Compliance Team.

The attached document details the KPIs that will require monitoring and these will form part of the contract requirements.

KPI’s can be provided through the Compliance, Live View, Reporting, and Management system.

# Performance Indicators

## In order to ensure that the contract is meeting the standards required a number of Performance Indicators have been included within the contract. These may change during the life of the contract.

## The performance indicators will be reported on a monthly basis and relate to inspections due during that month. At the end of each month a new list of premises to be inspected will be submitted to Homes in Somerset detailing the type of inspection due in the following month.

| Indicator | Number completed | Completed on time | Completed late | Not completed | PI % | Assigned to |
| --- | --- | --- | --- | --- | --- | --- |
| Number of inspections due in month |  |  |  |  |  | Contractor |
| Number of C1 failures |  |  |  |  |  | Contractor |
| Number of inspection reports submitted to HIS ** |  |  |  |  |  | HiS |
| Second or subsequent visit required to gain access |  |  |  |  |  | Contractor |
| Tenant notified of visit by contractor |  |  |  |  |  | Contractor |
| Number of Annual Portable appliance tests Due each Month |  |  |  |  |  | Contractor |
| Reactive repair carried out Monthly. |  |  |  |  |  | Contractor |

## ** The number of inspection reports should tally with the number of inspections undertaken, relating to Periodic and Lighting Inspections.

# General Contract Requirements

The contractor is required to submit a copy of their code of practice and certification of registration annually or when any changes are made.

The contractor shall not sub-let the works to a third-party contractor without written consent from a member of the Homes in Somerset, Property Services department.

The Contractor must provide, on appointment, general risk assessments and method statements (RAMS) for routine and standard operation to be carried out.  Further RAMS will be required before commencement of any works outside the scope of those standard operations or when appropriate.

The Contractor will, before final appointment, provide references from past or existing clients to comment on the standard of work and operations.

Work shall not commence unless Homes in Somerset has given written permission (electronic or physical) to proceed, or the contractor is in receipt of an official order.

The order number must be quoted on all correspondence, service records and invoices.

All contractor visiting staff shall wear identity badges and make an appointment with the tenant/caretaker/support at home co-ordinator or other persons acting on behalf of Homes in Somerset prior to visiting.

The contractor shall, during inspection, testing and servicing carry out minor repairs e.g. tighten a joint, replace a screw etc. to ensure the integrity of equipment is maintained and appliances remain safe.

Any serious defect or unsafe situation must immediately be notified to Homes in Somerset prior to the engineer leaving the site, who with either authorise the repair or isolation of the system/part of system until the required repair can be completed.

The contractor has authorisation to spend a maximum of £350.00 per site on remedial actions that can reasonably be carried out at the time of the service visit – A full breakdown of works and costs must be provided in these instances.

All work outside of the normal contract will be charged as per the agreed rate rounded to the nearest 10 minute.

The contractor will advise Homes in Somerset of any changes to legislation, British Standards or guidance relating to fire safety.

# New Technologies

Homes in Somerset are committed to embracing smart technologies in order to better manage electrical safety across their portfolio, and in so doing, reduce their environmental impact.

Throughout the term of this contract, Homes in Somerset will look to implement the latest technology in servicing, monitoring and record keeping of all electrical systems.  This may include the ability to monitor and extract data when access to premises is not possible, provision of early warning of unit failure, or advise when a system has been tampered or interfered with.

In so doing, Homes in Somerset aim to reduce travel to and from premises, costs and energy. Smart technologies will also allow Homes in Somerset to demonstrate consistent and continuous compliance across their property portfolios with added stakeholder reassurance.

Those tendering for this contract should demonstrate a willingness to share this commitment and provide a case study to support this.