## RC62 Checklist
RC62 Checklist - Recommendations for fire safety with photovoltaic panel installations
6.1 Compliance with fire safety legislation (section 1) |  | Yes | No | N/A | Action required | Due date | Sign on completion | Comments | Contractor Comments
6.1.1 | Has a suitable and sufficient fire risk assessment been undertaken in compliance with the Regulatory Reform (Fire Safety) Order 2005 (or equivalent legislation in Scotland and Northern Ireland) or been reviewed following the installation of PV panels? (5.1.1) | [6 empty] | Client responsibility.
6.1.2 | Have elements of a photoelectric panel installation, such as the power inverter, which represent significant potential sources of ignition in an area where an explosive atmosphere may form been addressed in any assessment carried out in compliance with the Dangerous Substances and Explosive Atmospheres Regulations (DSEAR)? (5.1.2)
6.1.3 | Have installers complied with building legislation, such as Approved Documents A and B to the Building Regulations (or the equivalent legislation in Scotland and Northern Ireland) and also observed local planning requirements? (5.1.3)
6.1.4 | Where installations are proposed on historic buildings, have national heritage organisations such as English Heritage, Historic Scotland and Cadw been consulted? (5.1.4) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.2 Business continuity (section 2)
6.2.1 | Is management aware that even a small fire resulting in a loss of power, even on a temporary basis can have a disproportionate effect on a business and be sufficiently severe to result in severe disruption, with associated loss of orders, jobs, income and profit? (5.2.1) | [6 empty] | Client responsibility.
6.2.2 | Have steps been taken to ensure the continued smooth running of the business by making a suitable emergency plan? (5.2.2) | [6 empty] | Client responsibility.
6.2.3 | Has the emergency plan been tested by means of a tabletop exercise, with the results being assessed and amendments made to the plan as necessary? (5.2.3) | [6 empty] | Client responsibility.
6.2.4 | Has consideration been given to applying commercially available computer programmes to develop and check the adequacy of the plan? (5.2.4) | [6 empty] | Client responsibility.
6.2.5 | Have carefully drafted quality assurance measures been applied at the design, installation, start-up and operating stages of PV systems, as well as when programming servicing and maintenance or replacement of panels? (5.2.5) | [6 empty] | Client responsibility.
6.3 Fire safety management (section 3)
6.3.1 | Are all waste materials swept up and removed at the end of each working period during the installation process? (5.3.1)
6.3.2 | At the commissioning stage, did the nominated operators of the system have the function and control of the system explained to them by the installer and full details of the system and its operation handed over in writing? (5.3.2)
6.3.3 | Are windblown litter and leaves not allowed to accumulate, especially around or beneath PV panels? (5.3.3)
6.3.4 | Do all installation engineers receive suitable instruction when they arrive at the premises as to the sound of the fire alarm and the actions that they should take if hearing the alarm or discovering a fire? (5.3.4)
6.3.5 | Is the possibility of deliberate fire raising from outside the building by intruders or from within by staff addressed? (5.3.5)
6.3.6 | Unless completely unavoidable, is hot work such as welding, flame cutting and similar activities prohibited during the installation process or in the vicinity of PV panels following installation? (5.3.6)
6.3.7 | If for justified reasons hot work, including operations involving hot work on roofs, has to be undertaken, is it only conducted under an effective Permit to Work system? (5.3.7)
6.3.8 | Is automatic smoke detection inside a building, especially those that are normally unoccupied, in which electrical control equipment for PV panels is located? (5.3.8)
6.3.9 | Are a suitable number of appropriate portable fire extinguishers available adjacent to the control and switchgear and immediately accessible in the case of a fire? (5.3.9)
6.3.10 | Is it appreciated that although in most cases the installation of water sprinklers is beneficial for the protection of property, such an installation will not be designed to protect the photovoltaic panels? (5.3.10)
6.3.11 | Is care taken that obstructions and stored materials do not reduce the level of ventilation provided for the inverters? (5.3.11)
6.3.12 | Is the installation serviced and maintained in accordance with the installer’s instructions? (5.3.12) | [6 empty] | Client responsibility.
6.4 Design (section 4)
6.4.1 | Has consideration been given to the fact that PV panels may be located on roofs, walls or at ground level and that for maximum benefit, they should face approximately south? (5.4.1)
6.4.2 | Has care been taken that trees do not grow so as to shade or allow significant deposits of twigs and leaves to fall onto the panels? (5.4.1)
6.4.3 | Has the option of fully integrated PV roof tiles or wall panels been considered as they may be practical and economically attractive? (5.4.2) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.4.4 | Has due consideration been given to ease of installation, access for maintenance and ease of removal and replacement in the event of damage or fault? (5.4.2)
6.4.5 | Has it been ensured at the design stage that a sufficient area of roof remains free of panels to allow access and maintenance work to be carried out safely? (5.4.3)
6.4.6 | Has a comprehensive survey of the site of the intended installation been undertaken by a qualified surveyor at the initial design stage to ensure that the stability of the structure will not be compromised and aerodynamic effects will not impact on other parts of the building or neighbouring premises? (5.4.4)
6.4.7 | Does the survey report address issues concerning the means for ensuring that the thermal insulation and fire protection properties of the roof are maintained following the installation and that the roof remains watertight? (5.4.5)
6.4.8 | Where designs of new build premises include the integration of PV panels into the fabric of the structure, is care taken that the products selected are such that the fire-related properties of the elements of structure remain compliant with the requirements of Approved Document B to the Building Regulations or equivalent legislation in Scotland and Northern Ireland? (5.4.6) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.4.9 | Has careful consideration been given where it is proposed to site PV panels on combustible roofs? (Wherever possible this should be avoided.) (5.4.7)
6.4.10 | Where consideration is being given to panels of a type that also allow them to serve as elements of glazing, has specialist advice been sought? (5.4.8) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.4.11 | Has it been checked that mounting systems do not interfere with other functions of a structure and thus do not straddle heat expansion joints or fire compartment walls? (5.4.9)
6.4.12 | Do panels conform to BS EN 61215 or BS EN 61646 in conjunction with BS EN 61730-1 and BS EN 61730-2 so that they may withstand inclement weather conditions? (5.4.10)
6.4.13 | Is the layout of the panels on the roof such that areas of panels are separated by panel-free areas so that effective firefighting is possible? (5.4.11)
6.4.14 | Are panels securely fixed using suitable mounting systems that are securely fastened to the supporting structure of the roof? (5.4.12)
6.4.15 | Where the panels to be installed are of a type that has micro-inverters mounted behind each unit, has access to these components been addressed at the design stage, especially in the case of panels located in the middle of roof? (5.4.13) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.4.16 | Where PV panels are to be installed on an existing roof has consideration been given to the additional weight presented by the panels? (5.4.14)
6.4.17 | Has a structural engineer or roofing specialist been consulted at the planning stage regarding the proposed extra loads? (5.4.15)
6.4.18 | Have the problems associated with finding suitable fixing centres for attaching panels to older roofs been addressed? (5.4.16) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.4.19 | Have the hazards associated with the winter build up of ice and snow by panels on the roof been addressed by fitting low protective mesh barriers to the eaves? (5.4.17)
6.4.20 | Has a structural engineer or roofing specialist been consulted to ensure that the combined weight of the panels, snow and ice would not compromise the design load for the roof? (5.4.17).
6.4.21 | Have the problems associated with cavities below panels introducing lateral wind forces resulting in uplift been considered at the design stage? (5.4.18)
6.4.22 | Has care been taken when designing large free-standing arrays that the land selected is not prone to flooding in poor weather and not made available for grazing animals or commercial crops? (5.4.19) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.4.23 | Is undergrowth controlled manually, by the planting of specially selected grasses or by the use of non-chlorate-based weed killers? (5.4.19) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.4.24 | Are arrays of photovoltaic panels on agricultural premises sited so as not to be exposed to substances such as ammonia from cowsheds that can lead to premature ageing of the panels? (5.4.20) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.4.25 | Are long runs of high value cable buried to deter theft? (5.4.21) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.4.26 | Where necessary are ground mounted panels and control equipment protected from damage by vehicles by kerbs or bollards? (5.4.23) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
6.5 Installation (section 5)
6.5.1 | Is there effective coordination of all specialists involved in the design, planning, installation and commissioning stages? (5.5.1)
6.5.2 | Have the PV panel systems been manufactured and installed by a competent organisation recognised by the Microgeneration Certification Scheme (MCS)? (5.5.2)
6.5.3 | Have appropriate panels been selected for the application and mounted in accordance with the manufacturer’s instructions? (5.5.3)
6.5.4 | Have mounting systems that hold the panels parallel to the angle of the roof been used? Where those that increase this angle have to be used, has careful planning been undertaken to formulate a strategy for protecting the roof from any additional loading from the effects of wind or an increased build up of snow or ice? (5.5.4)
6.5.5 | Is sufficient space available to access the roof area to allow panels to be taken up and installed? (5.5.5)
6.5.6 | Is the location of the PV panels away from outlets for dusts and fumes and in a position where they will not be exposed to sources of heat or steam, and maintained clear of deposits, especially those from cooking areas? (5.5.6)
6.5.7 | Are PV panels and unprotected cables located so as not to be laid over a fire compartment wall? If the laying of cables over or through a fire compartment wall is unavoidable then are the cables protected using cable ducts that extend at least 1m each side of the wall and provide the same degree of fire resistance as the compartment wall over or through which they pass? (5.5.7)
6.5.8 | Is ancillary switchgear within the building kept clear of all storage and are control units located in cabinets providing at least 60-minute fire resistance and where necessary protected from damage by suitable bollards or guard rails? (5.5.8)
6.5.9 | Do the Installations incorporate power inverters that comply with BS EN 62109 and products that are selected and installed to ensure that the installation has a sufficiently long work life with a high efficiency of power conversion? (5.5.9)
6.5.10 | Are suitable components specified and installed in accordance with the manufacturer’s instructions, especially where they may be required to operate effectively at temperatures over 35oC? (5.5.10)
6.5.11 | Are power inverters acknowledged as a fire hazard when the hazard zones are identified during the DSEAR assessment for the premises? (5.5.11)
6.5.12 | Are the wiring and other elements of the electrical installations designed, installed and periodically tested by an electrician competent in working on DC as well as AC installations, and in accordance with the current edition of BS 7671? (5.5.12)
6.5.13 | Have ground fault detection units been installed to prevent short circuits? (5.5.13)
6.5.14 | Are the cables, housings and junction boxes selected following consideration of the environmental conditions, especially on agricultural premises where corrosive gases such as ammonia may be released from slurry pits and the like? (5.5.14)
6.5.15 | Are panels and wiring located where they are not likely to be damaged by rodents? (5.5.15)
6.5.16 | Do components of low voltage control and switchgear circuits comply with the relevant parts of BS EN 61439, with generator junction boxes on the DC side of the installation incorporating sufficient protective insulation to protect against the maximum open circuit voltage of the panel array? (5.5.16)
6.5.17 | Is a load break switch that is suitable for isolating DC voltages provided on the DC side of the circuit unless this facility is pre-installed in the current inverter? Is a further double pole isolation switch installed to allow the inverter to be isolated from the AC mains electricity supply necessary for its operation? (5.5.17)
6.5.18 | Is care taken to ensure that AC isolator switches are not mistakenly installed in DC circuits as this can lead to a build up of heat within the switch enclosure and subsequently a fire? (5.5.18)
6.5.19 | Are prominent notices displayed on the DC side of the installation warning that components may still be live even after disconnection from the current inverter? (5.5.19)
6.5.20 | Is care exercised with the DC side of the installation as protection against overload by the use of some forms of conventional circuit breakers is ineffective? (Consideration should be given to installing an electrical arc detection facility as this provides a more rapid form of protection than conventional over current protection devices.) (5.5.20)
6.5.21 | Are long runs of DC wiring avoided and is DC wiring laid so as to avoid being routed through hidden areas and areas where highly combustible materials such as hay and straw may be handled or stored? (5.5.21)
6.5.22 | Is care taken to avoid damage to cables by abrasion or pulling across sharp edges? (5.5.22)
6.5.23 | Is the PV installation installed so as not to compromise the effectiveness of any existing lightning protection system? (5.5.23)
6.5.24 | Are cables and wiring on the AC side of the installation protected by suitable surge protection devices such as circuit breakers or preferably residual current devices? (5.5.24)
6.5.25 | Are all extraneous metal components adequately bonded and earthed? (5.5.25)
6.5.26 | Is wiring protected from the affects of sunshine and the elements? (5.5.26)
6.5.27 | Following the installation, are checks made to ensure that all holes around cables passing through fire compartment walls, floors and ceilings in the building are suitably fire stopped? (5.5.27)
6.5.28 | Will the commissioning of the system only be undertaken by trained, competent personnel? (5.5.28)
6.6 Maintenance (section 6)
6.6.1 | Is all maintenance undertaken strictly in accordance with the installer’s instructions on an annual basis by competent engineers familiar with the form of installation and with appropriate access equipment? (5.6.1)
6.6.2 | Is serious consideration given to carrying out a thermographic examination of the panels in order to identify hot spots in the panels and at the time of each service visit? (5.6.2)
6.6.3 | As well as an initial inspection following the installation, are periodic safety examinations of the structure carried out according to a risk assessment which considers the age, form of construction and location of the installation? (5.6.3)
6.6.4 | Are safety devices installed to isolate the current inverter from the DC supply and the converted AC current in order to permit safe maintenance or exchange of the inverter? (5.6.4)
6.6.5 | Are the PV panels of a type that allows the bypass diodes to be changed? (5.6.5)
6.6.6 | Is a PV generation meter connected inside the building to provide a real-time indication of how much electricity the system is generating? (5.6.6)
6.6.7 | Is the cleaning of panels only undertaken by specialist personnel using equipment supplied from an electric socket protected to an IP55 or IP56 level of ingress protection in accordance with BS EN 60529? (5.6.7)
6.6.8 | Are the cavities beneath the panels left unenclosed? (5.6.8)
6.6.9 | Are redundant and damaged panels disposed of by a licensed waste carrier as some components contain traces of heavy metals? (5.6.9)
6.7 Security (section 7)
6.7.1 | Are all panels marked with non-removable serial numbers which are recorded by the owner or with the post code of the installation? (5.7.1)
6.7.2 | Does the security risk assessment for the premises focus on denial of access to the site as a whole? Following this, is consideration given to the security threat to individual building(s)? (5.7.2)
6.7.3 | Is access to roofs and to ladders and other climbing aids denied to intruders? (5.7.3)
6.7.4 | Does security comprise a combination of measures, typically involving a combination of physical protection and electronic security systems, such as intruder alarms and security lighting, tailored to the needs of the individual premises or site concerned? (5.7.4)
6.7.5 | For high security premises, do measures include total perimeter fencing and on-site or patrolling security guards? (5.7.4)
6.7.6 | Has some form of physical protection that prevents panel removal been adopted? (5.7.5)
6.7.7 | Are non-return or ‘tighten-and-break’ anti-theft screw heads used to fasten panels to mounting frames? (5.7.6)
6.7.8 | Is careful attention given to protecting vulnerable, remote and rural systems? (5.7.7)
6.7.9 | In some cases, such as small remote systems powering batteries for environmental monitoring equipment or road signs, are monitored alarms installed? (5.7.8)
6.7.10 | In the case of large installations, has a reinforced concrete wall been built around the panel mountings, to prevent access to the supporting structure and its bolts? (5.7.9)
6.7.11 | Has consideration been given to connecting PV panels in remote and urban installations into an array as a security measure? (5.7.10)
6.8 Provisions for the fire and rescue service (section 8)
6.8.1 | Have arrangements been made to provide prompt access to the site for the fire and rescue service on their arrival? (5.8.1)
6.8.2 | Are arrangements in hand for firefighters to be met by security personnel or other designated staff? (5.8.1)
6.8.3 | Is a clear external route maintained to allow high reach vehicles and pumping appliances to gain suitable access to all buildings? (5.8.2)
6.8.4 | Is suitable information provided for the fire and rescue service at a prominent location, such as the gatehouse? (5.8.3)
6.8.5 | In the case of large installations, are firefighters invited to visit the premises to familiarise themselves with the property and the locations of PV panels on the site? (5.8.4)
6.8.6 | Has consideration been given to the fact that PV panels on the roof can prevent the dissipation of heat and smoke and thus smoke build up in the building may be more rapid than otherwise would have been the case? (5.8.5)
6.8.7 | Is a prominent switch provided in a readily accessible location on each installation to isolate the DC side of the PV system near the panels (a ‘fire service switch’) to ensure the safety of firefighting personnel? (5.8.6)
6.8.9 | Is the isolation switch tested during routine maintenance visits, with the results being recorded? (5.8.6)
6.8.10 | As well as operating the fire service switch, are fire service personnel also able to disconnect the installation from the mains electricity at the intake so as to render the AC side of the installation voltage-free? (5.8.7)
6.8.11 | Are signs indicating the presence of a PV panel installation prominently displayed for the fire and rescue service? (5.8.8)