PRODUCT AND WORKMANSHIP PERFORMANCE

SPECIFICATION FORMING PART OF

THE CLIENT REQUIREMENTS

LAND, DESIGN & BUILD

FOR ALPHA HOUSING ASSOCIATION

December 2024

ARCHITECTURAL SPECIFICATION

Where Contractor is Referred to throughout this Document

The Contractor is to be the Developer as defined in

The Development Agreement and Client Requirements

These specifications were drafted prior to the NI Building Regulation Amendments in June 2022 and Suppliers are deemed to have taken these amendments into account and updated their specifications as appropriate.

In this document, any reference to a British Standard shall be deemed to include an equivalent International Standard where applicable

Table of Contents

Title					Page

B	Complete buildings/ structures/ units		6

B15	Prefabricated framed constructions		8

C	Demolition/ Alteration/ Renovation		14

C11	Site investigation		16

C20	Demolition		18

F	Masonry		21

F10	Brick/ block walling		23

F30	Accessories/ sundry items for brick/ block/ stone walling		30

F31	Precast concrete sills/ lintels/ copings/ features		41

G	Structural/Carcassing metal/timber		45

G12	Isolated structural metal members		47

G20	Carpentry/ timber framing/ first fixing		50

H	Cladding/Covering		59

H11	Curtain Walling 		61

H21	Timber weatherboarding		74

H31	Metal profiled/flat sheet cladding/covering		76

H32	Plastics profiled sheet cladding/covering		82

H65	Single lap roof tiling		85

H71	Lead sheet coverings/ flashings		91

H72	Aluminium strip/sheet coverings/flashings		98

J	Waterproofing		103

J10	Cementitious mortar tanking/ damp proofing		105

J40	Flexible sheet tanking/ damp proofing		109

J42	Single layer polymeric sheet roof coverings		116

K	Linings/Sheathing/Dry partitioning		122

K10	Plasterboard dry linings/ partitions/ ceilings		124

K11	Rigid sheet flooring/ sheathing/ decking/ sarking/ linings/ 		132

Casings

K40	Demountable suspended ceilings				139

L	Windows/Doors/Stairs		146

L10	Windows/ Rooflights/ Screens/ Louvres		148

L20	Doors/ shutters/ hatches		153

L30	Stairs/ ladders/ walkways/ handrails/ balustrades		158

L40	General glazing		161

M	Surface finishes		163

M10	Cement based levelling/ wearing screeds		165

M20	Plastered/ Rendered/ Roughcast coatings		171

M40	Stone/ concrete/ quarry/ ceramic tiling/ mosaic		179

M50	Rubber/ plastics/ cork/ lino/ carpet tiling/ sheeting		184

M60	Painting/clear finishing		190

M61	Intumescent coatings for fire protection of steelwork		197

N	Furniture/Equipment		200

N10	General fixtures/ furnishings/ equipment		202

N14	General signage systems		207

N15	Fire and safety signage systems		212

N17	Portable firefighting systems		215

N25	Permanent access and safety equipment		217

P	Building fabric sundries		220

P10	Sundry insulation/ proofing work		222

P12	Fire stopping systems		227

P20	Unframed isolated trims/ skirtings/ sundry items		231

P21	Door/ window ironmongery		233

P30	Trenches, pipeways and pits for buried engineering services	235

P31	Holes, chases, covers and supports for services		238

Q	Paving/Planting/Fencing/Site furniture		240

Q28	Topsoil and growing media		242

Q30	Seeding/ turfing		246

Q31	External planting		252

Q35	Landscape maintenance		260

Q40	Fencing		271

Q50	Site/ street furniture/ equipment		276

R	Disposal systems		278

R10	Rainwater drainage systems		280

R11	Above ground foul drainage systems		285

R12	Below ground drainage systems		291

Z	Building fabric reference specification		303

Z10	Purpose made joinery		305

Z11	Purpose made metalwork		308

Z12	Preservative/ fire retardant treatment		313

Z20	Fixings and adhesives		315

Z21	Mortars		319

Z22	Sealants		322

Z31	Powder coatings		324

Z33	Anodizing		328

B

Complete buildings/ structures/ units

B15

Prefabricated framed constructions

B15 Prefabricated framed constructions

To be read with Preliminaries/ General Client Requirements.

10    REFER TO CLIENT REQUIREMENTS FOR WHEN TO SUPPLY SPECIFICATION DATA.

•	 Submit the following module information:

-	Drawings: Typical plan, section, elevations and details, at suitable scales.

-	Technical information, reports, calculations and certification demonstrating compliance

with specification.

-	Schedule of loads to be transmitted to supporting structure.

-	Details of connections to supporting structure.

-	Schedule of builder's work, special provisions and special attendance by others.

-	Examples of standard documentation from which project quality plan will be prepared.

-	Installation method statements and programme.

Proposals for replacing damaged or failed items/ constructions.

GENERAL

110A	CONTRACTORS DESIGNED TIMBER FRAMED DWELLINGS Generally

•	 THE DEVELOPER IS RESPONSIBLE FOR THE OVERALL DESIGN, PERFORMANCE,

CO-ORDINATION AND ERECTION OF THE TIMBER FRAME, WALL INSULATION,

WATERPROOF & VAPOUR CONTROL MEMBRANES, AND ASSOCIATED FIXINGS TO

ACHIEVE THE FOLLOWING AIR TIGHTNESS, CODE FOR SUSTAINABLE HOMES ETC

DESIGN CRITERA AS SET OUT IN THE WORKS INFORMATION DRAWINGS AND

SPECIFICATIONS.

•	 THE DEVELOPER IS TO DETERMINE WHETHER IT WILL BE THEM

OR THEIR APPOINTED SPECIALIST TIMBER FRAME MANUFACTURER/SUPPLIER

WHO IS RESPONSIBLE FOR THE PROVISION AND INSTALLATION OF

COMPONENTS AND MATERIALS IN CONNECTION WITH THE OVERALL TIMBER

FRAME CONSTRUCTION INCLUDING SHEATHINGS, INSULATIONS, WATERPROOF &

VAPOUR CONTROL MEMBRANES, SERVICE ZONES AND ANY OTHER INTEGRAL

COMPONENTS OF THE TIMBER WALL, FLOOR AND ROOF CONSTRUCTIONS.  THE

CONTRACTOR IS TO RETURN WITH THIER TENDER PRICE A LIST DETAILING THE

SCOPE OF WORKS BEING CARRIED OUT BY EACH OF THE TIMBER FRAME

MANUFACTURER/SUPPLIER AND CONTRACTOR IN RELATION TO THE OVERALL

TIMBER FRAME CONTRUCTION.

•	 TIMBER FRAME IS TO PROVIDE A SUITABLE AND STABLE STRUCTURE TO WHICH

THE OUTER MASONRY LEAFS CAN BE TIED BACK TO FOR SUPPORT IN

ACCORDANCE WITH BUILDING REGULATIONS (NI) AND APPROPRIATE BRITISH

AND EUROPEAN STANDARDS.  TIMBER FRAME TO BE CONSTRUCTED AS

NECESSARY TO SUIT THE MODULES, COURSING, AND DIMENSIONS OF

BRICKWORK AND BLOCKWORK AS NEXCESSARY - NOT WITHSTANDING ANY

DIMENSIONS SHOWN ON WORKS INFORMATION DRAWINGS.

•	 Manufacturer: Contractors choice.  Timber frame elements to have a minimum design life

of 60 year.  Contractor to provide minimum 25year warranty and minimum 3no. references

and examples from similar constructions.

•	 Timber Frame Structure Generally:

Timber frame to be designed to carry the external masonry skin as necessary - refer to

sections F10 & M20.

Timber frame to be designed to accommodate any additional contractors designed

structural steel necessary for loadbearing support of structures and fabric above.  Any

additional structural steel elements to be fireproofed accordingly and fully integrated into

timber frame design.

Provide calculations and design certificates to the satisfaction of Building Control and

Structural Consultant.

•	 Supporting structure: Ground bearing & suspended concrete floors and masonry leaf as

detailed on Structural Engineers information.  Contractor is responsible for ensuring that

timber frame design is completely compatible with supporting structure and carry out any

necessary works in deviation to the works information.  Contractor to coordinate

construction proposals and fixing details as necessary - Provide details for CA approval.

•	 External walls:

- Frame:

Species: As supplied.

Cross section size: 89mm as necessary - designed by timber frame manufacturer. .

Stud centres: 400mm as necessary - designed by timber frame manufacturer. .

- Outer facing: Thermal Foil breather membrane on 9mm OSB sheathing as section F30 -

to be determined by timber frame designer.

- Insulation: Rigid PIR interstud insulation as F30.

Thickness: As F30.

- Inner facing: Vapour control layer and Rigid PIR insulation as section F30, 35mm

service zone and impact resistant plasterboard.

•	 Party walls:

-	Frame:

Species:  [As supplied].

Cross section size:  [89mm As necessary - designed by timber frame manufacturer. ].

Stud centres:  [400mm As necessary - designed by timber frame manufacturer. ].

-	Outer facing:  [None, 72mm mineral wool interframe insulation between party stud walls

to be determined by timber frame designer].

-	Insulation:  [Mineral wool interstud insulation].

Thickness:  [As section F30].

- 	Inner facing:  [9mm OSB boarding, 19mm plasterboard, vapour control layer, 12.5mm

plasterboard, 35mm service zone and impact resistant plasterboard].

- 	Other requirements:  [Party wall construction to satisfy Robust Detail E-WT-1].

•	 Internal walls:

-	Type: All.

-	Frame:

Species: As supplied.

Cross section size: 89mm As necessary - designed by timber frame manufacturer..

-	Insulation: Acoustic mineral wool between suds of walls between bathrooms / kitchens

and bedrooms / living areas.

Thickness: 50mm as section P10.

-	Facing material: 15mm impact resistant plasterboard as section K10 with skim plaster

finish.

•	 Roof:

-	Structure: Contractor designed timber trussed rafters as section G20.

-	Insulation: Quilt insulation as section P10.  Additional ceiling.

Thickness: 350mm as specified.  Additional rigid PIR, vapour & service zone to all

dwellings.

-	Finish: 15mm plasterboard with bonding & skim finish as section K10.  Moisture

resistant plasterboard to bathrooms, WCs and kitchens.

•		Ground floor construction: In situ concrete slab / suspended hollow precast concrete; as

section E05: 100mm floating sand / cement screed as section M10.

-	Insulation: Rigid board insulation as section M10.

Thickness: 200mm.

•	 Upper floor construction: VARIES - REFER TO K11; Plasterboard ceilings with bonding &

skim finish as section K10.  Moisture resistant plasterboard to bathrooms, WCs and

kitchens.

•	 Other requirements: All timber to be FSC or similar third party certified to comply with

BREEAM Code for Sustainable Homes.

PERFORMANCE

205	DESIGN 	OF TIMBER FRAME

•	 Standard: In accordance with BS 5268-2 to -7.  BS 6399 Part2 (wind loads).  BS6399 Part

1 & Part3 (loadings).  NHBC Standards Volumes 1&2 1992.  Current Building Regulations

(Northern Ireland).

215A	STRUCTURAL INTEGRITY

•	 Requirement: Design coverings/ flashings and methods of attachment to prevent loss of

weathertightness and permanent deformation due to wind pressure or suction.

•	 Wind loads: Calculate to BS 6399-2, Standard Method.

•	 Imposed roof load (no access): Determine from BS 6399-3.

•	CONSTRACTORS DESIGN TO INCLUDE ALL INTERNAL AND EXTERNAL WALLS,

TRUSSES, RAFTERS, JOISTS, BRACING, BINDERS & FIXINGS, INFILL TIMBERS,

ATTIC CATWALK AREA, DESIGN FOR FUTURE HOISTS, WATER TANK AND M&E

EQUIPMENT SUPPORT AREAS, HIPS, VALLEYS, TRIMMERS, DORMERS,

CANOPIES, SOLAR PANEL SUPPORTS ETC. ALL AS INDICATED ON THE

ARCHITECT AND M&E ENGINNERS DRAWINGS.

220	FIRE RATINGS

•	 Reaction to fire:

-	Standard: Generally to BS EN 13501-1.

-	Class:

External wall surfaces: 1.

Internal linings: 1.

Roof surfaces: AA.

•	 Resistance to fire:

-	Standard: To BS 476-20 to -23.

-	Period of resistance:

Structural and separating elements: 60 minutes.

225A	ACOUSTIC PERFORMANCE – DWELLINGS

•	 Method of measurement: In accordance with BS EN ISO 140.

-	Rating: In accordance with BS EN ISO 717.

•	 Testing company: UKAS accredited or European equivalent.

•	 Sets of tests:

-	Type: Dwelling house.

-	Number required: In accordance with NI Building Regulations. Acoustic tests are to be

carried out at pre-completion stage, by a qualified acoustic engineer following the normal

programme of testing described in Technical Document G : Appendix B.  Acoustic

testing will not apply to any relevant part of the building where the Contractor

adopts a design detail or details from the set approved and published by Robust Details

Ltd.

•	 Airborne sound insulation:

-	Source room: Living room & habitable rooms.

-	Measurement room: Living room & habitable rooms.

-	Required sound insulation value: Walls, Floors & Stairs to have minimum 45dB airborne

sound insulation.

•	 Impact sound insulation:

-	Source room: Living room & habitable rooms.

-	Measurement room: Living room & habitable rooms.

-	Required sound insulation value: Floors & Stairs to have maximum 62dB impact sound

insulation.

•	 Test certificates: Submit as soon as available.

242A	THERMAL INSULATION Generally for houses (no CSH)

•	 Calculation method: SAP 2009.

•	 Required U-values:

-	External walls: 0.18 W/m²K.

Windows: 1.4 W/m²K.

Doors: 1.3 W/m²K.

-	Floors: 0.10 / 0.09 W/m²K.

-	Roof: 0.10 W/m²K.

245A	DURABILITY

•	 Minimum life span:

-	Structure:

Element: ALL TIMBER FRAME WALL, FLOOR & ROOF ELEMENTS.

Required life span: minimum of 60 years.

250	WATER PENETRATION

•	 Requirement: Under site exposure conditions moisture must not penetrate onto internal

surfaces, or into cavities not designed to be wetted.

255	INTERSTITIAL CONDENSATION

•	 Requirement: Determine interstitial condensation risk of roofs and external walls using the

method described in BS 5250, Appendix D.

•	 Outdoor psychrometric conditions (notional): To BS 6229, table A.1.

-	Indoor psychrometric conditions (notional):

-	Temperature: 20 degrees C.

-	Relative humidity: 55%.

-	Vapour pressure: 1.285 kPa.

•	 Calculated amount of winter interstitial condensate (maximum): 0.5kg/m2.

•	 Calculated annual net condensate retention (maximum): 5% of winter condensate.

260	SURFACE CONDENSATION

•	 Requirement: Determine surface condensation risk of external walls using the method

described in BS EN ISO 13788.

•	 Temperature factor (fmin): Provide satisfactory value.

-	Thermal insulation: Revise if necessary.

•	 Damage and nuisance from surface condensation: Ensure this does not occur.

265	ADDITIONAL SECURITY

•	 Windows, doors, shutters:

-	Standard: To ENV 1627.

Required resistance class: All to Secured by Design Standards.

275A	ENVIRONMENTAL ASSESSMENT – BREEAM Code for Sustainable Homes

•	 BREEAM requirements:

-	All to be in accordance with works information Code for Sustainable Homes Pre-

Assessment.

Other requirements:

Not applicable.

FABRICATION

510	INFORMATION FROM MANUFACTURER

•	 Prior to fabrication of frame, manufacturer to provide:

-	Drawings showing all construction details, including connections and manufactured

tolerances.

-	Risk assessments for the installation and construction process.

-	Installation instructions including training requirements for installers.

-	 Requirements for storage of materials.

EXECUTION

710	TRANSPORTATION

•	 General: Handling, lifting and transportation must not cause damage, or impair the

intended performance of elements or components when subsequently erected.

720	DELIVERY

•	 Inspection: Upon delivery inspect all materials to ensure they are free from damage and

that the required accuracy of erection can be achieved.

730	STORAGE

•	 Support: So as not induce excessive stress into the components.

•	 Protection: Prevent the ingress of water.

740	SUPPORTING STRUCTURE

•	 Survey: Before commencing installation, carry out survey sufficient to verify that required

accuracy of erection can be achieved.

•	 Tolerances: + 10 mm on overall height.

750	ERECTION

•	 Lifting, positioning, fixing:

-	Do not drag units.

-	Lift units from manufacturer's designated points only.

Provide temporarily support, as required.

760	ASSEMBLY

•	 Framing components: Cut squarely or as required for an angular fit against abutting

members.

•	 Fixings: Size and pattern as determined by structural calculation.

•	 Splices: Not permitted except where specifically designed.

•	 Anchor bolts and straps: Correctly positioned at all locations shown on the drawings.

•	 Insulation: Ensure continuity.

770	ACCURACY OF ERECTION

•	 Alignment: Offset on plan or section to vary by not more than 10mm.

•	 Finished appearance: Notwithstanding the tolerances stated above, frames must be

square, regular, true to line, level and plane.

COMPLETION

910	DOCUMENTATION

•	 Manuals: Frame manufacturer to provide manuals detailing repair and modification of the

erected components and level of expertise required to carry out modifications.

C

Demolition/ Alteration/ Renovation

C11

Site investigation

C11 Site investigation

To be read with Preliminaries/ General conditions.

GENERAL REQUIREMENTS

140A	ACCESS TO THE SITE

•	 Details: The Contractor is to visit the site during the tender period and familiarise

themselves with the site conditions and any visible site features.  The Contractor is to take

into consideration the various specialist surveys and reports procured by the Employer in

relation to establishing the nature of the site, its conditions and constraints if any.  It will be

presumed that on submitting their tender price, the Contractor has visited the site as

prescribed, satisfied themselves and taken all site conditions into consideration in their

price.  Contractor also to refer to CDMC's Pre-Construction information.

•	 Contact: Employer - refer to ITT contact details.

150A	PUBLIC SAFETY

•	 Protection of the public and occupiers of adjoining property: Erect temporary fences,

hoardings, footpaths, warning lights, etc. before starting work.

•	 Means of escape from adjoining properties in the event of fire: Maintain for the duration of

the Works.

160A	SITE SAFETY

•	 Excavations and boreholes: Support sides and keep free from ground and surface water.

170A	SURVEY INSTRUMENTS

•	 Equipment calibration: In accordance with manufacturer's recommendations.

•	 Site use calibration: To BS 7334.

•	 Calibration: Use only persons accredited by the United Kingdom Accreditation Service

(UKAS).

•	 Calibration compliance: Submit evidence prior to use.

180	COMPETENCE

•	 Skill and experience: Appropriate for the type of work.

-	Evidence: Submit prior to commencement.

190	PROTECTION

•	 Protect the following: Trees, shrub planting, roots and vegetation etc of existing landscape

features to be retained.  Refer to site layout and landscape architect's proposals.

C20

Demolition

C20 Demolition

To be read with Preliminaries/General conditions

GENERAL REQUIREMENTS

130A	GROUNDWORKS

•	 Old foundations, slabs and the like: Break out, remove, dispose of or recycle as necessary.

•	 Contaminated material: Remove, and carry out remediation as specified.

SERVICES AFFECTED BY DECONSTRUCTION/ DEMOLITION

210	SERVICES REGULATIONS

•	 Work carried out to or affecting new and/ or existing services: Carry out in accordance with

the byelaws and/ or regulations of the relevant Statutory Authority.

220	LOCATION OF SERVICES

•	 Services affected by deconstruction/ demolition work: Locate and mark positions.

•	 Mains services marking: Arrange with the appropriate authorities for services to be located

and marked.

-	Marking standard: In accordance with National Joint Utilities Group 'Guidelines on the

positioning and colour coding of underground utilities' apparatus'.

230	SERVICES DISCONNECTION ARRANGED BY CONTRACTOR

•	 General: Arrange with the appropriate authorities for disconnection of services and removal

of fittings and equipment owned by those authorities prior to starting deconstruction/

demolition.

240A	DISCONNECTION OF DRAINS

•	 General: Locate, disconnect and seal disused foul, surface water, and land drains.

•	 Sealing: Permanent, and within the site.

Any drainage which is redundant / no longer required should be removed and disposed of

and backfilled as necessary.

250A	LIVE FOUL AND SURFACE WATER DRAINS

•	 Drains and associated manholes, inspection chambers, gullies, vent pipes and fittings:

-	Protect; maintain normal flow during deconstruction/ demolition.

-	Make good any damage arising from deconstruction/ demolition work.

-	Leave clean and in working order at completion of deconstruction/ demolition work.

260	SERVICE BYPASS CONNECTIONS

•	 General: Provide as necessary to maintain continuity of services to occupied areas of the

site on which the deconstruction/ demolition is taking place and to adjoining sites/

properties.

•	 Minimum notice to adjoining owners and all affected occupiers: 72 hours, if shutdown is

necessary during changeover.

270	SERVICES TO BE RETAINED

•	 Damage to services: Give notice, and notify relevant service authorities and/ or owner/

occupier regarding damage arising from deconstruction/ demolition.

•	 Repairs to services: Complete as directed, and to the satisfaction of the service authority or

owner.

DECONSTRUCTION/ DEMOLITION WORK

310	WORKMANSHIP

•	 Standard: Demolish structures in accordance with BS 6187.

•	 Operatives:

-	Appropriately skilled and experienced for the type of work.

-	Holding, or in training to obtain, relevant CITB Certificates of Competence.

•	 Site staff responsible for supervision and control of work: Experienced in the assessment

of risks involved and methods of deconstruction/ demolition to be used.

320	GAS OR VAPOUR RISKS

•	 Precautions: Prevent fire and/ or explosion caused by gas and/ or vapour from tanks,

pipes, etc.

330	DUST CONTROL

•	 General: Reduce airborne dust by periodically spraying deconstruction/ demolition works

with an appropriate wetting agent. Keep public roadways and footpaths clear of mud and

debris.

•	 Lead dust: Submit method statement for control, containment and clean-up regimes.

340	HEALTH HAZARDS

•	 Precautions: Protect site operatives and general public from hazards associated with

vibration, dangerous fumes and dust arising during the course of the Works.

350	ADJOINING PROPERTY

•	 Temporary support and protection: Provide. Maintain and alter, as necessary, as work

proceeds. Do not leave unnecessary or unstable projections.

•	 Defects: Report immediately on discovery.

•	 Damage: Minimize. Repair promptly to ensure safety, stability, weather protection and

security.

•	 Support to foundations: Do not disturb.

391	ASBESTOS-CONTAINING MATERIALS – UNKNOWN OCCURRENCES

•	 Discovery: Give notice immediately of suspected asbestos-containing materials when

discovered during deconstruction/ demolition work. Avoid disturbing such materials.

•	 Removal: Submit statutory risk assessments and details of proposed methods for safe

removal.

410	UNFORESEEN HAZARDS

•	 Discovery: Give notice immediately when hazards such as unrecorded voids, tanks,

chemicals, are discovered during deconstruction/ demolition.

•	 Removal: Submit details of proposed methods for filling, removal, etc.

MATERIALS ARISING

510	CONTRACTOR'S PROPERTY

•	 Components and materials arising from the deconstruction/ demolition work: Property of

the Contractor except where otherwise provided.

•	 Action: Remove from site as work proceeds where not to be reused or recycled for site

use.

520	RECYCLED MATERIALS

•	 Materials arising from deconstruction/ demolition work: Can be recycled or reused

elsewhere in the project, subject to compliance with the appropriate specification and in

accordance with any site waste management plan.

•	 Evidence of compliance: Submit full details and supporting documentation.

-	Verification: Allow adequate time in programme for verification of compliance.

F

Masonry

F10

Brick/ block walling

F10 Brick/ block walling

To be read with Preliminaries/ General conditions.

TYPES OF WALLING

112A	CLAY FACING BRICKWORKCLAY BRICKWORK EXTERNAL LEAF TO WALLS OF

TIMBER FRAMED DWELLINGS

•	 Bricks: To BS 771-1.FL Durability.

-	Water Absorption:<14%

-	Standard work sizes:215x102.5x65mm, tolerances to BS 3921.

-	Compressive strength: >20N/mm2

-	Tolerance / Range : T2 / R1

-	Frost Resistance : F2

-	Soluble salt content "Low" (L)

-	Efflorescence: Nil/Slight

-	Thermal conductivity: 0.6W/mK (P-90%)

•	 Manufacturer: Contractor to make allowance for the provision of one of the following facing

brick finish specifications (Contractor to construct 1mx1m sample wall panels of each brick

samples as necessary on site for selection & acceptance by Client & CA:

-	Special shapes: Refer to detailed drawings as necessary.

•	    Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: Group 2.

-	Additional requirements: Contractor to mix brick batches and pallets throughout in

accordance with the manufacturers recommendations / instructions to maintain an even

and consistent brick finish throughout development .

•	 Bond: Half lap stretcher.

•	 Joints: Bucket handle.

•	 Features: Refer to elevational drawings as necessary.

345A	CONCRETE COMMON BRICKWORK GENERALLY

•	 Bricks: To BS EN 771-3.

-	Configuration: Solid.

-	Compressive strength:

Mean value: 30 N/mm².

Category: II.

-	Freeze/ Thaw resistance: Suitable for exposed external use below d.p.c.

-	Work sizes (length x width x height): 215 x 103 x 65 mm.

-	Special shapes: None.

-	Additional requirements: None.

•	 Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: 1:5 masonry cement: sand 4 N/mm² (mortar class 4).

-	Additional requirements: None.

•	 Bond: Half lap stretcher.

350A	CONCRETE COMMON BLOCKWORKGENERALLY

•	 Blocks: To BS 6073-1.dense aggregate

-	Manufacturer: Contractor's choice and agreed with CA & Structural Engineer.

-	Type: Solid.

-	Average compressive strength (minimum): 15 N/mm².

-	Thermal conductivity (maximum) certified by UKAS accredited laboratory at 3% moisture

content to BS EN 12664: 0.11 W/mK.

-	Work sizes (length x height x thickness): 440 x 215 x 100 mm, 440 x 140 x 100 mm.

-	Special shapes: None.

•	 Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: 1:1:4 cement:lime:sand.

-	Additional requirements: None.

•	 Bond: Half lap stretcher.

352A	CONCRETE COMMON BLOCKWORKTO LOAD BEARING WALLS

•	 Blocks: To BS 6073-1.dense aggregate

-	Manufacturer: To be chosen by contractor and agreed with architect.

Product reference: To be chosen by contractor and agreed with architect.

-	Type: Solid.

-	Average compressive strength (minimum): 10 N/mm².

-	Thermal conductivity (maximum) certified by UKAS accredited laboratory at 3% moisture

content to BS EN 12664: 0.11 W/mK.

-	Work sizes (length x height x thickness): 440 x 215 x 215 mm.size achieved by laying

440x215x100 on flat.

-	Special shapes: None.

•	 Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: 1:1:4 cement:lime:sand.

-	Additional requirements: None.

•	 Bond: Half lap stretcher.

355A	LIGHTWEIGHT CONCRETE COMMON BLOCKWORK GENERALLY

•	 Blocks: To BS EN 771-3.

-	Manufacturer: Contractor's choice and agreed with CA & Structural Engineer.

-	Configuration: Hollow.

-	Compressive strength:

Mean value: 7 N/mm².

-	Freeze/ Thaw resistance: Frost resistant.

-	Thermal properties: Thermal conductivity: 0.49 W/mK.

-	Work sizes (length x width x height): 440 x 100 x215  mm.

-	Special shapes: None.

-	Additional requirements: None.

•	 Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: 1:1:6 cement:lime:sand.

-	Additional requirements: None.

•	 Bond: Half lap stretcher.

TESTING

410B	COMPRESSIVE STRENGTH OF MORTAR FOR EACH WALLING TYPE

-  	Testing authority: NAMAS (UKAS) approved laboratory

-  	Test method: in accordance with B.S. 5628: part 1: 1992

-  	Preliminary tests procedure:(to be carried out by ready mix premix mortar

supplier or supplier for mobile on site batching plant if used)

-  	Specimens: (laboratory determination of strengths for mortar designations,

(mixes) proposed for use in the building.)

Number of specimens: 6.

Type: 75mm or 100mm cubes,

Preparation: At least six weeks before walling commences.

-  	Specimen testing: Half of specimens at 7 days. Remainder at 28 days.

Retarded mixes: not allowed on this scheme.

-  	Response to result: If mean compressive strength at 28 days is not within

the range given below repeat tests with more suitable sand or next higher

designation

-  	Site tests procedure: As follows.

-  	Number of specimens: Six per 150m² of walling or per storey whichever the

more frequent.

-  	Specimen types: As preliminary test, but prepared during construction.

-  	Specimen testing: Half of specimens at 7 days. Remainder at 28 days.

Retarded mixes: Extend curing periods to include retardation period.

-  	Required test mean compressive strength at 28 days (N/mm²): To be within

the following range:

Preliminary tests  	Site tests

Min.  		Min.

N/mm²  		N/mm²

(MPa)  		(MPa)

3.6  		2.5

-  	Results: Submit to engineer for approval.

.

415A	FRESH MORTAR CEMENT CONTENT

-  	Test method: 6 no. 75mm or 100mm cubes prepared on site for every 150m2 of

wall.

-  	Test specimens: Test mortar for load bearing walls.

-  	Results: Submit to engineer for approval.

WORKMANSHIP GENERALLY

430	CONDITIONING OF CLAY AND CALCIUM SILICATE BRICKS

•	 Bricks delivered warm from manufacturing process: Do not use until cold.

•	 Absorbent bricks in warm weather: Wet to reduce suction. Do not soak.

440A	CONDITIONING OF CONCRETE BRICKS/ BLOCKS

•	 Autoclaved concrete bricks/ blocks delivered warm from manufacturing process: Do not

use (Do not use until 28 days old).

•	 Age of non-autoclaved concrete bricks/ blocks: Do not use until at least four weeks old.

•	 Avoidance of suction in concrete bricks/ blocks: Do not wet.

Use of water retaining mortar admixture: Submit details.

460	MORTAR GROUPS

•	 Mix proportions: For a specified group select a mix design from the following:

________________________________________________________________________

__

Group  		1  	2  	3  	4

________________________________________________________________________

__

PC*:lime:sand with or without air entraining additive

1:0-0.25:3  	1:0.5-4.5  	1:1:5-6  		1:2:8-9

________________________________________________________________________

__

Masonry cement:sand containing PC* and lime in approx ratio 1:1, and an

air entraining additive

-  	1:3  	1:3.5-4  		1:4.5

________________________________________________________________________

__

Masonry cement:sand containing PC* and inorganic materials other than lime

and air entraining additive

-  	1:2.5-3.5  	1:4-5  	1:5.5-6.5

________________________________________________________________________

__

PC*:sand and air entraining additive

1:3            	1:3-4  	1:5-6  	1:7-8

________________________________________________________________________

__

PC* = Portland cement

•	 Batching: Mix proportions by volume.

•	 Mortar type: Continuous throughout any one type of masonry work.

500	LAYING GENERALLY

•	 Mortar joints: Fill vertical joints. Lay bricks, solid and cellular blocks on a full bed.

•	 Bond where not specified: Half lap stretcher.

•	 Vertical joints in facework: Even widths. Plumb at every fifth cross joint.

520	ACCURACY

•	 Courses: Level and true to line.

•	 Faces, angles and features: Plumb.

•	 Permissible deviations:

-	Position in plan of any point in

relation to the specified building

reference line and/ or point at

the same level  		± 10 mm.

-	Straightness in any 5 m length  		± 5 mm.

-	Verticality up to 3 m height  		± 10 mm.

-	Verticality up to 7 m height  		± 14 mm.

-	Overall thickness of walls  		± 10 mm.

-	Level of bed joints up to 5 m

(brick masonry)  		± 11 mm.

-	Level of bed joints up to 5 m

± 13 mm.

560	COURSING BRICKWORK

•	 Gauge: Four brick courses including bed joints to 300 mm.

595	LINTELS

•	 Bearing: Ensure full length masonry units occur immediately under lintel ends.

610	SUPPORT OF EXISTING WORK

•	 Joint above inserted lintel or masonry: Fully consolidated with semidry mortar to support

existing structure.

635	JOINTING

•	 Profile: Consistent in appearance.

645	ACCESSIBLE JOINTS NOT EXPOSED TO VIEW

•	 Jointing: Struck flush as work proceeds.

665	POINTINGTO ALL WALLING

•	 Joint preparation: Remove debris. Dampen surface.

•	 Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: 1:1:6 cement:lime:sand.

-	Additional requirements: None.

•	 Profile: Approved.

671	FIRE STOPPING

•	 Avoidance of fire and smoked penetration: Fit tightly between cavity barriers and masonry.

Leave no gaps.

690	ADVERSE WEATHER

•	 General: Do not use frozen materials or lay on frozen surfaces.

•	 Air temperature requirements: Do not lay bricks/ blocks:

-	In cement gauged mortars when at or below 3°C and falling or unless it is at least 1°C

and rising.

-	In hydraulic lime:sand mortars when at or below 5°C and falling or below 3°C and rising.

-	In thin joint mortar glue when outside the limits set by the mortar manufacturer.

•	 Temperature of walling during curing: Above freezing until hardened.

•	 Newly erected walling: Protect at all times from:

-	Rain and snow.

-	Drying out too rapidly in hot conditions and in drying winds.

ADDITIONAL REQUIREMENTS FOR FACEWORK

710	THE TERM FACEWORK

•	 Definition: Applicable in this specification to brick/ block walling finished fair.

-	Painted facework: The only requirement to be waived is that relating to colour.

730	BRICK/ CONCRETE BLOCK SAMPLES

•	 General: Before placing orders with suppliers submit for approval of appearance labelled

samples of the following: Minimum 3no types of brickwork for Client and CA approval .

•	 Selection of samples: Representative of the range in variation of appearance.

740	FINISHED MASONRY WORK REFERENCE PANELS

•	 General: Before proceeding to construct the following walling types, construct panels as

specified. Give notice when panels are dry.

•	 Selection of masonry units: Reasonably representative of the average quality of the whole

order to be delivered .

•	 Panel types:

-	Walling type: All external brickwork .

Location: On site .

Size: 1.0 x 1.0 m .

Other requirements: None .

745	MASONRY SAMPLE PANELS

•	 Sampling frequency: A panel for each type and delivery of masonry unit.

•	 Selection of masonry units: Reasonably representative of the average quality of the whole

order to be delivered .

•	 Panel types: As clause 740.

750	COLOUR CONSISTENCY OF MASONRY UNITS

•	 Colour range: Submit proposals of methods taken to ensure that units are of consistent

and even appearance within deliveries.

•	 Conformity: Check each delivery for consistency of appearance with previous deliveries

and with approved reference panels; do not use if variation is excessive.

•	 Finished work: Free from patches, horizontal stripes and racking back marks.

760	APPEARANCE

•	 Brick/ block selection: Do not use units with damaged faces or arrises.

•	 Cut masonry units: Where cut faces or edges are exposed cut with table masonry saw.

•	 Quality control: Lay masonry units to match relevant reference panels.

-	Setting out: To produce satisfactory junctions and joints with built-in elements and

components.

-	Coursing: Evenly spaced using gauge rods.

•	 Lifts: Complete in one operation.

•	 Methods of protecting facework: Submit proposals.

780	GROUND LEVEL

•	 Commencement of facework: Not less than 150 mm below finished level of adjoining

ground or external works level.

790	PUTLOG SCAFFOLDING

•	 Use: Not permitted in facework.

800A	TOOTHED BOND

-  	Toothed bond not allowed without prior approval. New and existing face-work in

same plane: Bond together at every course to achieve continuity.

830	CLEANLINESS

•	 Facework: Keep clean.

•	 Mortar on facework: Allow to dry before removing with stiff bristled brush.

•	 Removal of marks and stains: Rubbing not permitted.

F30

Accessories/ sundry items for brick/ block/ stone walling

F30 Accessories/ sundry items for brick/ block/ stone walling

To be read with Preliminaries/ General conditions.

CAVITIES

110	CONCRETE FILL TO BASE OF CAVITY

•	 Concrete generally: To BS EN 206-1 and BS 8500-2.

-	Designated concrete: GEN 1 .

Workability: High.

•	 Extent: Maintain 75 mm between top of fill and external ground level and a minimum of 225

mm between top of fill and ground level dpc.

•	 Placement: Compact to eliminate voids.

120	CLEANLINESS

•	 Cavity base and faces, ties, insulation and exposed dpcs: Free from mortar and debris.

132A	PERPEND JOINT PLASTICS WEEP HOLES

•	 Manufacturer: Contractor's choice .

-	Proprietary plastic perpend weep hole to suit mortar joint. BBA approved and securely

fixed.

•	 Locations: Through outer leaf immediately above base of cavity, at cavity trays, stepped

dpcs and external openings. 75 mm above top of cavity fill at base of cavity.

•	 Provision: At not greater than 1000 mm centres and not less than two over each opening.

140A	WALL CAVITY THERMAL FOIL BREATHER MEMBRANE TO OUTER FACE OF

CONTRACTORS DESIGNED TIMBER FRAME

•	 Type:  [Proprietary BBA approved breather membrane with non-woven polypropylene

core and high purity aluminium foil layer with a thermal resistance of 0.77W/m2K and a

vapour resistance of 0.55MNs/g].

•	 Manufacturer:  [Contractors choice, provide sample for CA approval].

-	Fitting:  [In accordance with TRADA recommendations for timber frame construction.

Aluminium foil facing to airspace to create low emissivity air gap. To be fully lapped and

sealed to dpcs and cavity trays with proprietary compatible tape all in accordance with

manufacturers instructions].

155B	INSULATION TO BETWEEN STUDS OF TIMBER FRAMED EXTERNAL  WALLS TO

DWELLINGS

•	 Insulation: High performance rigid thermoset polyisocyanurate (PIR) insulant manufactured

with a blowing agent that has zero Ozone Depletion Potential (ODP) and Global Warming

Potential (GWP) of less than 5 in accordance with the requirements of BS 4841-1. .

-	Standard: BS EN 13165.

-	Product certification: To be BBA and IAB certified for this application. BS EN ISO 9001:

2000/IS EN ISO9001:2008.  To be installed in accordance with the manufacturer's

instructions.

•	 Manufacturer: Contractor's choice, sample to be provided for CA approval.

Face size (length x width): 1200 x 450 mm.

•	 Thickness (nominal): 90 mm.

•	 Thermal conductivity: Aged - 0.022 W/mK.

•	 Reaction to fire class: Class 1 fire rating on both core and facings, producing less than 5%

smoke obscuration when tested to BS 5111-1:1974 low risk.

•	 Additional requirements:   	To be highly resistant to transmission of water vapour (more

than 100MN.s/g) and air movement in accordance with BS EN 12086.  Compressive

strength typically in excess of 125 kPa at 10% compression when tested to BS EN 826: 1996

(Thermal insulating products for building applications. Determination of compression

behaviour) .

•	 Placement: Secure with no gaps between studs of external timber frame walls.

Joints between boards, at closures and penetrations: No gaps and free from debris.

155C	INSULATION TO INTERNAL FACE OF STUDS OF TIMBER FRAMED EXTERNAL

WALLS TO DWELLINGS

•	 Insulation: High performance rigid thermoset polyisocyanurate (PIR) insulant faced on both

sides with a proprietary low emissivity composite foil facing.  To be manufactured with a

blowing agent that has zero Ozone Depletion Potential (ODP) and Global Warming

Potential (GWP) of less than 5 in accordance with the requirements of BS 4841-1. .

-	Standard: BS EN 13165.

-	Product certification: To be BBA and IAB certified for this application. BS EN ISO 9001:

2000/IS EN ISO9001:2008.  To be installed in accordance with the manufacturer's

instructions.

•	 Manufacturer: Contractor's choice, sample to be provided for CA approval.

Face size (length x width): 1200 x 450mm, 1200 x 600mm.

•	 Thickness (nominal): 25 mm.

•	 Thermal conductivity: Aged - 0.022 W/mK.

•	 Reaction to fire class: Class 1 fire rating on both core and facings, producing less than 5%

smoke obscuration when tested to BS 5111-1:1974 low risk.

•	 Additional requirements:   	To be highly resistant to transmission of water vapour (more

than 100MN.s/g) and air movement in accordance with BS EN 12086.  Compressive

strength typically in excess of 125 kPa at 10% compression when tested to BS EN 826: 1996

(Thermal insulating products for building applications. Determination of compression

behaviour).  Joints to be taped with suitable proprietary compatible low emissivity foil faced

tape .

•	 Placement: Secure with no gaps between studs of external timber frame walls.

Joints between boards, at closures and penetrations: No gaps and free from debris.

156A	VAPOUR CONTROL LAYER TO BE SANDWICHED BETWEEN WALL INSULATIONS

•	 Specification clause: Proprietary Low emissivity air barrier And Vapour control layer to be of

triple ply construction with polywoven core and solid corrosion resistant aluminium layer

Layer to have a water vapour resistance in excess of 250 MNs/g Vapour control layer to be

fitted into wall/ceiling/ in accordance with BS 5250: 2002 and manufacturers instructions.

Only tapes approved by the manufacturer to be used.

•	 Type:  [Proprietary BBA approved 500 gauge / 125micron polythene vapour barrier ].

•	 Manufacturer:  [Contractors choice, provide sample for CA approval].

•	 -  Fitting:  [In accordance with BS5250 & BS9250.  To be fully lapped and sealed with

proprietary compatible tape in accordance with manufacturers instructions].

•	 Vapour resistance:  [min. 589 MNs/g].

160	AIR BRICKS IN EXTERNAL WALLING

•	 Standard: To BS 493, class 1.

•	 Manufacturer: To be chosen by contractor and approved by architect .

-	Product reference: To be chosen by contractor and approved by architect .

•	 Apertures: Rectangular hole .

•	 Work sizes:  To suit 215 x 65 mm brickwork module or specified brick .

•	 Material/ Colour: Proprietary upvc. To match adjoining masonry. Sample to be approved by

architect .

•	 Placement: Built in with no gaps at joints.

165A	GRATINGS/ VENTILATORS IN INTERNAL WALLING

•	 Standard: To BS 493, class 2.

•	 Manufacturer: As per Mechanical & Electrical consultants' specification .

•	 Other requirements: Sample to be approved by architect .

•	 Placement: Built in with no gaps at joints.

171	VENTILATION DUCTS IN EXTERNAL WALLING

•	 Manufacturer: See separate mechanical/electrical specification .

-	Product reference: - .

•	 Placement: Across cavity, sloping away from inner leaf. Full mortar joints to seal cavity.

•	 Protection from water penetration to inner leaf: Where barrier is not integral to duct, form

stepped dpc cavity tray with stop ends above duct, extending 150 mm on each side.

172A	VENTILATION DUCTS IN EXTERNAL WALLING Periscope type vent ducts to ventilate

sub-floor void.

•	 Manufacturer: Contractors choice, provide sample for CA approval .

-	Product reference: Proprietary third party accredited extending / adjustable cavity vent

suitable for timber frame construction.  Vent to be 'periscope' type extending vent where

necessary to suit floor and external ground levels.  Provide compatible proprietary

airbrick to standard brick face dimensions. .

•	 Placement: Minimum 2m centres on opposite sides of building to provide cross ventilation -

ventilation must ensure a minimum of 3000m2/m of cross ventilation throughout the

subfloor. Full mortar joints to seal cavity.

•	 Protection from water penetration to inner leaf: Where barrier is not integral to duct, form

stepped dpc cavity tray with stop ends above duct, extending 150 mm on each side. Air

brick to be driving rain resistant.

•	 Accessories: Proprietary compatible air brick with minimum ventilation area of 6000mm2

and periscope vertical sleeve as necessary.

173A	VENTILATION DUCTS IN EXTERNAL WALLING Periscope type vent ducts to ventilate

sub-structure voids.

•	 Manufacturer: Contractors choice, provide sample for CA approval .

-	Product reference: Proprietary third party accredited extending / adjustable cavity vent

suitable for timber frame construction.  Vent to be 'periscope' type extending vent where

necessary to suit floor and external ground levels.  Provide compatible proprietary

airbrick  to standard brick face dimensions. .

•	 Placement: Minimum 1.5m centres at lower and high levels to provide adequate cross

ventilation - ventilation must ensure a minimum of 3000m2/m of ventilation throughout the

sub-structure void. Full mortar joints to seal cavity.

•	 Protection from water penetration to inner leaf: Where barrier is not integral to duct, form

stepped dpc cavity tray with stop ends above duct, extending 150 mm on each side. Air

brick to be driving rain resistant.

•	 Accessories: Proprietary compatible air brick with minimum ventilation area of 6000mm2

and periscope vertical sleeves as necessary.

175	CAVITY VENTILATORS

•	 Manufacturer: Contractors choice, provide sample for CA approval .

-	Product reference: Proprietary BBA approved .

•	 Material/ colour: Plastics/ to match adjoining masonry .

•	 Number and location: 1500mm centres, top & bottom of enclosed cavity sections .

185A	PARTY WALL CAVITY CLOSER / SEALER TO PARTY WALL CAVITY VERTICALLY

AND AT TOP OF WALL BELOW ROOF

•	 Manufacturer: Contractor's choice - provide sample for CA approval .

-	Product : Compatible system of proprietary composite end cap sealer and cavity barrier

with enhanced acoustic, thermal and fire resistance properties to meet requirements of

NI Technical Booklet F1 (for party wall u-value of 0.0W/mwK filled cavity condition) &

Technical Booklet G October 2012.

Proprietary composite end cap sealer to comprise of a fire rated mineral wool bat to fill

party cavity with bitumen composite membrane and acoustically rated fillers lapped to

party wall leafs to seal cavity.

Proprietary composite party wall cavity barrier to have factory bonded DPC and have

enhanced acoustic and fire resistance properties.  To be compatible with end cap sealer

product / installation.  Cavity barrier to have minimum 50mm overlap with party wall leafs

.

•	 Accessories: Use galvanised steel staples to install end cap sealer in accordance with

manufacturer's instructions to timber framed party walls.  Structural grade galvanised steel

wall cap clips to be installed in accordance with manufacturer's instructions to masonry

party walls .

•	 Fire Resistance: min 60 minutes.

Additional requirements: To be manufactured with a blowing agent that has zero Ozone

Depletion Potential (ODP) and Global Warming Potential (GWP) of less than 5 in

accordance with the requirements of BS 4841-1..

REINFORCING/ FIXING ACCESSORIES

200	VERTICAL CAVITY BARRIERSALL (EXCEPT AT PARTY WALLS)

-  	Manufacturer: Contractor's choice - provide sample for CA approval.

-  	Product : Proprietary polythene sleeved mineral fibre cavity barrier complete with

integral polythene fixing flanges to achieve 30minutes fire resistance. Size to suit cavity

thickness to perform as specified taking into account any differential movement in the

cavity.

-  	Other requirements : To be LPCB third party approved for performance and quality.

Insulant to have zero Ozone Depletion Potential (0DP) and a Global Warming Potential

(GWP) of less than 5.

-  	Fixing: Both fixing flanges to be secured back to inner leaf at minimum 150mm

centres using proprietary clout nails or electro galvanised staples all in accordance with

manufacturer's instructions.

205	VERTICAL CAVITY BARRIERS IN CAVITY AT PARTY WALL JUNCTION

-  	Manufacturer: Contractor's choice - provide sample for CA approval.

-  	Product : Proprietary white glass tissue faced semi-rigid mineral fibre insulation

bonded to a polythene dpc with 40mm laps on each side  to achieve 60minutes fire

resistance and have acoustic properties to reduce flanking sound. Size to suit cavity

thickness to perform as specified taking into account any differential movement in the

cavity.

-  	Other requirements : To be third party approved for performance and quality. To

have zero Ozone Depletion Potential (0DP) and a Global Warming Potential (GWP) of less

than 5.

-  	Fixing:  In accordance with manufacturer's instructions and good practices for

detailing of dpcs as per BS EN 5628 Part3, BS8215, BS 8000 Part3.  To be built in as

masonry proceeds with dpc facing against outer masonry leaf.

206	HORIZONTAL CAVITY BARRIERS

-  	Manufacturer: Contractor's choice - provide sample for CA approval.

-  	Product : Proprietary polythene sleeved mineral fibre cavity barrier complete with

integral polythene fixing flanges to achieve 30minutes fire resistance. Size to suit cavity

thickness to perform as specified taking into account any differential movement in the

cavity.

-  	Other requirements : To be LPCB third party approved for performance and quality.

Insulant to have zero Ozone Depletion Potential (0DP) and a Global Warming Potential

(GWP) of less than 5.

-  	Fixing: Both fixing flanges to be secured back to inner leaf at minimum 150mm

centres using proprietary clout nails or electro galvanised staples all in accordance with

manufacturer's instructions. Breather membrane of timber frame to be cut to overlap the top

flange of the cavity barrier.

236A	WALL TIES IN MASONRY CLADDING TO TIMBER FRAMES

Standard: To BS 5268-6.1 1996

Manufacturer:  Contractor's choice, provide sample for CA approval.

-	Product : Type 6 cranked wall tie suitable for timber frame construction.

Material/ finish:  Austenitic Stainless Steel.

Sizes:  To suit 50mm cavity.

Additional requirements: Ties to be fixed back to timber studs of timber frame as in

accordance with manufacturer's instructions.

•	 Fixing ties to timber frame: Securely with 50 mm x 11 gauge stainless steel annular ringed

shank nails or stainless steel 4x30mm proprietary screw in accordance with

manufacturer's instructions.

•	 Embedment in mortar beds (minimum): 50 mm.

•	 Placement: Slope downwards away from timber frame, without bending.

•	 Spacing:

-	Horizontal centres: To suit stud centres (max 900crs).

-	Vertical centres: 450mm . Minimum of 2.5 ties per 1 sq.m of wall.

•	 Provision of additional ties: Within 225 mm of reveals of openings and at no more than 300

mm centres vertically.

281A	LATERAL RESTRAINT SLIP TIES FOR MOVEMENT JOINTSIN EXTERNAL LEAF

•	 Standards: To BS EN 1996-1-1, BS EN 845-1

Manufacturer:  Contractor's choice, provide sample for CA approval.

-	Product : Proprietary 225mm lateral restraint tie with integral debonding sleeve to allow

expansion & contraction at vertical movement joints in masonry.

Material/ finish: Austenitic stainless steel: grade 1.4301 (304), with sleeve to one half .

•	 Fixing centres: 450mm centres.

-  	Fixing: In accordance with manufacturer's instructions.

FLEXIBLE DAMP PROOF COURSES/ CAVITY TRAYS

330A	DAMP PROOF COURSE -IN EXTERNAL LEAF

•	 Manufacturer: Contractor's choice, provide sample for CA approval .

-	Product : Proprietary BBA approved Co-Polymer Thermoplastic DPC tested to BS DD86

Part1.

-	Nominal width : 102.5mm/116mm, to suit complete width of masonry leaf in either

facing brick or blockwork & render.

-	Nominal thickness : 0.8mm

-	Tensile strength : min 20.5N/mm2

-	Tear strength : min 175N/mm2

-	Water vapour permeability : max 0.21g/m2/day  .

-  	Fixing:  In accordance with manufacturer's instructions and good practices for

detailing of dpcs as per BS EN 5628 Part3, BS8215, BS 8000 Part3.  To be built in as

masonry proceeds min 150mm above ground level, step dpc as necessary. Joints and

laps to be minimum 100mm and be fully bonded with compatible proprietary jointing

tape.

370A	PREFORMED CAVITY TRAYS ALL HORIZONTAL

•	 Manufacturer:  [Contractor's choice, provide sample for CA approval] .

-	Product :  [Proprietary BBA approved solid polyethylene dpc cavity tray tested to BS DD86

Part1 with cavity upstand.

-	Nominal width : 50mm, to suit cavity width.

-	Tensile strength : min 20.5N/mm2

-	Tear strength : min 175N/mm2

-	Water vapour permeability : max 0.21g/m2/day] .

-  	Fixing:  In accordance with manufacturer's instructions and good practices for

detailing of dpcs as per BS EN 5628 Part3, BS8215, BS 8000 Part3.  To be built in as

masonry proceeds and to be lapped with timber frame breather membrane and fully

bonded with compatible proprietary jointing tape. Provide stop ends as per 380A.

375A	PREFORMED ABUTMENT CAVITY TRAYS

•	 Manufacturer:  [Contractor's choice, provide sample for CA approval] .

-	Product :  [Proprietary BBA approved solid pethylene dpc abutment cavity tray with

cavity upstand and integral ready shaped lead flashing.

-	Nominal width : 50mm, to suit cavity width.

-	Tensile strength : min 20.5N/mm2

-	Tear strength : min 175N/mm2

-	Water vapour permeability : max 0.21g/m2/day] .

-  	Fixing:  In accordance with manufacturer's instructions and good practices for

detailing of dpcs as per BS EN 5628 Part3, BS8215, BS 8000 Part3.  To be built in as

masonry proceeds and to be lapped with timber frame breather membrane and fully

bonded with compatible proprietary jointing tape.

380A	PREFORMED DPC/ CAVITY TRAY JUNCTION CLOAKS/ STOP ENDS

•	 Manufacturer:  [Contractor's choice, provide sample for CA approval] .

-	Product :  [Proprietary BBA approved solid pethylene dpc cavity tray stop end.

-	Nominal width : 50mm, to suit cavity width.

-	Tensile strength : min 20.5N/mm2

-	Tear strength : min 175N/mm2

-	Water vapour permeability : max 0.21g/m2/day] .

-  	Fixing:  In accordance with manufacturer's instructions and good practices for

detailing of dpcs as per BS EN 5628 Part3, BS8215, BS 8000 Part3.  To be built in as

masonry proceeds and to be lapped with timber frame breather membrane and fully

bonded with compatible proprietary jointing tape.

INSTALLATION OF DPCS/ CAVITY TRAYS

415A	HORIZONTAL DPCS

•	 Placement: In continuous lengths on full even bed of fresh mortar, with 200 mm laps at

joints and full laps at angles.

•	 Width: At least full width of leaf unless otherwise specified. Edges of dpc not covered with

mortar or projecting into cavity.

•	 Overlying construction: Immediately cover with full even bed of mortar to receive next

masonry course.

•	 Overall finished joint thickness: As close to normal as practicable.

425A	GROUND LEVEL DPCS

•	 Joint with damp proof membrane: Continuous and effectively sealed in accordance with

manufacturers recommendations.

435	STEPPED DPCS IN EXTERNAL WALLS

•	 External walls on sloping ground: Install dpcs not less than 150 mm above adjoining

finished ground level.

445A	SILL DPCS

•	 Form and placement: Provide proprietary cavity tray as 370A and proprietary stop ends as

380A.

455	COPING/ CAPPING DPCS

•	 Placement: Bed in one operation to ensure maximum bond between masonry units, mortar

and dpc.

•	 Dpcs crossing cavity: Provide rigid support to prevent sagging.

465	SEALING DPCSGENERALLY

•	 Overlaps and junctions: Seal with Lap 200mm and seal with adhesive recommended by

dpc manufacturer .

485A	CAVITY TRAYS OVER OPENINGS AND OTHER CAVITY BRIDGINGS

•	  Length: To extend not less than 200 mm beyond ends of lintels/ bridging’s.

515	DPC/ CAVITY TRAY LEADING EDGE IN FACEWORK - FLUSH

•	Treatment at face of masonry: Finish flush and clear of mortar at the following locations: External wall dpc 150mm above ground level .

560	VERTICAL DPCS GENERALLY

•	 Form: In one piece wherever possible.

-	Joints: Upper part overlapping lower not less than 100 mm.

570	JAMB DPCS AT OPENINGS

•	 Joint with cavity tray/ lintel at head: Full underlap.

•	 Joint with sill/ horizontal dpc at base: Full overlap.

•	 Projection into cavity: Not less than 25 mm.

•	 Relationship with frame: In full contact.

JOINTS

610A	MOVEMENT JOINTS WITH SEALANT TO EXTERNAL MASONRY LEAF

•	 Joint preparation and sealant application: As section Z22.

•	 Filler: Closed cell polyethylene foam .

-	Thickness: To match design width of joint.

-	Manufacturer: Contractor's choice, provide sample for CA approval .

-	Product : Low density, compressible, closed cell polythene filler suitable for structural

expansion joints and building facades in accordance with BS 5628:Part3

-	Density : 35kg/m3

-	Water absorb ion after 6 weeks immersion : 3% by volume

-	Compressive strength at 50% strain : 115kN/m2

-	Recovery after load - min 95%  .

-	Placement: Build in as work proceeds with no projections into cavities and to correct

depth to receive sealant system.

•	 Sealant:

-	Designation: Proprietary cold applied gun grade polysulphide sealant  .

-	Manufacturer: Contractor's choice, provide sample for CA approval  .

-	Product reference: Proprietary cold applied gun grade waterproof flexible polysulphide

sealant to BS EN ISO 11600:2003  .

-	Colour: To match mortar of facing brickwork OR colour to match proprietary render finish

depending on finish, to be approved by CA  .

650	POINTING IN FLASHINGS

•	 Joint preparation: Free of debris and lightly wetted.

•	 Pointing mortar: As for adjacent walling.

•	 Placement: Fill joint and finish flush.

660	PINNING UP TO SOFFITS

•	 Top joint of loadbearing walls: Fill and consolidate with mortar.

PROPRIETARY SILLS/ LINTELS/ COPINGS/ DRESSINGS

720A	SILLS

•	 Standard: To BS 5642-1.

•	 Material: Precast concrete .

•	 Manufacturer: Contractor's choice, provide sample for CA approval .

Dimensions: Generally 2 course 140mm high with minimum 50mm

sill projection from finished face of wall. Sill to extend beyond each side of window opening

by 102.5mm unless otherwise indicated. In facing brickwork sills to be stooled.  Sills with

steel reinforcement as necessary .

•	 Finish: Steel shuttered smooth finish .

•	 Mortar for bedding/ jointing: Cement gauged as section Z21.

-	Standard: To BS EN 998-2 .

-	Mix: as wall .

-	Additional requirements: None .

•	 Joints: Bucket handle.

•	 Bedding one piece sills: Leave bed joints open except under end bearings and masonry

mullions. On completion, point to match adjacent work.

755A	PREFABRICATED STEEL LINTELS MUST BE USED WITH ALL WALL OPENINGS

•	 Standard: To BS EN 845-2.

•	 Manufacturer: Contractor's choice, provide sample for CA approval .

-	Product : BBA approved to suit span, loading, wall and finish types .

•	 Types: Suitable for timber frame, installed in accordance with manufacturers instructions .

•	 Material/ finish: Z1 grade galvanised steel to BS 2989: 1982 (BS EN 10327: 2004) with a

zinc coating type G600 (H3) giving a minimum zinc coating of 600g/m2 (including both

sides).  .

•	 Sizes: To suit span, loading, wall and finish types .

•	 Additional requirements: Proprietary galvanised and powder coated insulated to suit

opening and leaf sizes. Bed on mortar used for adjacent work .

•	 Bearing length (minimum): 150 mm .

760A	COPING UNITS

•	 Standard: To BS 5642-2.

•	 Material: Precast concrete .

•	 Manufacturer: Contractor's choice, provide sample for CA approval .

Dimensions: As required or as shown on drawings.

•	 Finish: Steel shuttered smooth finish .

•	 Mortar for bedding/ jointing: Cement gauged as section Z21.

-	Standard: To BS EN 998-2 .

-	Mix: 1:3 masonry cement:sand (mortar class 6) .

-	Additional requirements: To match adjoining masonry .

•	 Joints: Full and finished flush.

•	 Placement: Lay on a full bed of mortar to line and level.

MISCELLANEOUS ITEMS

830	BUILDING IN FRAMES

•	 Preparation: Remove horns and provide support.

•	 Fixing cramps: Fully bed in mortar.

840	OPENINGS FOR FRAMES

•	 Formation: Use accurate, rigid templates to required size.

850A	WALL PLATES

•	 Integral with timber framing element.

F31

Precast concrete sills/ lintels/ copings/ features

F31 Precast concrete sills/ lintels/ copings/ features

To be read with Preliminaries/ General conditions.

TYPES OF COMPONENT

112	 DESIGNATED CONCRETE PRECAST GENERALLY

•	 Concrete: Designated to BS 8500-2: Submit proposals .

•	 Reinforcement type/ strength grade: Contractor's choice - stainless steel .

-	Cover to reinforcement (nominal): Minimum cover 30mm plus 15mm fixing tolerance .

•	 Aggregates:

-	Size (maximum): 15mm .

-	Coarse recycled aggregate: RCA permitted .

•	 Matching sample for finish to visible faces: As agreed .

•	 Other requirements: None .

125	SUBSTITUTION OF PROPRIETARY CONCRETE FOR DESIGNATED CONCRETE

•	 Concrete: Component manufacturer's 'proprietary' concrete.

•	 Substitution: Submit proposals for each substitution, including:

-	Identity of concrete: Submit labelled sample .

-	Performance: Limiting values for w/c ratio, cement/ combination content or, alternatively

the Exposure class to BS 8500, to which concrete conforms.

-	Reinforcement: Type and cover.

-	Evidence of performance: Third party certification by body

from a UKAS accredited laboratory.

130	CONCEALED PRECAST LINTELS

•	 Standard: To BS EN 845-2.

-	Verification of performance: Submit calculations or test certificates.

140A	CONCEALED PRECAST LINTELS

•	 Concrete: Designated to BS 8500-2: Minimum RC30.

-	Aggregate (maximum): size: 20 mm.

•	 Reinforcement provision for spans up to 1800 mm

Clear span  	Section  	Bearing  	Reinforcement

____________________________________________________________

Up to  	140 mm deep  	150 mm at  	One. 12 mm mild

900 mm  	x width 	of both ends  	steel bar for wall each 105 mm of

wall thickness.

____________________________________________________________

900 to  	215 mm deep  225 mm at  	One. 16 mm mild

1800 mm  	x width 	of both ends  	steel bar for wall each 105 mm of

wall thickness.

____________________________________________________________

•	 Cover to reinforcement (nominal): 20 mm minimum.

•	 LINTELS OVER 1800mm TO BE CONTRACTOR DESIGNED TO BE CAPABLE OF

SUPPORTING FULL WIDTH OF MASONRY LEAF ABOVE.

Performance: LINTELS TO BE DESIGNED TO BS6399:Part1 & BS8110:Part1 AND TO

THE REQUIREMENTS OF BUILDING REGULATIONS (NI).

150	CONCEALED PRECASTPADSTONES .

•	 Concrete: Designated to BS 8500-2: Minimum RC30.

-	Aggregate size (maximum): 20 mm.

•	 Other requirements: none .

GENERAL REQUIREMENTS

210A	MOULDS

•	 Constructed accurately to give straight, square and true components. Permissible

fabrication and operating tolerances: Length 0 to +6 mm, other dimensions ±3 mm.

-  	Maintained in clean, sound condition and inspected carefully for defects before

each reuse.

-  	Damaged moulds must not be repaired and reused if this would impair the surface

appearance of the components.

-  	Constructed to prevent loss of grout.

-  	Designed to permit de-moulding without damage to the components.

-  	Coated evenly with a suitable release agent, which must not be allowed to touch

the reinforcement.

Timber graining to the surface of exposed pre-cast concrete will not be acceptable.

220	CONCRETE GENERALLY

•	 Specification: To  BS 8500-2 and BS EN 206-1.

•	 Producer: Currently certified by a body accredited by UKAS to BS EN 45011 for product

conformity certification of ready-mixed concrete.

•	 Chloride class of concrete:

-	Excluding SRPC: C1 0.40.

-	Using SRPC: C1 0.20.

-	Reinforced and heat cured: C1 0.10.

-	Pre-stressed: C1 0.10.

•	 Admixtures containing calcium chloride: Not allowed.

250	REINFORCEMENT

•	 Carbon steel reinforcement: As appropriate to BS 4449, BS 4482 and BS 4483.

-	Cutting and bending: To BS 8666.

•	 Galvanized reinforcement: Galvanized to BS EN ISO 1461 after cutting. Chromate treated.

•	 Stainless steel reinforcement: To BS 6744.

-	Designation 1,4301.

-	Cutting and bending: To BS 8666.

•	 Non structural reinforcement: Include to resist shrinkage and handling stresses.

•	 Bimetallic corrosion and staining: Prevent by appropriate selection and use of materials.

•	 Condition at time of placement: Clean, free of corrosive pitting, loose materials and

substances that adversely affect reinforcement, concrete, or bond between the two.

•	 Fixing: Accurate and secure.

-	Method: Wire tying, approved steel clips or tack welding if permitted.

-	Concrete cover: Maintain free of all tying wire or clips.

255	QUALITY ASSURANCE OF REINFORCEMENT

Reinforcement to BS 4449, BS 4483, BS 6744: Obtain valid

certificates of approval for product conformity issued by the

UK Certification Authority for Reinforcing Steels.

260	CASTING AND CURING

•	 Placing of concrete: Thoroughly compact.

•	 Protection against drying out: Methods and duration to

BS EN 13369 clause 4.2.1.3.

•	 Immature components: Avoid movement, vibration, overloading, physical shock, rapid

cooling and thermal shock.

•	 Delivery to site: Not until at least 14 days after casting.

261	CUTTING

•	 Cutting of precast concrete components: Not permitted.

262	RECORDS

•	 Records for each type of component: Maintain details including:

-	Unique identification number.

-	Identification of the producer.

-	Identification of the place of production.

-	Correlation with records of mixes, including batch numbers.

-	Date of each stage of manufacture.

-	Dates and results of all tests, checks and inspections.

-	Dimensions related to specified levels of accuracy.

-	Specific location in the finished work.

-	Weight of the unit.

-	Damage and making good.

-	Any other pertinent data, e.g. if unit is a production control unit.

•	 Availability of records for inspection: On request.

FAIR FACED COMPONENTS

310	CONTROL SAMPLES

•	 Required samples: After finalization of design, one each of the following components:

Coping unit & sill.

•	 Approval of appearance: Obtain before manufacture of remaining units.

•	 Identification and storage location: Clearly label and retain at factory for comparison with

production units.

330	MIXES FOR VISIBLE FACED COMPONENTS

•	 Constituent materials and mix design for each finish type: To remain constant.

•	 Colour and appearance of each finish type: To remain constant.

•	 Aggregates: To BS EN 12620.

-	Origin: Single source for each finish type, having sufficient quantity for whole contract.

341	CONDITIONS FOR SEPARATE FACING AND BACKING MIXES

•	 Difference in cement content: Not greater than 80 kg/m³.

•	 Thickness of facing mix: 10 mm greater than maximum aggregate size, minimum 25 mm.

•	 Location of reinforcement: Minimum 20 mm away from the interface between mixes.

•	 Compaction of facing and backing mix: Carry out to create monolithic construction.

350	QUALITY OF FINISHES

•	 Appearance standard: As established by samples.

365	COVER ON EXPOSED AGGREGATE FACES

•	 Nominal cover: Exclusive of aggregate projection.

370	COVER ON VISIBLE FACES

•	 Spacers: Not permitted.

•	 Proposed method statement: Submit.

380	CONSISTENCY OF PRODUCTION METHODS

•	 Production methods: To remain consistent for each matching type of finish.

-	Finish appearance: To remain within the range of variation indicated by the samples

submitted.

•	 Changes to production methods: If variations are proposed for components of the same

finish, submit evidence that there will be no difference in appearance.

390	INSPECTION

•	 Completed components: Give notice when ready to be inspected at factory.

INSTALLATION

420	LAYING

•	 Mortar for bedding and jointing: As section Z21.

-	Mix: As used for adjacent work .

-	Packing: If required use slate.

•	 Bedding components: On full bed of mortar

•	 Removal of marks, stains and extraneous mortar on visible faces: Rubbing not permitted.

430	SUPPORT OF EXISTING WORK OVER NEW LINTELS

•	 Joint above lintels: Fully fill and compact with semidry mortar.

440	ONE PIECE SILLS/ THRESHOLDS

•	 Bed joints: Leave clear of mortar except at end bearings and beneath masonry mullions.

-	On completion: Point with mortar to match adjacent work.

G

Structural/Carcassing metal/timber

G12

Isolated structural metal members

G12 Isolated structural metal members

To be read with Preliminaries/ General conditions.

PRODUCTS

320A	STEEL GENERALLY

•	 Steel: To BS EN 10210-1 and To BS EN 10025-2.

-	Grade: S275JR internally, S275J0 externally.

-	Section properties and dimensions:

-  To BS 4-1 ;

-  To BS EN 10056 ; and

-  To BS EN 10210-2.

-	Surface condition: Free from heavy pitting and rust, burrs, sharp edges and flame cutting

dross.

350A	PROPRIETARY ANCHORS GENERALLY

•	 Manufacturer: Contractor's choice - provide sample for CA approval.

Anchor type: Bonded anchor .

•	 Material: Carbon steel

•	 Coating applied by manufacturer: Galvanized.

FABRICATION

510A	FABRICATION OF STEEL MEMBERS

•	 Cuts and holes: Accurate and neat.

•	 Welding: Metal arc method to BS EN 1011-2.

-	Welded joints: Fully fused, with mechanical properties not less than those of the parent

metal.

-	Site welding: Not permitted.

EXECUTION

610	INSTALLATION

•	 Accuracy: Members positioned true to line and level using, if necessary, steel packs of

sufficient area to allow full transfer of loads to bearing surfaces.

•	 Fixing: Use washers under bolt heads and nuts.

-	Tapered washers: Provide under bolt heads and nuts bearing on sloping surfaces. Match

taper to slope angle and align correctly.

620	BONDED ANCHORS

•	 Holes: Clean and free from dust at time of installing anchor.

•	 Permeable sleeves: Use in conditions where otherwise the loss of bonding agent would be

unacceptably high.

•	 Other requirements: 24 hours after installation, tighten anchors in masonry to installation

torque. Report movements..

630	SITE TESTING OF ANCHORS TO MASONRY

•	 Standard: To BS 5080.

•	 Preliminary tests: Not required.

•	 Proof tests: Test 10% of working fixings to 1.5 times working load.

•	 Test results: Report failures and seek instructions.

640	PREPARATION AND PRIMING

•	 Sequence of working: Fabricate, prepare, prime.

•	 Surfaces inaccessible after assembly: Apply full treatment and coating system including, if

necessary, local application of site coatings.

•	 Galvanized/ sherardized fasteners: After steelwork erection and before applying site

coatings, thoroughly degrease and clean. Etch prime.

650	SHOP PRIMINGGENERALLY

•	 Preparation: To BS EN ISO 12944-4. Remove fins, burrs, sharp edges and weld spatter

and clean out crevices.

-	Surface finish: Blast cleaned to BS EN ISO 8501-1, grade Sa 2½.

-	Prepared surfaces: Keep in a dry atmosphere and apply first coating without delay.

•	 Priming:

-	Primer: Solvent free epoxy.

Number of coats: Two.

Dry film thickness (minimum): 40 micrometres per coat.

-	Application: To BS EN ISO 12944-7.

•	 Other requirements: Confirm that proposed primer is suitable for use on hand cleaned steel

and Overcoat ends of beams built into solid external walls with high build bituminous paint.

Extend coating 150mm from face of wall onto exposed steelwork.

COMPLETION

910	STEEL TO TIMBER JOINTS

•	 General: Inspect accessible bolted and coach screwed joints and tighten fasteners if

necessary.

-	Timing: Immediately prior to installation of finishes, on Completion, and at end of Defects

Rectification or Liability Period.

-	Confirmation: Give notice when inspections and adjustments have been made.

G20

Carpentry/ timber framing/ first fixing

G20 Carpentry/ timber framing/ first fixing

To be read with Preliminaries/ General conditions.

GENERAL

105	TIMBER PROCUREMENT

•	 Timber (including timber for wood based products): Obtained from well managed forests/

plantations in accordance with:

-	The laws governing forest management in the producer country or countries.

-	International agreements such as the Convention on International Trade in Endangered

Species of wild fauna and flora (CITES).

•	 Documentation: Provide either:

-	Documentary evidence (which has been or can be independently verified) regarding the

provenance of all timber supplied, or

-	Evidence that suppliers have adopted and are implementing a formal environmental

purchasing policy for timber and wood based products.

110	SUSTAINABILITY

Contractor shall select timbers for carpentry and finished joinery, plywood and particle

boards with certification from the following schemes where appropriate. Certificate

evidence to be provided to CA.

CSA  	Canadian Standards Association

FSC  	Forest Stewardship Council Certification Scheme

MTCC  	Malaysian Timber Certification Scheme

PEFC  	Programme for the Endorsement of Forest Certification Programmes

SFI  	Sustainable Forestry Initiative

115	CONTRACTOR DESIGNED STRUCTURAL COMPONENTS

•	 Design standard: To BS 5268-2.

•	 Completion of design: Design and detail members and connections to satisfy loading

requirements specified or otherwise calculable from the information given.

•	 Design parameters: Dead and imposed loads for roof and floors & Basic wind speed and

wind factors to be accounted for in design.

•	 Drawings:

-	Content: Drawings must show:

Geometry of structure.

Wood species and grades/ strength classes.

Target/ Finished sizes of all timber sections.

Joints not detailed on Engineer's drawings, their locations, and evidence as to their

structural adequacy.

-	Submission: At least two weeks before commencing fabrication.

Copies: Digital.

•	 Compliance with design standard: Demonstrate by calculation or by prototype load testing

in accordance with BS 5268-2, Section 8.

150	STRENGTH GRADING OF TIMBER

•	 Grader: A company currently registered under a third party quality assurance scheme

operated by a certification body approved by the UK Timber Grading Committee.

160A	GRADING AND MARKING OF SOFTWOOD

•	 Timber of a target/ finished thickness less than 100 mm and not specified for wet exposure:

Graded at an average moisture content not exceeding 20% with no reading being in

excess of 24% and clearly marked as 'DRY' or 'KD' (kiln dried).

•	 Timber graded undried (green) and specified for installation at higher moisture contents:

Clearly marked as 'WET' or 'GRN'. WET or GRN timber must not be used without prior

approval.

•	 Structural timber members cut from large graded sections: Regraded to approval and

marked accordingly.

PRODUCTS

210	STRUCTURAL SOFTWOOD (GRADED DIRECT TO STRENGTH CLASS)FOR

STRUCTURAL USE GENERALLY

•	 Grading standard: To BS 4978, BS EN 519, BS EN 14081, or other national equivalent and

so marked.

•	 Strength class to BS EN 338: C24.  Contractor to design for a minimum design life of 60

years.

•	 Treatment: Organic solvent impregnation to NBS section Z12 and British Wood Preserving

and Damp-proofing  Association Commodity Specification C8, Service life: 40 years.

230A	GRADED SOFTWOOD (AS SPECIFIED BY ENGINEER).

-  	Strength graded to the appropriate standard or rules for the specified grade and so

marked.

Species and origin: From renewable sources

Grade: As specified by Structural Engineer

-  	Preservative treatment: As section Z12 and British Wood Preserving and Damp-

proofing Association Commodity Specification C8

-  	Moisture content at time of erection: As clause 450.

260A	STRUCTURAL HARDWOOD (STRENGTH CLASS NOT SPECIFIED).

-  	Strength graded to BS 5756 and so marked.

Species and origin: From renewable sources

Grade: As specified by Structural Engineer

Surface finish: Regularised

-  	Preservative treatment: As section Z12 and British Wood Preserving and Damp-

proofing Association Commodity Specification C8

-  	Moisture content at time of erection: As clause 450.

270A	UNGRADED SOFTWOODFOR NON STRUCTURAL USE

-  	Free from decay, insect attack (except pinhole borers) and with no knots wider than

half the width of the section.

-  	Surface finish: Regularised

-  	Preservative treatment: As section Z12 and British Wood Preserving and Damp-

proofing Association Commodity Specification C8

Moisture content at time of erection: As clause 450.

276	WROT TIMBER FOR SINGLE BOARDS FOR EXTERNAL EXPOSED JOINERY,

CANOPY BRACKETS AND THE LIKE.

-  	Quality of timber and fixing: To BS 1186:Part 3.

Species: From renewable sources

Moisture content at time of fixing: 13 to 19%.

-  	Preservative treatment: As section Z12 and British Wood Preserving and Damp-

proofing Association Commodity Specification C5.

-  	Other requirements: Undercut bottom edges of boards to form drip.  All corner

junctions mitred.  All joins of boards to be fully supported behind.

310	STRUCTURAL PLYWOODFOR GENERAL FRAMING/ CARCASSING

•	 Standard: To the relevant national standards and quality control procedures specified in BS

5268-2, and so marked.

•	 Type: Contractor's choice - provide sample for CA approval.

•	 Grade: Marine.

•	 Nominal thickness/ number of plies: 18mm.

•	 Finish: Sanded.

•	 Treatment: -.

311	NONSTRUCTURAL PLYWOODGENERALLY FOR DORMER CHEEKS, GUTTER

LININGS ETC

•	 Standard: To an approved national standard.

•	 Thickness: 19mm.

•	 Appearance class to BS EN 635: E.

•	 Bond quality to BS EN 314-2: Class 3.

•	 Finish: Sanded.

•	 Treatment: Marine grade treatment.

312	PLYWOOD FOR NON VISIBLE GENERAL USEGENERALLY

•	 Standard: To an approved national standard.

•	 Thickness: 18mm.

•	 Appearance class to BS EN 635: I.

•	 Bond quality to BS EN 314-2: Class 2.

•	 Finish: Unsanded.

•	 Treatment: As section Z12 and British Wood Preservation and Damp-proofing Association

Commodity Specification C8.

350	TRUSSED RAFTERS

•	 Design and fabrication: To BS 5268-3.

•	 Manufacturer: A firm currently registered under a third party quality assurance scheme.

•	 Truss system: Agrément certified. Contractor designed for a minimum design life of 60

years.

•	 Ancillary components to be supplied by the truss fabricator: Gable ladders & double

trusses as required.

•	 Treatment: Organic solvent type as section Z12 and BWPDA Commodity Specification C8.

WORKMANSHIP GENERALLY

401	CROSS SECTION DIMENSIONS OF STRUCTURAL SOFTWOOD AND HARDWOOD

•	 Dimensions: Dimensions in this specification and shown on drawings are target sizes as

defined in BS EN 336.

•	 Tolerances: The tolerance indicators (T1) and (T2) specify the maximum permitted

deviations from target sizes as stated in BS EN 336, clause 4.3:

-	Tolerance class 1 (T1) for sawn surfaces.

-	Tolerance class 2 (T2) for further processed surfaces.

402	CROSS SECTION DIMENSIONS OF NONSTRUCTURAL SOFTWOOD

•	 Dimensions: Dimensions in this specification and shown on drawings are finished sizes.

•	 Maximum permitted deviations from finished sizes: As stated in BS EN 1313-1:

-	Clause 6 for sawn sections.

Clause NA.2 for further processed sections.

403	CROSS SECTION DIMENSIONS OF NONSTRUCTURAL HARDWOOD

•	 Dimensions: Dimensions in this specification and shown on drawings are finished sizes.

•	 Maximum permitted deviations from finished sizes: As stated in BS EN 1313-2:

-	Clause 6 for sawn sections.

-	Clause NA.3 for further processed sections.

420	WARPING OF TIMBER

•	 Bow, spring, twist and cup: Not greater than the limits set down in BS 4978 or BS EN 519

for softwood, or BS 5756 for hardwood.

430A	SELECTION AND USE OF TIMBER

•	 Timber members damaged, crushed or split beyond the limits permitted by their grading:

Do not use.

•	 Notches and holes: Position in relation to knots or other defects such that the strength of

members will not be reduced.

•	 Scarf joints, finger joints and splice plates: Do not use without approval.

•	 Refer to Code for Sustainable Homes documentation with regards to sourcing of timber.

440	PROCESSING TREATED TIMBER

•	 Cutting and machining: Carry out as much as possible before treatment.

•	 Extensively processed timber: Retreat timber sawn lengthways, thicknesses, planed,

ploughed, etc.

•	 Surfaces exposed by minor cutting/ drilling: Treat with two flood coats of a solution

recommended by main treatment solution manufacturer.

450	MOISTURE CONTENT

•	 Moisture content of wood and wood based products at time of installation: Not more than:

-	Covered in generally unheated spaces:  	24%.

-	Covered in generally heated spaces:  	20%.

-	Internal in continuously heated spaces:  	20%.

451	MOISTURE CONTENT TESTING

•	 Procedure: When instructed, test timber sections with an approved electrical moisture

meter.

•	 Test sample: Test 5% but not less than 10 lengths of each cross-section in the centre of

the length.

•	 Test results: 90% of values obtained to be within the specified range. Provide records of all

tests.

480	TRUSSED RAFTER TESTING

•	 Standard: To BS EN 595.

•	 Number/timing of tests: Five at random during the contract.

•	 Purpose of testing: General quality control.

•	 Test reports: Submit as soon as available.

510	PROTECTION

•	 Generally: Keep timber dry and do not overstress, distort or disfigure sections or

components during transit, storage, lifting, erection or fixing.

•	 Timber and components: Store under cover, clear of the ground and with good ventilation.

Support on regularly spaced, level bearers on a dry, firm base. Open pile to ensure free

movement of air through the stack.

•	 Trussed rafters: Keep vertical during handling and storage.

520	EXPOSED END GRAIN

•	 Components: Seal exposed end grain of the following before delivery to site:

-.

•	 Sealer: Clear end grain sealer.

530	PAINTED FINISHES

•	 Structural timber to be painted: Primed as specified before delivery to site.

540	CLEAR FINISHES

•	 Structural timber to be clear finished: Keep clean and apply first coat of specified finish

before delivery to site.

550	EXPOSED TIMBER

•	 Planed structural timber exposed to view in completed work: Prevent damage to and

marking of surfaces and arrises.

JOINTING TIMBER

570	JOINTING/FIXING GENERALLY

•	 Generally: Where not specified precisely, select methods of jointing and fixing and types,

sizes and spacings of fasteners in compliance with section Z20.

590A	METAL PLATE FASTENERS/GUSSETS

•	 Manufacturer: Contractor's choice - provide sample for CA approval.

-	Product : Proprietary hot dip galvanised steel.

630	BOLTED JOINTS

•	 Bolt spacings (minimum): To BS 5268-2, table 81.

•	 Holes for bolts: Located accurately and drilled to diameters as close as practical to the

nominal bolt diameter and not more than 2 mm larger.

•	 Washers: Placed under bolt heads and nuts that would otherwise bear directly on timber.

Use spring washers in locations which will be hidden or inaccessible in the completed

building.

•	 Bolt tightening: So that washers just bite the surface of the timber. Ensure that at least one

complete thread protrudes from the nut.

-	Checking: At agreed regular intervals up to Completion. Tighten as necessary.

640	BOLTED JOINTS WITH CONNECTORS

•	 Connectors: To BS EN 912.

-	Types and sizes: As shown on drawings.

-	Bolt hole: Where appropriate, size to suit bolt diameter.

-	Manufacturer: Contractors choice.

-	Product reference: -.

-	Finish: Galvanized.

•	 Bolts and washers: To BS 5268-2.

•	 Connector location: Where not otherwise shown, spacings, end and edge distances to be

not less than Standard values to BS 5628-2, section 6.

•	 Centres of bolt holes: Not more than 2 mm from positions shown on drawings.

•	 Assembly: Do not crush timber, deform washers or overstress bolts.

670	ANTICORROSION FINISHES FOR FASTENERS

•	 Galvanizing: To BS 7371-6, with internal threads tapped and lightly oiled following

treatment.

•	 Sherardizing: To BS 7371-8, Class 1.

•	 Zinc plating: To BS EN ISO 4042 and passivated.

ERECTION AND INSTALLATION

710	PROPOSALS FOR ERECTING STRUCTURAL TIMBER

•	 Proposals: Submit details of:

-	Method and sequence of erection.

-	Type of cranage.

-	Temporary guys and bracing proposed for use during erection.

•	 Latest date for submission: 10 days before erection starts.

740	PRE-ERECTION CHECKING

•	 Timing: Not less than 10 days before proposed erection start date.

•	 Checklist:

-	Foundations and other structures to which timber structure will be attached: Check for

accuracy of setting out.

-	Holding down bolts: Check for position, protruding length, condition and slackness.

•	 Inaccuracies and defects: Report without delay.

•	 Erection: Obtain permission to commence.

750	MODIFICATIONS/REPAIRS

•	 Defects due to detailing or fabrication errors: Report without delay.

•	 Methods of rectification: Obtain approval of proposals before starting modification or

remedial work.

•	 Defective/damaged components: Timber members/ components may be rejected if the

nature and/or number of defects would result in an excessive amount of site repair.

760	TEMPORARY BRACING

•	 Provision: As necessary to maintain structural timber components in position and to ensure

complete stability during construction.

770	ADDITIONAL SUPPORTS

•	 Provision: Position and fix additional studs, noggings and/ or battens to support edges of

sheets materials, and wall/ floor/ ceiling mounted appliances, fixtures, etc. shown on

drawings

•	 Material properties: Additional studs, noggings and battens to be of adequate size and

have the same treatment, if any, as adjacent timber supports.

775	BEARINGS

•	 Timber surfaces which are to transmit loads: Finished to ensure close contact over the

whole of the designed bearing area.

•	 Packings: Where provided, to cover the whole of the designed bearing area.

-	Crushing strength: Not less than timber being supported.

-	In external locations: Rot and corrosion proof.

780	WALL PLATES

•	 Position and alignment: To give the correct span and level for trusses, joists, etc.

•	 Bedding: Fully in fresh mortar.

•	 Joints: At corners and elsewhere where joints are unavoidable use nailed half lap joints. Do

not use short lengths of timber.

784	JOISTS GENERALLY

•	 Centres: Equal, and not exceeding designed spacing.

•	 Bowed joists: Installed with positive camber.

•	 End joists: Positioned approximately 50 mm from masonry walls.

786	JOISTS ON HANGERS

•	 Hangers: Bedded directly on and hard against supporting construction. Do not use packs

or bed on mortar.

•	 Joists: Cut to leave not more than 6 mm gap between ends of joists and back of hanger.

Rebated to lie flush with underside of hangers.

•	 Fixing to hangers: A nail in every hole.

791A	PROPRIETARY JOIST HANGERS GENERALLY.

•	 Manufacturer: Contractor's choice, provide sample for approval.

-	Product : As per Contractor's Design as required and be fit for purpose intended.

•	 Material/ finish: Hot dip galvanized steel plate.

•	 Size: To suit joist, design load and crushing strength of supporting construction.

795	TRIMMING OPENINGS

•	 Trimmers and trimming joists: When not specified otherwise, not less than 25 mm wider

than general joists.

800A	TRUSSED RAFTER INSTALLATION

-  	Carefully inspect each truss before erection to ensure compliance with shop

drawings and specification, including:

Grades and sizes of members

Types, sizes and positions of nail plates

Gaps between ends of members at joints

Full penetration of nails.

-  	Erect trusses plumb, at equal centres not exceeding designed spacing and in

accordance with BS 5268:Part 3, clause 30 and Appendix B.

-  	Do not use damaged trusses and do not modify without approval.

-  	Fix securely with truss clips ensuring that rafters do not bear on wall plates.

-  	Do not fix ceiling chords to internal walls until roofing is complete and cisterns

installed and filled.

805A	TRUSS CLIPS

•	 Manufacturer:  [Contractor's choice, provide sample for approval].

-	Product :  [As per Contractor's Design as required and be fit for purpose intended].

•	 Material/ finish: Galvanized steel.

•	 Fasteners: Fix securely with 32 x 3.5 mm galvanized or sherardized square twisted nails in

every hole.

810A	PERMANENT BRACING OF TRUSSED RAFTERS

-  	Contractor Designed. Set out as shown Truss Manufacturer's design drawings

unless approved otherwise.

-  	Fix bracing and binders to every rafter, strut or tie with not less than two 75 x 3.35

mm galvanized round wire nails.

-  	Any lap joints must be side by side extending over and nailed to at least two truss

members.

Where a binder crosses a brace, interrupt and plate the binder.

820A	VERTICAL RESTRAINT STRAPS AT EAVES

-  	Material/finish: Galvanised steel.

Size: Not less than 30 x 2.5 mm cross section, min. 100 mm cranked end and min.

900 mm long.

-  	Centres: Position as Contractors Design, Structural Engineers recommendations or

at not more than 1000m centres.

-  	Fix straps securely to timber members with not less than two 30x 3.5 mm galv

square twist nails.

-  	Fix straps securely to masonry with not less than 5 No. 50 x 12 gauge sherardized

screws evenly spaced.

Locate at least one screw within 150 mm of the bottom end of each strap.

830A	LATERAL RESTRAINT STRAPS GENERALLY

-  	Material/finish: Galvanised steel.

Size: Not less than 30 x 5 mm cross section, min. 150 mm cranked end and min.

1200 mm long.

-  	Fix straps to top of joists/rafters/ties at not more than

300 m centres and as shown on drawings.

-  	Ensure that cranked end is in tight contact with cavity face of wall inner leaf and is

not pointing upwards.

-  	Fix noggings and packs beneath straps which span joists/rafters/ties running

parallel to wall. Noggings and packs to fit tightly, be not less than three quarters of

joist/rafter/tie depth and at least 38 mm thick. Notch joists so that straps fit flush with

surface. Do not notch rafters/ties.

-  	Fix straps to joists/rafters/ties with not less than four 50 mm x 8 gauge sherardized

countersunk screws, evenly spread.

840A	STRUTTING TO FLOOR JOISTS

-  	Contractor Designed.  Unless specified otherwise, securely fix strutting between

joists as follows:

Joist spans of 2.5 to 4.5 m: One row at centre span.

Joist spans over 4.5 m: Two rows equally spaced.

-  	Unless specified otherwise strutting to be one of the following:

Herringbone strutting, at least 38 x 38 mm softwood and located clear of top and

bottom edges.

Solid strutting, at least 38 mm thick softwood and at least three quarters of depth of

joist.

-  	Outer joists to be blocked solidly to perimeter walls.

850A	INSPECTION GENERALLY

•	 Structural timber-work: Give CA reasonable opportunity to inspect structural timberwork

before covering up.

860	BOLTED JOINTS INSPECTION

•	 Timing: Inspect all accessible bolts at the end of the Defects Liability Period and tighten if

necessary.

910A	EAVES SOFFIT VENTILATION

Manufacturer:  [Contractor's choice, provide sample for approval].

-  	Proprietary BBA approved over fascia ventilator pack with integral underlay

support/protection. Complete with gutter spacing brackets.

-  	Provide compatible proprietary rafter tray ventilation unit by same manufacturer.

-  	Airway: Provide the equivalent of a continuous opening of not less than 10

000mm2/m for full length of eaves.

950A	FASCIAS AND BARGE BOARDSPVC-U

Manufacturer:  [Contractor's choice, provide sample for approval].

Product : Proprietary BBA approved fascias & barge boards to be compatible with PVC-U

soffits..

•	 Material: Cellular PVC-U core with impact modified PVC-U skin and containing no lead or

cadmium.

•	 Finish: Smooth satin.

•	 Colour: Contractor to make allowance for provision of colour and effect options with

samples in white, grey, black, and oak timber effect (and other timber effect as requested)

for CA approval.  Client / CA's selected chosen colour / finish to have no financial or

programming implications to the contract - Contractor to provide samples in good timing to

facilitate proper consideration.

•	 Nominal depth: 150 mm / 175 mm / 200 mm / 225 mm, refer to drawings.

•	 Edge profile: Square.

•	 Accessories: Corner trims, joint trims and stop ends as necessary.

•	 Other requirements: Provide manufacturers warranty for min. 10 years.  Provide .

•	 Support: Refer to detailed drawings.  19mm external grade plywood backing board on 50 x

38 mm preservative treated softwood at same centres as rafters.

-	Provide additional support at joints.

•	 Fixings: Colour As recommended by manufacturer.  Colour caps over fixings to match

board colour.

955A	SOFFITSPVC-U

•	 Manufacturer:  [Contractor's choice, provide sample for approval].

Product :  [Proprietary BBA approved soffit boards to be compatible with PVC-U fascias /

barge boards.].

Material:  [Cellular PVC-U core with impact modified PVC-U skin and containing no lead or

cadmium].

Finish:  [Smooth satin].

Colour:  [Contractor to make allowance for provision of colour and effect options with

samples in white, grey, black, and oak timber effect (and other timber effect as requested)

for CA approval.  Client / CA's selected chosen colour / finish to have no financial or

programming implications to the contract - Contractor to provide samples in good timing to

facilitate proper consideration].

Nominal thickness:  [9mm].

•	 Accessories:  [Corner trims, joint trims and stop ends as necessary].

Other requirements:  [Provide manufacturers warranty for min. 10 years. Provide additional

10mm continuous compatible ventilator strip to soffit when any colour or finish other than

white is specified].

Support:  . 50 x 38 mm preservative treated softwood at same

centres as rafters. Support to be taken from trussed rafters to allow differential movement

between wall & roof.

-	Provide additional support at joints.

•	 Fixings:  [Colour As recommended by manufacturer.  Colour caps over fixings to match

board colour].

H

Cladding/Covering

H11

Curtain Walling

H11 Curtain Walling

To be read with Preliminaries/ General conditions.

TENDERING

10	INFORMATION TO BE PROVIDED WITH TENDER

•	 Submit the following curtain walling particulars:

-	Typical plan, section and elevation drawings at suitable scales.

-	Typical detailed drawings at large scales, including fixing details .

-	Technical information and certification demonstrating compliance with specification of

proposed incorporated products and finishes, including sample .

-	Certification, reports and calculations demonstrating compliance with specification of

proposed curtain walling.

-	Proposals for connections to and support from the building structure and building

components.

-	Proposals for amendments to primary supporting structure and for secondary supporting

structure additional to that shown on preliminary design drawings.

-	Schedule of builder's work, special provisions and special attendance by others.

-	Examples of standard documentation from which project quality plan will be prepared.

-	Preliminary fabrication and installation method statements and programme.

-	Schedule of products and finishes with a design life expectancy less than that specified

in clause 440, with proposals for frequencies and methods of replacement.

-	Proposals for replacing damaged or failed products.

-	Areas of non-compliance with the specification.

TYPES OF CURTAIN WALLING

115A	ALUMINIUM FRAMED CURTAIN WALLING

•	 All vertical glazed screens shall be manufactured from a single specialist supplier Curtain

Walling system manufacturer. The system shall be in a single colour finish, and be able to

contain glazed units and inserts as described in their appropriate specification. Curtain

Walling screens are to comply with the requirements of 'Secure by Design' and to have

been previously tested and ultimately manufactured to the standard required in BS7950

•	 Fabrication Partners:

A list of specific and approved fabrication partners for this installation can be made

available to the main contractor on request. The fabricator shall make provision for

producing construction drawings for approval prior to commencing works.

•	 Product Reference:

3rd party accredited thermally broken aluminium framed Curtain Walling - provide 3no

samples for acceptance.

•	 Material:

All profiles to be extruded from aluminium alloy 6060 T6, T5 or T4 complying with BS EN

12020-2; 2001 / BS 755-9; 2001.

•	 Finish:

The finish to all aluminium profiles shall generally be Polyester Powder Coated to BS EN

12206 in a RAL colour from the full colour range of satin, gloss and matt to satisfy a

corrosion classification as defined by the paint supplier, and to an average thickness of 60

microns. All powder coating shall be supported by a manufacturers/applicators guarantee

for a 25year guarantee finish. Project requirements must be clearly identified by the design

team responsible.

Colour: Choice from the full colour range of satin, gloss and matt finish RAL colours is to

be available to the Client. For building control purposes and meeting the LRV requirement,

the following colours have been considered pre-tender. Generally Ral 7015 (satin finish)

polyester powder coated (LRV of 9 points). Highlighted doors on elevations & schedules to

be Ral 7038 (satin finish) polyester powder coated (LRV of 43 points). Should colours not

be available at the time, the Client will choose an alternative from the full ranges.

It will be the responsibility of the glazing contractor to ensure that all profiles, panels,

flashings, and other necessary trims associated with his works that require powder coating

are processed in accordance with the corrosion classifications laid down in ISO 12944 – 2.

Polyester Powder Coating to have a 15 year guarantee.

•	 Performance:

The curtain walling system is to have a Weather Tightness test certificate to EN 13050 and

dynamically tested to CWCT Standard Test Method for Building Envelopes using a

representative two-storey sample.

Static Air Permeability - <1.5m³/hr. at 600 Pa

Static Water Penetration - Zero ml at 600 Pa

Dynamic Water penetration - Zero ml at 600 pa

Structural performance - 2400 Pa (140mph)

Safety Gust Performance - 3600 Pa (210mph)

The full test report details are to be made available upon request.

•	 Exposure:

Design Wind Pressure to be in accordance with BS 6399 - Part 2: 1997

•	 Thermal Performance:

All curtain walling screens, windows, doors and their respective inserts, in conjunction with

the appropriate glazing specification, shall be capable of meeting the current approved

Building Regulations for Northern Ireland. If more onerous, the U-values dictated in this

specification will take precedence as they are required for the SBEM calculations.

Details/evidence of all calculations/methods of determining the required project average U-

value for windows, screens and doors shall be submitted by the fabricator with all tender

submissions for approval. Further details illustrating actual U-values for each individual

window design, detailing the applicable frame, glazing and whole window U-values, and

the total average U-value for all the windows, demonstrating a compliant design, in

accordance with the methods stated within approved Building Regulations for Northern

Ireland, to be submitted to the Contract Administrator for approval.

•	 Air Tightness:

The air tightness of the screens must be installed in line with current legislation and CWCT

recommendations (Centre for Window and Cladding Technology, Bath University). All

screens are to have a continuous EPDM barrier fitted to the cill by the glazing contractor

(as per Metal Technology's standard details). All interface details are to be applied and

installed as per the specified details developed by the project Architect/Designer, and/or in

conjunction with the Accredited Details as published by Building Control NI.

•	 Air Permeability:

The maximum permissible air exfiltration rate through the curtain walling, windows, doors

and rooflights must not exceed 5 m3/(h.m2)@50Pa (or as required)

•	 Structure:

All profiles to be designed so as the maximum deflection of any member shall not exceed

L/200 of its span (L<3000mm) and not exceeding 5mm+L/300 of its span (3000<L>7500)

without any evidence of any permanent deformation once the load has been removed.

The relevant transoms and mullions are to be designed accordingly to act as structural

members. All sash vents shall be sized in accordance with the manufacturers

recommendations.

Windows that are less than 1100mm from the finished floor level  are to act as guarding

and are to withstand the horizontal line loads required by the Northern Ireland Building

Regulations 2012, for example at first floor level or where there is a drop in level of more

than 600mm.

The Contractor is responsible for the design and installation of any steel structure required

to support any aspect of the curtain walling. Details of extent, detail, location and impact on

the aesthetics of the curtain walling is to be forwarded to the CA prior to any ordering or

manufacture taking place.

•	 Construction:

All glazed screens shall be manufactured, installed and glazed in strict accordance with the

Systems Company's instructions and guidelines as set down in their technical literature,

details and specifications. The system shall be pressure equalised and self-draining by

means of overlapping the transoms onto the mullion members. Water is then channelled to

the exterior of the building via the integral drainage chambers within the mullions. Where

the transoms connect to the mullions the connection shall be sealed by means of a

purpose made transom end seal. The system shall be thermally broken throughout by

means of a continuous thermal isolator located between the thermally enhanced pressure

plates and all structural members. The thermally enhanced pressure plate shall be held in

place by bespoke aluminium stitch plates. The thermally enhanced pressure plate shall be

retained by using No.10 x 11/2 (5.5 x 38mm) posi-panhead stainless steel self-tapping

screw, tightened to a torque of 3.5Nm. It shall be the responsibility of the glazing

subcontractor to submit details/evidence of all structural calculations/methods of

determining the required profiles for windows, screens and doors on each project with all

tender submissions for approval.

•	 External Cover Caps:

Extruded aluminium cover cap applied horizontally and vertically. Details of cover cap to be

forwarded to the CA for acceptance prior to any ordering or manufacture taking place.

•	 Glazing System:

Dry glazed using proprietary, high performance captive gaskets. All triple-glazed units,

panels and inserts shall be supported continuously along all four edges by a structural

member and held firmly in position by means of a screw fixed thermally enhanced pressure

plate with a snap on face cap. All gaskets to be bonded and sealed during construction,

using a suitable waterproof adhesive, to ensure watertight joint at all cruciform

connections.

•	 Sealed Unit Details:

All windows shall contain sealed units to achieve a U-value of 1.8w/m2k, which shall be

manufactured in accordance with BS EN 1279 Parts 2 and 3 and carry the necessary and

appropriate guarantee.

Generally- where no safety glass required

6mm float glass externally

16mm 'Argon' filled cavity

6mm float glass internally

Generally-  Where safety glass is required as per NI building regulations 2012, for example

where within 800mm from floor level or 1500mm above floor level in a door or in a side

panel within 300 mm of either edge of a door: Applies to ground floor internal and external

panes and First floor internal panes

6.4mm laminated safety glass externally (grd floor) 6.4mm float glass externally (1st floor)

16mm 'Argon' filled cavity

6.4mm laminated glass internally (ground and first floors)

To all double glazed units:

'Warm edge' spacer bar

Soft coat low 'E' generally

Obscure patterned where required

Manifestation where annotated

Spandrel: Where annotated/required. Aluminium PPC tray internal

* Where critical areas of glazing are to resist horizontal line loads as per the building

regulations 2012, glazing manufacturer is to confirm glass thickness required to comply.

This is to be calculated in collaboration with the appointed aluminium window

manufacturer. These glazed areas are still to comply with a noise reduction of 37db for the

designated acoustic windows specified.

All glass will be subject to confirmation by the Contract Administrator, and shall be in

compliance with the Northern Ireland Building Regulations. The exact specification will be

determined by the _U_ Value calculation and structural requirements, all confirmed by the

Glazing Sub-Contractor. All glazing shall conform to BS6262. The glazing contractor is to

conduct a thermal safety check against glass fracture where required.

All doors to meet the specification above and to be fully compatible with the curtain walling

system and secured by design standards.

•	 Fixings:

All fixings shall be in strict accordance with the Systems Company's instructions and

guidelines as detailed in their technical literature and in accordance with the relevant

British Standards. All such accessories shall be manufactured from the Systems

Company's range of bracket and plate extrusions with all necessary _interlocking teeth_ and

slotted boltholes as detailed in their technical manual so as to allow for site tolerance and

structural movement.

All fixing of the screens to the building structure shall be achieved using a suitable anchor

and bracket fixing method capable of supporting all applicable loads and accommodating

the relevant fabrication, installation, site and expansion tolerances. Details of the method of

fixings shall be submitted to the Contract Administrator for approval prior to installation.

•	 Accessories:

All aluminium flashings, sills and other perimeter trims necessary to ensure the

performance of the glazing system shall be the responsibility of the glazing sub contractor

and shall be designed, fabricated, finished, install, secured and sealed in accordance with

the Systems Company's instructions and guidelines as detailed in their technical literature.

(It will be the responsibility of the glazing contractor to ensure that all profiles, panels,

flashings, pressings and other necessary trims associated with his works are processed in

one batch to ensure continuity of finish).

•	 Incorporated Components:

Where clearly indicated, these shall consist of the appropriate window and door inserts as

detailed in their specifications.

•	 Installation:

The 'CWCT Standard for Systemised Building Envelopes' is to be used as a reference for

all projects containing curtain walling. Screenwork should be installed by experienced and

qualified personnel, possessing either a recognised and relevant NVQ, or CWCT Window

Installers qualification.

•	 Accreditation:

The appointed Systems Company is to have ISO 9001 Quality Management Standard, and

ISO 14001 Environmental Management Systems Standard

120A	SPANDREL PANELS Refer to elevations and schedules

•	 Manufacturer: Contractor to provide proposals for acceptance

Product reference: Proprietary acrylic ceramic enamelled tempered spandrel glass to

double glazed unit within uPVC curtain walling .

•	 Colour/ texture: Colour to be grey glass.

U-value - 1.8w/m2k

Fixing: In accordance with manufacturers recommendations .

•	 Other requirements: Spandrel glass and double glazing construction to be fully integrated

and compatible with curtain walling/window system .

GENERAL REQUIREMENTS/ PREPARATORY WORK

210	DESIGN

•	 Curtain walling and associated features: Complete the detailed design. Submit before

commencement of fabrication.

•	 Related works: Coordinate in the detailed design.

215	DESIGN PROPOSALS

•	 Submission of alternative proposals: Preliminary design drawings indicate intent. Other

reasonable proposals will be considered.

220	SPECIFICATION

•	 Compliance standard: The Centre for Window and Cladding Technology (CWCT)

'Standard for systemised building envelopes'.

•	 Reference information: For the duration of the contract, keep available at the design office,

workshop and on site copies of:

-	The CWCT 'Standard for systemised building envelopes'.

-	Publications invoked by the CWCT 'Standard for systemised building envelopes'.

230	INFORMATION TO BE PROVIDED DURING DETAILED DESIGN STAGE

•	 Submit the following curtain walling particulars:

-	A schedule of detailed drawings and dates for submission for comment.

-	A schedule of loads that will be transmitted from the curtain walling to the structure.

-	Proposed fixing anchor details relevant to structural design and construction.

-	A detailed testing programme in compliance with the Main Contract master programme.

-	A detailed fabrication and installation programme in compliance with the Main Contract

master programme.

-	Proposals to support outstanding applications for Building Regulation consents or

relaxations.

232	QUALITY PLAN

•	 Requirement: Submit during detailed design.

•	 Content: In accordance with BS 5750, BS EN ISO 9001 and including the following:

-	Name of the quality manager.

-	Quality assessment procedures.

-	Inspection procedures to be adopted in checking the work.

-	Stages at which check lists will be used and samples of the lists.

-	List of work procedures on the correct use of materials or components, both off site and

on site.

-	List of product information with latest revisions.

-	Subcontractors involved in the work.

-	Subcontractors' quality plans.

-	Storage, handling, transport and protection procedures.

-	Procedure for registering and reporting non compliances.

-	Maintenance procedures and calibration records.

-	Certification that completed work complies with specification.

-	Check list register to ensure all items have been inspected and non compliances

discharged.

235	INFORMATION TO BE PROVIDED BEFORE COMMENCEMENT TESTING OR

FABRICATION OF CURTAIN WALLING

•	 Submit the following curtain walling particulars:

-	Detailed drawings to fully describe fabrication and installation.

-	Detailed calculations to prove compliance with design/ performance requirements.

-	Project specific fabrication, handling and installation method statements.

-	Certification for incorporated components manufactured by others confirming their

suitability for proposed locations in the curtain walling.

-	Recommendations for spare parts for future repairs or replacements.

•	 Recommendations for safe dismantling and recycling or disposal of products.

260	SAMPLES OF FIXINGS

•	 General: During detailed design, submit labelled samples of each type of fixing anchor,

including casting-in restraints and shims, together with manufacturers' recommended

torque figures.

270	FABRICATION SAMPLES

•	 General: During detailed design, submit samples of: Curtain Walling .

-	Obtain approval of appearance before proceeding.

DESIGN/ PERFORMANCE REQUIREMENTS

305	CWCT 'STANDARD FOR SYSTEMISED BUILDING ENVELOPES'

•	 General: Unless specified or agreed otherwise comply with:

Part 2 - Loads, fixings and movement.

Part 3 - Air, water and wind resistance.

Part 4 - Operable components, additional elements and means of access.

Part 5 - Thermal, moisture and acoustic performance.

Part 6 - Fire performance

Part 7 - Robustness, durability, tolerances and workmanship.

•	 Project performance requirements specified in this subsection: Read in conjunction with

CWCT performance criteria.

311A	INTEGRITY

•	 Requirement: The curtain walling must resist wind loads, dead loads and design live loads,

and accommodate deflections and movements without damage.

• Design wind pressure:   	as per the structural engineers recommendations and the

specification above.

•	 Hard body impact loads: To BS 8200:

-	Location and category: category A.

•	 Soft body impact loads - curtain walling to BS EN 14019:

-	Location and classification:   class E1.

•	 Soft body impact loads - glass to BS EN 12600:

Location and classification: (A) 1.

320	DEFLECTION UNDER DEAD LOADS

•	 Requirement: Framing members parallel to the curtain walling plane must not:

-	Reduce glass bite to less than 75% of design dimension.

-	Reduce edge clearance to less than 3 mm between members and immediately adjacent

glazing units, panel/ facing units or other fixed units.

-	Reduce clearance to less than 2 mm between members and movable components such

as doors and windows.

325	DEFLECTION UNDER WIND LOAD

•	 Requirement: To CWCT 'Standard for systemised building envelopes' clause 3.5 2 and the

following additional requirements:   None.

•	 Additional stiffness to CWCT 'Standard for systemised building envelopes' clause 3.5 4.2:

Not allowed.

332	APPEARANCE AND FIT

•	 Requirement: Design curtain walling system:

-	To ensure position and alignment of all parts and features as shown on preliminary

design drawings.

-	To accommodate deviations in the primary support structure.

•	 Primary support structure: Before commencing installation of curtain walling system, carry

out survey sufficient to verify that required accuracy of erection can be achieved.

-	Give notice: If the structure will not allow the required accuracy or security of erection.

-	Design tolerances: 10mm.

•	 Curtain wall envelope zone tolerances:

-	Width: 10mm.

Critical reference location: ..

•	 Maximum permitted component and installation tolerances: 10mm.

340	AIR PERMEABILITY

•	 Requirement: Permissible air leakage rates of 1.5m³/hr/m² for fixed lights and 2.0

m³/hr/lin.m for opening lights must not be exceeded when the curtain walling is subjected

to the peak test pressure.

•	 Permeability class to BS EN 12152:   A2.

Peak test pressure:   	600 Pa.

350	WATER PENETRATION

•	 Watertightness class to BS EN 12154: R5.

-	Peak test pressure: 600 Pa.

•	 Additional requirements: Underside of any transom not to be wetted at peak test pressure.

370	THERMAL PROPERTIES

•	 Method of calculating the thermal transmittance (U-value) of curtain walling/ each zone of

curtain walling: Weighted U-value.

•	 Average U-value of curtain walling:   1.8W/sqmK.

•	 Curtain wall zone interfaces: Co-ordinate to achieve required average U-value.

•	 Method for assessing thermal transmittance (U-value) of assemblies: By calculation.

385	THERMAL STRESS IN GLAZING

•	 Glass panes/ units: Must have adequate resistance to thermal stress generated by

orientation, shading, solar control and construction.

390	AVOIDANCE OF CONDENSATION

•	 Requirement: Notional psychrometric conditions under which condensation must not form

on building interior surfaces of framing members or any part of infill panels/ facings are:

-	Notional outdoor psychrometric conditions as BS 6229, table A1.

-	Notional indoor psychrometric conditions:

Temperature: 20°C.

Relative humidity:   	55%.

Vapour pressure:   	1.28 kPa .

420	FIRE RESISTANCE OF CURTAIN WALLING

•	 Standard: To BS 476-22.

-	Minimum periods and criteria: 30 min. integrity, 30 min, insulation .

425	INTERNAL SURFACE SPREAD OF FLAME OF CURTAIN WALLING

•	 Standard: To BS 476-7.

-	Class 1.

430	FIRE STOPPING

•	 Locations: At junctions of curtain walling with compartment walls and floors.

•	 Materials and methods of fixing: To ensure fire resistance not less than that specified for

compartment walls and floors.

450	SAFETY

•	 Finished surfaces of curtain walling: Accessible internal and external areas must not:

-	Have irregularities capable of inflicting personal injury.

-	Release irritant or staining substances.

460	STRUCTURAL SEALANT GLAZING REQUIREMENTS

•	 Structural sealant glazing units: Installable, removable and replaceable without site

application of structural bonding sealant.

•	 Structural sealant glazing design: Must limit design tensile stress of sealants to 138 kPa.

TESTING

510	COMPARISON (TYPE) TESTING

•	 Requirement: To CWCT 'Standard for systemised building envelopes', Part 8.

•	 Test results and reports: Before commencement of curtain walling fabrication and

installation, submit proof of compliance with this specification.

635	SITE HOSE TEST

•	 Requirement: To CWCT 'Standard for systemised building envelopes', 'Standard test

methods for building envelopes' Section 9.

Joints to be tested:   	As required.

PRODUCTS

710	ALUMINIUM ALLOY FRAMING SECTIONS

•	 Standard: To relevant parts of BS EN 515, BS EN 573, BS EN 755 and BS EN 12020.

•	 Alloy, temper and thickness: Suitable for the application and specified finish.

•	 Structural members: To BS 8118.

712	ALUMINIUM ALLOY SHEET

•	 Standards: To relevant parts of BS EN 485, BS EN 515 and BS EN 573.

•	 Alloy, temper and thickness: Suitable for the application and specified finish.

730	MECHANICAL FIXINGS

•	 Stainless steel: To BS EN ISO 3506, grade A2 generally, grade A4 when used in severely

corrosive environments.

•	 Carbon steel: To BS 4190 and suitable for galvanizing or other protective coating.

•	 Aluminium brackets, rivets and shear pins: To relevant parts of BS EN 755.

732	ADHESIVES

•	 General: Not degradable by moisture or water vapour.

735	FIXING ANCHORS

•	 Type and use: Reviewed and approved by fixing manufacturers. Submit confirmatory

information on request.

•	 Dimensions: Not less than recommended by their manufacturers.

•	 Adjustment capability: Sufficient in three dimensions to accommodate building structure

and curtain walling fabrication/ installation tolerances.

737	GLASS GENERALLY

•	 Standards: To BS 952 and relevant parts of:

-	BS EN 572 for basic soda lime silicate glass.

-	BS EN 1096 for coated glass.

-	BS EN 1748 for borosilicate glass.

-	BS EN 1863 for heat strengthened soda lime silicate glass.

-	BS EN 12150 for thermally toughened soda lime silicate glass.

-	BS EN 13024 for thermally toughened borosilicate glass.

-	BS EN ISO 12543 for laminated glass.

•	 Glass quality: Clean and free from obvious scratches, bubbles, cracks, ripplings, dimples

and other defects.

•	 Glass edges: Generally undamaged. Shells and chips not more than 2 mm deep and

extending not more than 5 mm across the surface are acceptable if ground out.

739	DIMENSIONAL TOLERANCES ON GLASS

•	 Measurement of tolerances: Before any thermal toughening/ heat strengthening.

•	 Pane dimensions less than 1500 mm:

-	For 3 to 6 mm thick glass: ± 1.0 mm.

-	For 8 to 12 mm thick glass: ± 1.5 mm.

-	For 15 mm thick glass: ± 2.0 mm.

-	For 19 mm and 25 mm thick lass: ± 2.5 mm.

•	 Pane dimensions more than 1500 mm:

-	For 3 to 6 mm thick glass: ± 1.5 mm.

-	For 8 to 12 mm thick glass: ± 2.0 mm.

-	For 15 mm thick glass: ± 2.5 mm.

-	For 19 mm and 25 mm thick lass: ± 3.0 mm.

•	 Pane squareness: Not more than 4 mm difference in diagonal measurements.

741	DISTORTIONAL TOLERANCES ON GLASS

•	 Measurement of tolerances: After any thermal toughening/ heat strengthening.

•	 Maximum bow: 0.2% of pane dimension.

•	 Maximum roller wave:

-	For 3 to 5 mm thick glass: 0.5 mm.

-	For 6 to 10 mm thick glass: 0.3 mm.

-	For 12 mm and thicker glass: 0.15 mm.

•	 Maximum edge dip:

-	For 3 to 5 mm thick glass: 0.8 mm.

-	For 6 to 10 mm thick glass: 0.5 mm.

For 12 mm and thicker glass: 0.25 mm.

745	INSULATING GLASS UNITS

•	 Standard and labels for hermetically sealed units: To BS EN 1279.

•	 Label: Each pane.

•	 Colour of aluminium perimeter spacers:   grey.

•	 Perimeter taping: Not to be used.

•	 Perimeter seals:

-	Resistant to UV light degradation on exposed edges.

-	Compatible with structural, assembly and weather sealants.

760	GASKETS

•	 Material:

-	Noncellular rubber to BS 4255-1.

-	Cellular rubber to ASTM-C509.

•	 Continuity: Outer gaskets of single front sealed curtain walling systems and inner gaskets

of drained and ventilated or pressure equalized curtain walling systems must be formed in

a complete frame with sealed joints. Vulcanized rubber gaskets must have factory moulded

corner joints.

•	 Durability: Resistant to oxidation, ozone and UV degradation.

765	WEATHERSTRIPPING OF OPENING UNITS

•	 Material:

-	Noncellular rubber to BS 4255-1.

-	Cellular rubber to ASTM-C509.

-	Polypropylene woven pile, silicone treated.

•	 Attachment: Fixed in undercut grooves in framing sections using preformed corners, with

any joints in the length.

770	GENERAL SEALANTS

•	 Selection: In accordance with BS 6213 from:

-	Silicone.

-	One part polysulfide.

-	Two part polysulfide.

-	One or two part polyurethane.

•	 Classification and requirements: To BS EN ISO 11600.

•	 Reaction to contact products and finishes: Stable and compatible.

FABRICATION AND INSTALLATION

910	GENERALLY

•	 Electrolytic corrosion: Prevent. Submit proposed methods.

•	 Fixings: Concealed unless indicated on detailed drawings. Where exposed they must

match material and finish of the products fixed.

•	 Fabrication: Machine cut and drill products in the workshop wherever possible.

•	 Identification of products: Mark or tag to facilitate identification during assembly, handling,

storage and installation. Do not mark surfaces visible in the completed installation.

915	GLAZING

•	 Requirement: As section L40, unless specified otherwise in this section.

•	 Directional patterned/ wired glass: Generally fix parallel to surround and align adjacent

panes where seen together at close quarters.

917	FIXINGS/ ADHESIVES APPLICATION

•	 Requirement: As section Z20, unless specified otherwise in this section.

920	SEALANT APPLICATION

•	 Requirement: As section Z22, unless specified otherwise in this section.

930	ASSEMBLY

•	 General: Carry out as much assembly as possible in the workshop.

•	 Joints (other than movement joints): Rigidly secured, reinforced where necessary and fixed

with hairline abutments.

•	 Displacement of components in assembled units: Submit proposals for reassembly on site.

955	FIXING ANCHOR INSTALLATION

•	 Site drilling or cutting into structure: Submit proposals for positions other than shown on

detailed drawings.

•	 Concrete supporting structure:

-	Cast-in inserts: Provide detailed locational information. Protect cavities in inserts from

entry of concrete.

-	Edge fixing distances: Not less than recommended by fixing anchor manufacturers.

•	 Corrective fabrication: Minimize. Where necessary, submit proposals.

970	CURTAIN WALLING INSTALLATION

•	 Securing to fixing anchors: Through holes formed during fabrication only.

•	 Tightening mechanical fasteners: To manufacturer's recommended torque figures. Do not

overtighten fasteners intended to permit differential movement.

•	 Protective coverings: Remove only where necessary to facilitate installation and from

surfaces that will be inaccessible on completion.

980	INTERFACES

•	 Flashings, closers, etc: Locate and form correctly to provide weathertight junctions with the

curtain walling.

982	IRONMONGERY

•	 Assembly and fixing: Accurately, using fasteners with matching finish supplied by

ironmongery manufacturer.

•	 Completion: Check, adjust and lubricate as necessary to ensure correct functioning.

985	MAINTENANCE

•	 Maintenance manual: Incorporate details within the Building Manual in accordance with

CWCT 'Standard for systemised building envelopes' clause 7.6.1.

Materials certification and test reports to be included: All as required.

H21

Timber weatherboarding

H21 Timber weatherboarding

To be read with Preliminaries/ General conditions.

116A	TIMBER WEATHERBOARDINGTO FRONT DOOR CANOPIES

•	 Substrate: Door canopy timber rafter.

•	 Breather membrane: Not required.

•	 Battens: Not required.

Boarding:

-	Quality of timber (exposed surfaces): To BS 1186-3, Class: CSH.

-	Species: Contractor's choice.

-	Profile: Tongued and grooved v-jointed.

-	Finished face dimension (overall width): 96 mm.

-	Finished thickness 19 mm.

-	Moisture content at time of fixing: 13-19 %.

-	Method of fixing to each support: Secret nailed .

•	 Other requirements: Provide stain and varnish finish as M60.

120	CONTROL SAMPLE

•	 General: Complete an area of boarding in an approved location and obtain approval of

appearance before proceeding.

145	TREATED TIMBER

•	 Surfaces exposed by minor cutting and/ or drilling: Treat with two flood coats of a solution

recommended for the purpose by main treatment solution manufacturer.

150	SURFACE TREATMENT

•	 Finishing system: Before fixing boards, apply first coat of specified system to all surfaces.

Apply liberally to end grain.

160	FIXING BOARDING

•	 General: Fix boards securely to give flat, true surfaces free from undulations, lipping, splits,

hammer marks and protruding fasteners.

•	 Movement: Allow for movement of boards and fixings to prevent cupping, springing,

excessive opening of joints or other defects.

•	 Heading joints: Position centrally over supports and at least two board widths apart on any

one support.

•	 Nail heads: Punch below surfaces that will be seen in the completed work.

H31

Metal profiled/ flat sheet cladding/ covering

H31 Metal profiled/ flat sheet cladding/ covering

To be read with Preliminaries/ General conditions.

TYPES OF CLADDING/ COVERING SYSTEM

120C	METAL	PROPRIETARY ALUMINIUM STANDING SEAM ROOF SYSTEM

" Manufacturer:  Contractors choice, provide sample for CA approval.  Contractor to

provide site specific system design information for approval.

"Performance:  Overall roofing build up to achieve a u-value of 0.10 W/sq.mK. Insulation

materials provided to have a zero Ozone Depletion Potential (ODP) and Global Warming

Potential (GWP) of less than 5 in accordance with the requirements of BS 4841-1. .

" Support structure: Contractor designed timber deck/ trusses.

-	Bearing width:  50 mm minimum.

-	Pitch:  Refer to Elevations and Sections, 1.5° minimum.

" External sheets: Clad Alloy Aluminium Standing Seam

-	Material: Aluminium alloy BS EN AW 3004 (AlMn1Mg1)

0.2% proof stress (Rp0.2) = 185 N/mm2 minimum.

Ultimate tensile strength (Rm) = 220 N/mm2 minimum.

Both faces clad with a zinc rich alloy as Clad Alloy.

-	Thickness: 0.9 mm (nominal)

Tolerance on thickness to be +0.05 mm and –0.025 mm. This is a class 2 thickness

tolerance as per BS EN 508-2:2000.

-	Finish:  Clad alloy Stucco embossed aluminium.

-	Other requirements: Sheets to be supplied in single length sheets.  Purlin centres and/or

gauge of sheets to be determined from manufacturer's load/span tables and the specific

loading for the project.

-	25 Year Guarantee: Contractor to provide the client with a 25 year system guarantee for

all metal roof system components, accessories and associated products described within

this specification.

Guarantee to be subject to:

"  	All the system components as defined in the specification to be supplied by a single

system supplier

"  	Provision of project specific calculation data as identified in the specification.

"  	A fully trained and approved roofing contractor installing the system.

"  	The system being installed by operatives who have been trained at a CITB

approved training centre.

"  	A satisfactory inspection of the completed roof system is undertaken by a qualified

Site Services team

"  	Accessories:  As necessary - Extruded Aluminium Alloy Gable End Channels,

Extruded Aluminium Alloy Gable End Hooks, Extruded Aluminium Alloy Tolerance Gable

Clip Extrusion, Extruded Aluminium Alloy Zed Spacer, Extruded Aluminium Alloy Flat Bar

22mm x 6mm, Fabricated Aluminium Alloy `U` Type Ridge Closures, Extruded

Aluminium Alloy Drip Angle 40mm x 20mm, profile ridge fillers, profile eaves fillers.

Fabricated aluminium alloy flashings – material and finish as per cladding sheets

Fabricated welded soaker units - material and finish as per cladding sheets

"  	End laps: No end laps – single length sheets.

"  	Side laps: Top sheets are mechanically seamed over head of support clips with a

proprietary mechanical _zipping_ machine.

"  	Spacers: Steel reinforced Polyamide Clips to improve thermal performance and

acoustics.

-	Fasteners: 6.0 mm diameter stainless steel torque controlled fasteners. Two fasteners

per clip positioned diagonally opposite in the holes of the base of the clip.

NB. The use of curved and/or long length sheets (e.g. over 25 m) may require a greater

number or different type of fastener, consult with manufacturers technical services for

project specific guidance.

-	Fixed point:  	Refer to project specific calculation for confirmation of the fixed point

design. Should any detail change, please refer to system supplier for updated

calculation.

-	Sub-purlin:  	40 mm deep top-hat profile sub-purlin x 1.6 mm thick galvanised steel to

BS EN 10326, grade S280GD+Z with designation 275 coating,

-	Fasteners:  6.3 mm diameter stainless steel self tapping fasteners. One fastener to be

installed at every truss position, both sides of the top-hat profile sub-purlin.

Final fixing requirements and specification to be confirmed by installing approved

cladding contractor in conjunction with specific building loads and internal conditions.

Please liaise with system supplier technical services.

Special note : Please refer to system supplier fastener calculations . Should any detail

change, please refer to updated calculation.

"  	Thermal insulation:  	As per clause 271.

"  	Breather membrane: As per clause 261.

"  	Lining sheet: not required.

Aluminium Site Welding: Aluminium site welding will be fully in accordance with industry

standard details and in accordance with roof system supplier standard recommendations

and industry guide to good practice by approved welding contractors.

Site Welding must be carried out fully in accordance with Approved Welding Procedure

Specification ASW/TIG/001 Rev 'B' 1997 as defined in BS EN ISO 9606-2 for material

gauges between 0.8mm-3.0mm thickness.

Site welding operatives must be certified to BS EN ISO 9606-2 standard for material

gauges between 0.8mm-3.0mm thickness.

Gas/flux shielding  	100%.AR

Gas flow rate shielding  		10L/mm.

Tungsten Electrode Type/Size  		2mm-2% Thoriated.

Interpass Temperature  		650 degree C maximum.

Welding position  	PA, PB & PF.(vertical up to cover all positions)

The weld test procedure shall be in accordance with BS EN ISO 15614-2:2005

All site welding activities to comply with SAFE Contractor, C.H.A.S. standards to ensure

works are carried out within current health and safety legislation

All site operations must be carried out to ISO 9001:2000 quality management standard

Average girth of weld achieved shall be 8 mm – 10 mm full weld penetration on butt

joints and open corners. Joints may be butt, overlap or fillet welded.

All Site Welding works to be carried out generally in accordance with the _Fire Prevention

on Construction Sites seventh edition: January 2009_ guidance notes.

All works to be carried out in accordance with the Risk, COSHH & PPE Assessment

Documents

121A   STRUCTURE:

Check that structure is in a suitable state to receive cladding before commencing fixing.

The subcontractor must confirm acceptance to Main Contractor and C A.

Support structure tolerances to be as per cladding manufacturer's recommendations.

Do not fix cladding until final coats of paint have been applied to outer surfaces of the

supporting structure.

122A   PROTECTION:

218  Store metal sheets under cover to keep dry and to prevent staining.

Storing should be all in accordance with the sheet and panel manufacturer's recommendations.

123A   FASTENINGS GENERALLY:

Type(s), size(s), material(s) and finish(es) as specified, or in the absence of such

specification, as Recommended for the purpose by the cladding manufacturer.

124A   FITTINGS AND ACCESSORIES GENERALLY:

Cappings, closure pieces, flashings, trims, gutters, fillers, spacers, tapes, sealants,

fixings, etc, where not specified, to be types recommended by the cladding

manufacturer.

125A   ISOLATING TAPE:

A type recommended for the purpose by the cladding manufacturer.  Apply to those

surfaces of supports, which would otherwise be in contact with cladding or accessories

after fixing.

126A   ROOF PENETRATIONS:

For SVP penetrations provide an adequate sized proprietary coated aluminium bolt-on

soaker unit compatible with roofing system.  Provide all necessary openings, seals,

trims, GRP weatherings, isolating tapes etc as necessary -  type recommended for the

purpose by the cladding manufacturer.  Apply coatings on site necessary to exposed

surfaces which would otherwise be in contact with cladding or accessories after fixing.

187A	DEFLECTION OF METAL CLADDING/ COVERING

•	 Roof covering: Maximum permitted deflection under distributed loads as a multiple of span

and due to:

-	Dead load: L/500.

-	Dead and imposed loads: L/200.

Dead and wind loads: L/90.

198	WATER PENETRATION

•	 Requirement: Under site exposure conditions, moisture must not penetrate onto internal

surfaces, or into cavities not designed to be wetted.

200	AVOIDANCE OF INTERSTITIAL CONDENSATION

•	 Requirement: Determine interstitial condensation risk of cladding/ covering system using

the method described in BS 5250 Appendix D. If necessary, provide a vapour control layer

to ensure that damage and nuisance from interstitial condensation does not occur.

•	 Outdoor psychrometric conditions (notional): To BS 6229, table A.1 as follows:

Winter  	Summer

-	Temperature  		-5°C  	18°C

-	Relative humidity  	90%  	65%

-	Vapour pressure  	0.36 kPa  	1.34 kPa

•	 Indoor psychrometric conditions (notional): As follows:

-	Temperature: 20°C .

-	Relative humidity: 55% .

-	Vapour pressure: 1.28 kPa .

•	 Calculated amount of winter interstitial condensate (maximum): 0.35 .

•	 Winter interstitial condensate:

-	Calculated amount (maximum): 0.35 kg/m².

-	Calculated annual net retention: Nil.

202	AVOIDANCE OF SURFACE CONDENSATION

•	 Requirement: Determine surface condensation risk of cladding/ covering system using the

method described in BS EN ISO 13788. If necessary, revise thermal insulation to provide

satisfactory temperature factor (fmin). ensure that damage and nuisance from surface

condensation does not occur.

FIXING CLADDING/ COVERING

219	FASTENERS

•	 Unspecified fasteners: Recommended for the purpose by the cladding/ covering

manufacturer.

221	FITTINGS AND ACCESSORIES

•	 Unspecified fittings and accessories: Recommended for the purpose by the cladding/

covering manufacturer.

234A	ALUMINIUM GUTTERSGENERALY

•	 Manufacturer: Contractor's choice  Agrément certified. Provide sample for CA approval.

-	Product reference: Proprietary single skin polyester powder coated aluminium gutter

system compatible with metal roofing system, fascia & soffit..

•	 Sizes: As detailed.

•	 Material: Galvanized mild steel to BS EN 10142 grade DX51D+Z with zinc coating

designation 600.

-	Gauge/ Thickness: Min. 3 mm.

-	External finish: Polyester Powder Coated.

•	 Jointing method: As recommended by manufacturer.

•	 Fixing method: 50 x 6 mm galvanized steel support straps at 1 m centres.

•	 Accessories: Outlets & stop ends as necessary.

271B	MINERAL WOOL THERMAL INSULATION [PROPRIETARY ALUMINIUM STANDING

SEAM ROOF SYSTEM]

•	 Standard: To BS EN 13162.

•	 Manufacturer: Contractors choice, provide sample for CA approval.

-	Product: Proprietary mineral fibre insulation.

•	 Thickness (minimum): 100mm in one layer compressed to overall thickness of 80mm.

•	 Installation: Continuous and not compressed between outer and lining sheets. Secure to

prevent future movement or dislodgement. Considered with overall roof construction and

350mm insulation at ceiling level and clip design by roof system manufacturer.

NOTE: Insulation within built up metal roof system is not to be included in thermal

calculation, only installed

for acoustic improvements.

280A	BREATHER MEMBRANE

•	 Standard: To BS 4016, type 3.

•	 Manufacturer: Contractors choice, provide sample for CA approval.

-	Product : Proprietary multilayer polypropylene non-woven core compatible with roof

system.

•	 Continuity: No breaks. Minimise joints.

-	Penetrations and abutments: Attach to breather membrane with tape. Achieve full bond.

-	Laps: Not less than 150 mm, bond with tape. Achieve full bond.

•	 Tape: As recommended by breather membrane manufacturer.

•	 Repairs: Lapped patch of breather membrane material secured with continuous band of

tape on edges.

•	 Junctions at flashings, sills, gutters etc. Overlap and allow free drainage to exterior.

300A	PROFILE FILLERS GENERALLY

•	 Material: Closed cell cross linked EP.

•	 Manufacturer: Contractors choice.

-	Product references: To be fully compatible with roofing system.

•	 Colour: Black.

•	 Thickness: min 30 mm.

•	 Fixing method: Self-adhesive tape.

-	Requirement: To close cavities/ regulate air paths within the external envelope. Tight fit

with no unintended gaps.

305	FIRE RESISTING PROFILE FILLERS

•	 Types: To accurately match sheet profile.

•	 Fixing method: Adhesive recommended by profile filler manufacturer.

410A	FIXING SHEETS GENERALLY

•	 Cut edges: Clean true lines.

•	 Penetrations: Openings to minimum size necessary.

-	Edge reinforcement: As recommended by roof system manufacturer and in accordance

with all relevant good practice guides.

•	 Sheet orientation: Exposed joints of side laps away from prevailing wind unless shown

otherwise on drawings.

•	 Sheet ends, laps and raking cut edges: Fully supported and with fixings at top of lap.

•	 Fasteners: Drill holes. Position at regular intervals in straight lines, centred on support

bearings.

-	Position of fasteners in oversized drilled holes: Central.

-	Fasteners torque: Sufficient to correctly compress washers.

•	 Debris: Remove dust and other foreign matter before finally fixing sheets.

•	 Completion: Check fixings to ensure watertightness and that sheets are secure.

•	 Cut edges: Paint to match face finish.

470	STRUCTURAL MOVEMENT JOINTS

•	 Type: Cover flashing fixed on one side over gap between sheets.

•	 Location: Coincident with structural movement joint.

•	 Width of gap: To match structural movement joint requirements.

•	 Requirement: Weathertight.

480A	FLASHINGS/ TRIMS GENERALLY

•	 Lap joint treatment:

-	Vertical and sloping flashings/ trims: End laps to be same as for adjacent sheeting.

-	Horizontal flashings/ trims: End laps to be 150 mm, sealed and where possible arranged

with laps away from prevailing wind.

•	 Method of fixing: To structure in conjunction with adjacent sheeting. Otherwise to sheeting.

-	Fasteners: In accordance with roof system manufacturers recommendations.

540	ABUTMENTS

•	 Junctions with flashings: Weathertight and neatly dressed down.

550	SEALING LAPS ON EXTERNAL SHEETS

•	 Sealant tape: Types recommended by sheet manufacturer.

-	Position: Below fixing positions in straight unbroken lines, parallel to and slightly back

from edge of sheet.

•	 Seal quality: Effective, continuous and not over compressed.

•	 End laps: Sealant tape positions:

-	Single line tape: Immediately below line of fasteners.

-	Second line tape (where specified): Slightly set back from edge of external sheet.

•	 Side laps: Sealant tape positions:

-	Single line tape: Outside line of fasteners.

-	Second line tape (where specified): On other side of fasteners.

554A	WATER VAPOUR SEALING AT LAPS AND PENETRATIONS IN METAL LININGS -

SEALANT TAPE

•	 Sealant tape: Contractors choice, to be compatible with roof system.

-	Position : Below fixing positions in straight unbroken lines, parallel to and slightly back

from edge of sheet.

•	 Seal quality: Effective, continuous and not over compressed.

H32

Plastics profiled sheet cladding/ covering

H32 Plastics profiled sheet cladding/ covering

To be read with Preliminaries/ General conditions.

TYPES OF CLADDING/ COVERING SYSTEM

111A	PVC-U 	TO SOFFIT OF FLAT ROOF CANOPIES

"  	 Humidity load: To BS EN ISO 13788, class: 4.

"  	 Support structure: 25x38mm treated timber battens.

Spanning form: Between timber joists.

"  	 System type: BBA approved single skin interlocking board system. V

jointed..

-  	Material: PVC-U to BS 4203.

-  	Profile: Squared edge flush profile.  Smooth finish.

-  	Nominal sizes: 125mm wide, 5mm thickness.

"  	 Light diffusion: Type C.

"  	 Finish/ Colour: Colour / foil finish from basic range.

"  	 Fire properties:

-  	Surface spread of flame to BS 476-7: Class 1.

"  	 Safety:

-  	Fragility class to ACR(M)001: A.

Accessories: Provide 10mm air gap and compatible angle ventilators and insect

mesh to

prevent insect ingress.

"  	 Primary sheet fasteners: 30mm stainless steel pins in accordance with

manufacturer's

instructions.

-  	Fastener profile location: In accordance with manufacturer's instructions.

-  	Sealing: Low modulus silicone As clause 330.

"  	 Other requirements: Provide all necessary compatible trims, starter trims

and jointing

channels.

GENERAL REQUIREMENTS

150	DESIGN

"  	 Cladding/ covering system: Complete the detailed design and submit before

commencement of fabrication.

-  	Standard: To BS 5427-1.

Related works: Coordinate in detailed design.

160	PRODUCT SAMPLES

•	 General: Before commencing detailed design submit labelled samples of the following: PV

C-U Cladding Board.

165	FASTENER SAMPLES

•	 General: During detailed design, submit labelled samples of each type of fastener.

DESIGN/PERFORMANCE REQUIREMENTS

191	WATER PENETRATION

•	 Requirement: Under site exposure conditions moisture must not penetrate onto internal

surfaces, or into cavities not designed to be wetted.

FIXING CLADDING/ COVERING

213	FASTENERS

•	 Unspecified fasteners: Recommended for the purpose by the cladding/ covering

manufacturer.

217	ACCESSORIES

•	 Unspecified accessories: Recommended for the purpose by the cladding/ covering

manufacturer.

220	PROFILE FILLERS

•	 Types: Supplied by cladding/ covering manufacturer accurately matching sheet profile.

-	Material/ colour: to match board.

•	 Locations: As shown on drawings, on the line of or above, fasteners and wherever

necessary to close off profile cavities from the outside and inside of the building.

•	 Fit: Tight with no gaps.

•	 Profile fillers in sealed laps: Bed in sealant on top and bottom surfaces.

230	FIXING SHEETS GENERALLY

•	 Cut edges: Clean true lines.

•	 Sheet orientation: Exposed joints of side laps away from prevailing wind unless shown

otherwise on drawings.

•	 Fastener hole location: At regular intervals in straight lines and not less than 50 mm from

edges of sheets and fittings.

•	 Crown fixing: For sheets with a profile depth greater than 20 mm support crowns at primary

fixings with profile fillers.

•	 Debris: No dust or foreign matter to be present within construction.

•	 Fasteners torque: Sufficient to correctly compress washer.

•	 On completion: Fixings to be watertight and sheets secure with no buckling or distortion.

240	MULTIPLE SKIN CONSTRUCTION

•	 Liner, intermediate and outer sheet fixing: No distortion will be accepted.

•	 Inaccessible surfaces: To be clean.

•	 Inner and outer sheet laps: Sealed.

260	ACCOMMODATION OF THERMAL MOVEMENT

•	 PVC-U and polycarbonate sheets: Use oversize holes for primary fixings in accordance

with sheet manufacturer's recommendations.

320	ABUTMENTS

•	 Junctions with flashings: Watertight and neatly dressed.

330	SEALING LAPS

•	 Sealant tape: Types recommended for the purpose by sheet manufacturer.

•	 End laps: Position sealant tape in straight, unbroken lines below fixing positions, parallel to

and slightly back from edge of sheet.

•	 Side laps: Position sealant tape outside the line of fasteners. Where a second tape is

specified, position on the other side of the fasteners.

•	 Laps between plastics sheets and other materials: Use sealant tape specified for other

materials.

•	 Seal quality: Effective, continuous and not overcompressed.

H65

Single lap roof tiling

H65 Single lap roof tiling

To be read with Preliminaries/ General conditions.

TYPES OF TILING

115B	CONCRETE ROOF TILINGPLAIN SINGLE LAP INTERLOCKING TILE TO ROOFS OF

ALL DWELLINGS - COLD ROOF CONSTRUCTION

•	 Substrate: Contractor Designed timber trusses / cut roof timbers.

•	 Pitch: Refer to drawings.

•	 Underlay: Proprietary BBA approved 3 layer heavy grade waterproof and vapour

permeable un-tearable roofing underlay. Minimum vapour transmission resistance

0.11MNs/g.  To incorporate vapour permeable core between two layers of non-woven spun

-bonded polypropylene.

-	Direction: Parallel to eaves.

-	Head-lap (minimum): 150 mm.

•	 Battens:

-	Size: 50 x 38 mm for truss / rafter spacings up to 600mm.

-	Fixing: 65 x 3.35 mm galvanized round plain shank nails.

•	 Tiles: To BS EN 490, interlocking.

-	Manufacturer: Contractors choice, provide samples for CA approval.

Product : Proprietary BBA approved flat, smooth, single-lap interlocking concrete roof tile

to be laid in broken bond pattern.

-	Colour: Standard colour to be confirmed by CA.

-	Size: As per manufacturers recommendations to suit PV panels.

-	Head-lap: 75mm minimum to manufacturers recommendations.

-	Fixing: Fixing specification to be obtained from roof tile manufacturer which is to be

specific to the particular siting, orientation, elevation and location of building. Submit

fixing specification to CA prior to commencing slating work.

Other requirements:  [Compatible proprietary dry ridge ventilating system and concrete

ridge tiles to be used on all dwellings in accordance with detail drawings.  Contractor to

cut underlay in accordance with manufacturers instructions to ventilate roof void.

Roof tiles to be compatible with Contractors choice of PV system to be installed on roof

in accordance with Code for Sustainable Homes and M&E Consultants Specification].

TILING GENERALLY

210	BASIC WORKMANSHIP

•	 General: Fix tiling and accessories to make the whole sound and weather tight at earliest

opportunity.

•	 Setting out: To true lines and regular appearance, with neat fit at edges, junctions and

features.

•	 Fixings for accessories: As recommended by tile manufacturer.

•	 Gutters and pipes: Keep free of debris. Clean out at completion.

240A	UNDERLAY

•	 Specification underlay to be of triple-ply construction with waterproof & vapour permeable

core laminated & protected between two layers of non-woven spun bonded polypropylene.

water vapour transmission resistance 0.17MNs/g weight g/m2 125. Resistance to wind

uplift: unrestricted use underlay to be laid in accordance with BS 5534:Part 1:1997 &

Manufactures instructions.

•	 Handling: Do not tear or puncture.

•	 Laying: Maintain consistent tautness.

•	 Vertical laps (minimum): 150 mm wide, coinciding with supports and securely fixed.

•	 Fixing: Galvanized steel, copper or aluminium 20 x 3 mm clout head nails in accordance

with manufacturers recommendations.

•	 Eaves: Where exposed, underlay must be BS 747/ BS 5534, Annex A Type 5U, or an

equivalent UV durable type.

•	 Penetrations: Use proprietary underlay seals or cut underlay to give a tight, watertight fit

around pipes and components.

•	 Ventilation paths: Do not obstruct.

245	BATTENS/ COUNTERBATTENS - TREATED

•	 Timber: Sawn softwood.

-	Standard: BS 5534, clause 4.12.1.

-	Permissible characteristics and defects: Not to exceed limits in BS 5534, annex C.

-	Moisture content at time of fixing and covering (maximum): 22%.

•	 Preservative treatment: As section Z12 and British Wood Preserving and Damp-proofing

Association Commodity Specification C8.

-	Type: Organic solvent.

265	BATTEN FIXING

•	 Setting out: Align parallel to ridge in straight horizontal lines to gauge of the tile. Align on

adjacent areas.

•	 Batten length (minimum): Sufficient to span over three supports.

•	 Joints in length: Square cut. Butt centrally on supports. Joints must not occur more than

once in any group of four battens on one support.

•	 Additional battens: Provide where unsupported laps in underlay occur between battens.

•	 Fixing: Each batten to each support. Splay fix at joints in length.

275	TILE FIXING

•	 Setting out: Lay each course with tails aligned.

•	 Ends of courses: Use special tiles to maintain bond and to ensure that cut tiles are as large

as possible.

•	 Perimeter tiles: Fix and clip all tiles.

•	 Nail fixed tiles: Use nails recommended by tile manufacturer. Fix through every hole of every tile

•	 Clip fixed tiles: Use clips recommended by tile manufacturer and clip every tile.

280	LOCAL AND GENERAL FIXING AREAS

•	 Definitions:

-	Local areas: Bands of tiling around edges or obstructions of each plane of the roof.

Calculate extent of each band in accordance with BS 5534, section 5.

General areas: Remaining areas of roof tiling.

290	MORTAR BEDDING/ POINTING

•	 Mortar: As section Z21, 1:3 cement:sand, with plasticizing admixtures permitted.

-	Bond strength providing resistance to uplift: To BS 5534.

•	 Weather: Do not use in wet or frosty conditions or when imminent.

•	 Preparation of tiles and accessories to be bedded: Wet and drain surface water before

fixing.

•	 Appearance: Finish neatly as work proceeds and remove residue.

EDGES/ JUNCTIONS/ FEATURES

305	GENERALLY

•	 Fittings and accessories: As recommended by tile manufacturer. Do not improvise.

-	Exposed fittings and accessories: To match tile colour and finish.

•	 Cut tiles: Cut only where necessary, to give straight, clean edges.

•	 Flashings: Fix with or immediately after tiling. Form neatly.

325	FIRE SEPARATING WALLS

•	 Separating walls: Completely fill space between top of wall and underside of tiles with

mineral wool quilt to provide fire stopping.

•	 Boxed eaves: Completely seal air paths in plane of separating wall with wire reinforced

mineral wool, not less than 50 mm thick, fixed to rafters and carefully cut to shape to

provide fire stopping.

355A	VENTILATED EAVES  OVER FASCIA VENTILATION SYSTEM

•	 Manufacturer: Contractors choice, provide sample for CA approval.

Product: Proprietary BBA approved over fascia eaves ventilation system in accordance

with BS5250 to provide ventilation to the roof void equivalent to 10000mm2/m.

Ventilators to have internal pin arrangement for resistance to driving rain and large

insects. Install continuously and use gutter bracket spacers where necessary.

•	 Ventilator trays:

-	Manufacturer: Contractors choice, provide sample for CA approval.

Product: Proprietary BBA approved PVC tray compatible with fascia ventilation system.

-	Fix to provide free passage of air over insulation.

•	 Underlay support: Proprietary BBA approved PVC skirt compatible with fascia ventilation

system.

-	Continuous to prevent water retaining troughs.

•	 Gutter: Dress underlay or underlay support tray to form drip into gutter.

•	 Undercourse and first course tiles: Fix with tails projecting 50mm over gutter or to centre of

gutter, whichever dimension is the lesser

360A	VENTILATED ABUTMENT  PROPRIETARY ABUTMENT VENTILATION SYSTEM

•	 Manufacturer: Contractors choice, provide sample for CA approval.

Product: Proprietary BBA approved over fascia eaves ventilation system in accordance

with BS5250 to provide ventilation to the roof void equivalent to 25000mm2/m.

Ventilators to have internal pin arrangement for resistance to driving rain and large

insects. Install continuously in accordance with manufacturer's instructions.

•	 Material : Plastics

•	 Requirements: Lap roofing membrane and provide fillets in accordance with manufacturer's

instructions

405A	DRY VERGES

•	 Underlay: Carry over full width of verge.

•	 Tiling battens: Carry over underlay and project as recommended by dry verge

manufacturer.

•	 Dry verges:

-	Manufacturer: Contractors choice, provide sample for CA approval.  Colour - Black or

Grey.  Aluminium to have PPC finish.

Product : Continuous verge piece/system in PVC / aluminium and compatible with tile

manufacturer.

-	Fixing: Clip / secret fix at regular centres in accordance with manufacturer’s

recommendations.  Individual dry verge tile/pieces will not be acceptable.

615	METAL VALLEYS

•	 Underlay: Cut to rake. Dress over tilting fillets to lap onto metal valley. Do not lay under

metal.

Roof tiles: Cut adjacent tiles to fit neatly.

-	Bedding: On mortar on fibre cement undercloaks laid loose each side of valleys.

Valley width between tiles: - .

660	SIDE ABUTMENTS

•	 Underlay: Turn up not less than 100 mm at abutments.

•	 Abutment tiles: Cut as necessary. Fix close to abutments.

670	TOP EDGE ABUTMENTS

•	 Underlay: Turn up not less than 100 mm at abutments.

•	 Top course tiles: Fix close to abutments.

700A	DRY VENTILATED TILE RIDGES

•	 Underlay: Provide air gap at apex as recommended by ventilator manufacturer.

•	 Dry ridge fixing battens: 50x50mm treated softwood battens and spacers.

•	 Dry ridge tiles:

-	Manufacturer: Contractors choice, provide sample for CA approval.  To be compatible

with tile manufacturer.

Product: Proprietary BBA approved dry mechanically fixed concrete ridge tile with

proprietary ridge ventilation system in accordance with BS5250 to provide ventilation to

the roof void equivalent to 10000mm2/m.

800	CHANGE OF ROOF PITCH

•	 Tiling substrate work: Fix timber tilting fillet to support flashing and course of tiles above

change of pitch.

•	 Roof tiles: Fix courses above and below changes of pitch and make weathertight with

flashing.

840A	VENTILATOR TILES: TO PROVIDE VENTILATION TO ROOF SPACE AS PER

DEVELOPER’S DRAWINGS

•	 Ventilator tiles:

-	Manufacturer:  [Contractor's choice].

•	    Product reference:  [Proprietary in line tile ventilators compatible with roof tiles].

-	Requirement:  [To provide 5mm continuous ventilation at approximately 2000mm c/s].

-	Positions:  [Where required to provide cross ventilation to roof spaces which are divided

by walls carried up to the u/s of the roof covering. Refer to roof plan. Generally to be

provided in horizontal and vertical lines on visibly adjacent roof planes.].

-	Performance Specification - Provide low level/high level roof space ventilation by means

of Tile ventilators with integral 4mm large insect screen and AA fire rating to BS 476:part

3:2004 size/profile to be agreed & approved. to be installed complete with Extension

sleeves and underlay opening protectors. Install as per Architects drawings to provide

the required ventilation area in accordance with the building regulations Approved

H71

Lead sheet coverings/ flashings

H71 Lead sheet coverings/ flashings

To be read with Preliminaries/ General conditions.

TYPES OF LEADWORK

130A	CLADDINGTO DORMER CHEEKS & CANOPIES

•	 Substrate: Marine grade plywood.

-	Preparation: ensure substrate surface is smooth, even, free from holes, projections, grit

and debris.

•	 Underlay: as clause H71/650.

•	 Type of lead: BS EN 12588.

-	Thickness: 2.50 or 2.65 mm (Code 6).

•	 Pretreatment: as Lead Sheet Association guidelines .

•	 Vertical joints: Welted seams. Refer to elevations for jointing appearance.

-	Spacing: 675mm c/s.

•	 Bottom edge detail: Dressed over lead soakers to pitched roof and clipped.

•	 Cross joints: 150 mm laps with terne coated stainless steel clip at centre of each bay.

-	Spacing: Determined by Contractor.

-	Alignment: In line with adjacent bays.

•	 Intermediate fixings: As Lead Sheet Association guidelines.

•	 Head detail: Secured just above soffit cladding to dormer.

•	 Other requirements: Treat with Patination oil.

210A	GUTTER LINING WITH PROPRIETARY EXPANSION JOINTS

•	 Substrate: 19 mm plywood to BS EN 636 on rafters at 400 mm centres.

-	Preparation: None.

•	 Underlay: 220 g/m² needle punched geotextile.

•	 Type of lead: Rolled.

-	Thickness: 1.75-2.00 mm (Code 4).

•	 Pretreatment: Apply thin coating of patination oil to underside of lead and allow to dry

before laying .

•	 Proprietary expansion joints: Neoprene (polychloroprene) and lead .

-	Manufacturer: Contractors choice.

Product reference: Neoprene expansion joint.

-	Spacing: Within 1 m of each corner and maximum centres of 2000 mm.

-	Weld to gutter linings.

•	 Outlets: Chute outlet through wall to hopper head.

322	SOAKERS FOR MITRED HIPS TO SLATE/ PLAIN TILE ROOFS

•	 Lead:

-	Thickness: 1.25-1.50 mm (Code 3).

•	 Dimensions:

-	Length: Slate/ tile gauge + lap + 25 mm.

Underlaps: Not less than 150mm.

325	SOAKERS FOR MITRED VALLEYS TO SLATE/ PLAIN TILE ROOFS

•	 Lead:

-	Thickness: 1.25-1.50 mm (Code 3).

•	 Dimensions:

-	Length: Slate/ tile gauge + lap + 25 mm.

Underlaps: Not less than 150 mm.

410A	APRON FLASHINGSGENERALLY

•	 Lead: BS EN 12588

-	Thickness: 1.75-2.00 mm (Code 4).

•	 Dimensions:

-	Lengths: Not more than 1500 mm.

-	End to end joints: Laps of not less than 100 mm.

-	Upstand: Not less than 75 mm.

-	Cover to abutment: Not less than 300 mm.

•	 Fixing: Clipped at not more than 500 mm centres.

430A	COVER FLASHINGSGENERALLY

•	 Lead:

-	Thickness: 1.75 or 1.80 mm (Code 4).

•	 Dimensions:

-	Lengths: Not more than 1500 mm.

-	End to end joints: Laps of not less than 100 mm.

-	Overlap to upstand: Not less than 50 mm.

-	Cover to roof: Not less than 75 mm.

•	 Fixing: Lead wedges into bed joint, clips to lead upstand at laps and 500 mm centres.

440A	SOAKERS AND STEP FLASHINGSGENERALLY

•	 Lead soakers: BS EN 12588

-	Thickness: 1.75-2.00 mm (Code 4).

-	Dimensions:

Length: Slate/ tile gauge + lap + 25 mm.

Upstand: Not less than 75 mm.

Underlay: Not less than 100 mm.

-	Fixing: By roofer.

•	 Lead step flashings:

-	Thickness: 1.75-2.00 mm (Code 4).

-	Dimensions:

Lengths: Not more than 1500 mm.

End to end joints: Laps of not less than 100 mm.

Cover: Overlap to soaker upstands of not less than 65 mm.

-	Fixing: Lead wedges at every course.

470	FLASHINGSGENERALLY

•	 Lead:

-	Thickness: 1.75 or 1.80 mm (Code 4).

•	 Dimensions:

-	Lengths: Not more than 1500 mm.

•	 Fixing: Fixing: Nail top edge at 150 mm centres and welt edge. Clip bottom edge at laps

and 500 mm centres..

497	LEAD DAMP PROOF COURSE/ CAVITY TRAY AT RAKING ABUTMENTS

•	 Lead:

-	Thickness: 1.75-2.00 mm (code 4).

-	Finish: Fully coated on both sides with high-build, bitumen based paint on the surfaces

which are to be embedded.

•	 Joints:

-	Generally: Lap not less than 50 mm.

-	Where the lead spans a cavity: Lead welded.

•	 Laying: On a thin even bed of wet mortar.

-	Next layer of overlying construction: Bed on mortar without delay and finish joint neatly.

-	Chase in bedding mortar under damp proof course: Rake out to a depth of 25 mm before

fully set, for subsequent fitting of flashing.

GENERAL REQUIREMENTS/ PREPARATORY WORK

510	WORKMANSHIP GENERALLY

•	 Standard: To BS 6915 and latest edition of 'Rolled lead sheet. The complete manual'

published by the Lead Sheet Association.

•	 Fabrication and fixing: To provide a secure, free draining and weathertight installation.

•	 Operatives: Trained in the application of lead coverings/ flashings. Submit records of

experience on request.

•	 Measuring, marking, cutting and forming: Prior to assembly wherever possible.

•	 Marking out: With pencil, chalk of crayon. Do no use scribers or other sharp instruments

without approval.

•	 Bossing and forming: Straight and regular bends, leaving sheets free from ripples, kinks,

buckling and cracks.

•	 Solder: Use only where specified.

•	 Sharp metal edges: Fold under or remove as work proceeds.

•	 Finished work: Fully supported, adequately fixed to resist wind uplift but also able to

accommodate thermal movement without distortion or stress.

Protection: Prevent staining, discolouration and damage by subsequent works.

515	LEADWELDING

•	 In situ leadwelding: Not permitted.

520	LEAD SHEET

•	 Production method:

-	Rolled, to BS EN 12588, or

-	Machine cast, Agrément certified and to code thicknesses with a tolerance (by weight) of

±5%, or

-	Sand cast, from lead free from bitumen, solder, other impurities, inclusions, laminations,

cracks, air, pinholes and blowholes; to code thicknesses but with a tolerance (by weight)

of ±10%.

•	 Identification: Labelled to show thickness/ code, weight and type.

550	LIGHTNING PROTECTION

•	 Lead coverings: Attach the following to a lightning protection system: as required .

-	Electrical continuity: Provide between lead sheets. Discontinuous sections must be

separately bonded.

555	LAYOUT

•	 Setting out of longitudinal and cross joints: Submit proposals.

560	CONTROL SAMPLES

•	 General: Complete areas of the finished work, and obtain approval of appearance before

proceeding:

•	 Size: 1500mm length.

•	 Location: Flashing at horizontal and raking roof wall abutments.

565	MOCK-UP

•	 General: At an agreed stage in the detailed design work construct  a mock-up as follows:

•	 Size: Submit proposals.

•	 Location: Part mock-up to one end of bay roof.

•	 Purpose: To agree final arrangement and appearance of leadwork.

•	 Inspection: Obtain approval of appearance before proceeding. Retain mock-up in

undisturbed condition until completion of lead installation.

610	SUITABILITY OF SUBSTRATES

•	 Condition: Dry and free of dust, debris, grease and other deleterious matter.

630	PLYWOOD UNDERLAY

•	 Standard: Manufactured to an approved national standard and to BS EN 636, section 7

(plywood for use in humid conditions).

•	 Sheet size: 2400 or 1200 x 1200 mm and 6 mm thick.

•	 Moisture content: Not more than 22% at time of covering. Give notice if greater than 16%.

•	 Laying: Cross joints staggered and a 0.5 to 1 mm gap between boards.

•	 Fixing: With 25 mm annular ringed shank copper or stainless steel nails, at 300 mm grid

centres over the area of each sheet and at 150 mm centres along edges, set in 10 mm

from perimeter edges.

Nail heads: Set flush or just below the surface.

640	TIMBER FOR USE WITH LEADWORK

•	 Quality: Planed, free from wane, pitch pockets, decay and insect attack (ambrosia beetle

excepted).

•	 Moisture content: Not more than 22% at time of covering. Give notice if greater than 16%.

•	 Preservative treatment: Organic solvent as section Z12 and British Wood Preserving and

Damp-proofing Association Manual - Commodity Specification C8.

650A	UNDERLAY TO LEADWORK

•	 Type: Contractor's choice to PIFA Standard 6/83A or BBA certified. 220g/m2 needle

punched non-woven polyester geotextile

-	Product reference: -.

•	 Handling: Prevent tears and punctures.

•	 Laying: Butt or overlap jointed onto a dry substrate.

-	Fixing edges: With copper or stainless steel staples or clout nails.

-	Do not lay over roof edges but do turn up at abutments.

•	 Wood core rolls: Fixed over underlay.

•	 Protection: Keep dry and cover with lead at the earliest opportunity.

FIXING LEAD

705	HEAD FIXING LEAD SHEET

•	 Top edge: Secured with two rows of fixings, 25 mm and 50 mm from top edge of sheet, at

75 mm centres in each row, evenly spaced and staggered.

•	 Sheets less than 500 mm deep: May be secured with one row of fixings, 25 mm from top

edge of sheet and evenly spaced at 50 mm centres.

710	FIXINGS

•	 Nails to timber substrates: Copper clout nails to BS 1202-2, or stainless steel (austenitic)

clout nails to BS 1202-1.

-	Shank type: Annular ringed, helical threaded or serrated.

-	Shank diameter: Not less than 2.65 mm for light duty or 3.35 mm for heavy duty.

-	Length: Not less than 20 mm or equal to substrate thickness.

•	 Screws to concrete or masonry substrates: Brass or stainless steel to BS 1210, tables 3 or

4.

-	Diameter: Not less than 3.35 mm.

-	Length: Not less than 19 mm.

-	Washers and plastic plugs: Compatible with screws and lead.

•	 Screws to composite metal decks: Self tapping as recommended by the deck and lead

manufacturer/ supplier for clips.

715	CLIPS

•	 Manufacturer: Fabricated on site.

•	 Material:

-	Lead clips: Cut from sheets of same thickness/ code as sheet being secured.

-	Copper clips:

Thickness: 0.60 mm.

Temper: BS EN 1172, designation R220 in welts, seams and rolls, R240 elsewhere;

dipped in solder if exposed to view.

-	Stainless steel clips:

Thickness: 0.38 mm.

Grade: BS EN 10088, 1.4301(304) terne coated if exposed to view.

•	 Dimensions:

-	Width: 50 mm where not continuous.

-	Length: To suit detail.

•	 Fixing clips: Secure each to substrate with either two screw or three nail fixings not more

than 50 mm from edge of lead sheet. Use additional fixings where lead downstands

exceed 75 mm.

•	 Fixing lead sheet: Welt clips around edges and turn over 25 mm.

760A	CONTINUOUS CLIPS

•	 Material:

-	Lead continuous clips:

Thickness: As that of leadwork being secured.

•	 Dimensions:

-	Width: To suit detail.

•	 Fixing clips: Secure at 200 mm centres.

•	 Fixing lead sheet: Welt edge around continuous clip and dress down.

765	CONTINUOUS CLIPS FOR CROSS JOINTS IN ROOFING

•	 Lead continuous clips: 50 mm wide, cut from sheets of same thickness/ code as sheet

being secured.

•	 Fixing clips: Leadweld top edge of clips to underlap sheet, 50 mm from lower edge of

overlap.

•	 Fixing lead sheet: Welt edge around continuous clip and dress down.

770	WEDGE FIXING INTO JOINTS/ CHASES

•	 Joint/ chase: Rake out to a depth of not less than 25 mm.

•	 Lead: Dress into joint/chase.

-	Fixing: Lead wedges at not more than 450 mm centres, at every change of direction and

with at least two for each piece of lead.

•	 Sealant: As that for movement joints, to be lead compatible.

-	Application: As section Z22.

JOINTING LEAD

810	FORMING DETAILS

•	 Method: Bossing or leadwelding except where   bossing is specifically required.

•	 Leadwelded seams: Neatly and consistently formed.

-	Seams: Do not undercut or reduce sheet thickness.

-	Filler strips: Of the same composition as the sheets being joined.

-	Butt joints: Formed to a thickness one third more than the sheets being joined.

-	Lap joints: Formed with 25 mm laps and two loadings to the edge of the overlap.

•	 Bossing: Carried out without thinning, cutting or otherwise splitting the lead sheet.

Details where bossing must be used: Not applicable .

830	STANDING SEAM JOINTS

•	 Joint allowance: 100 mm overlap, 75 mm underlap and copper or stainless steel clips at

not more than 750 mm centres.

•	 Forming joint: Welt overlap and clips around underlap, loosely turn over to form a standing

seam of consistent cross section.

860	DRIPS WITH SPLASH LAPS

•	 Underlap: Dress into rebate along top edge of drip.

-	Fixing: One row of nails at 50 mm centres on centre line of rebate.

•	 Overlap: Dress over drip and form a 40 mm splash lap.

865	DRIPS WITHOUT SPLASH LAPS

•	 Underlap: Dress into rebate along top edge of drip.

-	Fixing: One row of nails at 50 mm centres on centre line of rebate.

•	 Overlap: Dress over drip to just short of lower level.

970A	PATINATION OIL

•	 Manufacturer: Contractors choice.

-	Product: Proprietary BBA certified patination oil.

•	 Location: All visible leadwork.

•	 Application: As soon as practical, apply a smear coating to lead, evenly in one direction

and in dry conditions.

H72

Aluminium strip/ sheet coverings/ flashings

H72 Aluminium strip/ sheet coverings/ flashings

To be read with Preliminaries/ General conditions.

TYPES OF ALUMINIUM WORK

250A	ALUMINIUM FASCIA TO ENTRANCE DOOR & BAY WINDOW CANOPIES

•	 Substrate: Treated timber framing.

•	 Underlay: 220 g/m² polyester geotextile.

•	 Aluminium: Coated sheet/ strip.  Folded as detailed to create stepped profile. Corner joints

mitred.

-	Alloy designation: EN AW-1200.

-	Temper: H12.

-	Finish: Polyester powder coated. RAL Colour to be confirmed by CA.

-	Thickness: 2.0mm.

•	 Joints: Single lock welt.

-	Spacing: 7 m maximum.

•	 Edge details: Beaded drip at front, upstand at rear with tuck in.

•	 Fixing: Fixed clips at 450 mm centres. Secret fixed where possible.

•	 Other requirements: Provide treated timber packing as necessary.  Seal with suitable

mastic sealant as Z22.

410	APRON FLASHINGSGENERALLY

•	 Aluminium: Coated sheet/ strip.

-	Alloy designation: EN AW-1050A.

-	Temper: O.

-	Finish: Polyvinylidene fluoride (PVDF) coating.

-	Thickness: 0.7 mm.

•	 Dimensions:

-	Lengths: Not more than 2 m, with end to end joints lapped not less than 100 mm.

-	Upstand: Not less than 100 mm.

-	Cover to abutment: Not less than 150 mm.

Bottom edge welted 15 mm.

•	 Fixing: Aluminium wedges into bed joint, clips to bottom edge, at laps and 450 mm centres.

420	COVER FLASHINGS GENERALLY

•	 Aluminium: Coated sheet/ strip.

-	Alloy designation: EN AW-1050A.

-	Temper: O.

-	Finish: Polyester Powder Coated.

-	Thickness: 0.8 mm.

•	 Dimensions:

-	Lengths: Not more than 2 m, with end to end joints lapped not less than 100 mm.

-	Cover to roofing upstand: Not less than 75 mm, with bottom edge welted 15 mm.

•	 Fixing: Aluminium wedges into bed joint, clips to bottom edge, at laps and 450 mm centres

440	SOAKERS AND STEP FLASHINGS GENERALLY

•	 Aluminium: Coated sheet/ strip.

-	Alloy designation:  EN AW-1050A.

-	Temper:  	O.

-	Finish: Polyvinylidene fluoride (PVDF) coating.

-	Thickness: 0.7 mm.

•	 Soakers:

-	Cut and Folded for fixing by roofer.

-	Length: Slate/ tile gauge + lap + 25 mm.

-	Upstand: Not less than 75 mm.

-	Underlap: Not less than 100 mm.

•	 Step flashings:

-	Lengths: Not more than 2 m, with end to end joints lapped not less than 100 mm.

-	Cover: Overlap to soaker upstands not less than 60 mm, with bottom edge welted 15

mm.

Fixing: Aluminium wedges at every course, clips to bottom edge at laps.

GENERAL REQUIREMENTS/ PREPARATORY WORK

510	WORKMANSHIP GENERALLY

•	 Standard: Generally to CP 143-15.

•	 Fabrication and fixing: To provide a secure, free draining and completely weathertight

installation.

•	 Operatives: Trained in the application of aluminium coverings/ flashings. Submit records of

experience on request.

•	 Measuring, marking, cutting and forming: Prior to assembly wherever possible.

•	 Marking out: With pencil, chalk or crayon. Do not use scribers or other sharp instruments

without approval.

•	 Folding: With mechanical or manual presses to give straight, regular and tight bends,

leaving panels free from ripples, kinks, buckling and cracks. Use hand tools only for Folding

details that cannot be pressed.

•	 Surface protection: Fully coat surfaces to be embedded in concrete or mortar with high

build bitumen based paint, after Folding.

•	 Sharp metal edges: Fold under or remove as work proceeds.

•	 Joints: Do not use sealants to attain waterproofing.

•	 Finished aluminium work: Fully supported, adequately fixed to resist wind uplift and able to

accommodate thermal movement without distortion or stress.

-	Protection: Prevent staining, discolouration and damage by subsequent works.

516	WELDING

•	 In situ welding: Permitted subject to completion of a 'hot work permit' form and compliance

with its requirements.

520A	ALUMINIUM STRIP/ SHEET

•	 Standard: To BS EN 485, BS EN 507, BS EN 515 and BS EN 573.

-	Stamped or labelled with alloy designation, temper, finish and thickness.

•	 Manufacturer: Contractors choice, provide sample for CA approval.

525A	COATED ALUMINIUM  STRIP/ SHEET

Standard: To BS EN 485, BS EN 507, BS EN 515 and BS EN 573.

-	Stamped or labelled with alloy designation, temper, finish and thickness. Polyester

powder coated finish.

Manufacturer:  [Contractors choice, provide sample for CA approval].

535	INTEGRITY OF ALUMINIUM

•	 Requirement: Design coverings/ flashings and methods of attachment to prevent loss of

weathertightness and permanent deformation due to wind pressure or suction.

•	 Wind loads: Calculate to BS 6399-2.

555	LAYOUT

•	 Setting out of longitudinal and cross joints: Submit proposals.

560A	CONTROL SAMPLES

•	 General: Complete areas of finished work and obtain approval of appearance before

proceeding:

•	 Location: One canopy for CA and client COW approval.

610	SUITABILITY OF SUBSTRATES

•	 Condition: Dry and free of dust, debris, grease and other deleterious matter.

630	PLYWOOD UNDERLAY

•	 Standard: Manufactured to an approved national standard and to BS EN 636, section 7

(plywood for use in humid conditions).

-	Sheet size: 2400 or 1200 x 1200 mm and 6 mm thick.

•	 Laying: Parallel to perimeter edges with cross joints staggered and a 0.5 to 1 mm gap

between sheets.

•	 Fixing: With 25 mm annular ringed shank aluminium or galvanized steel nails, at 300 mm

grid centres over the area of each sheet and at 150 mm centres along edges, set in 10 mm

from perimeter edges and in pairs across joints.

-	Nail heads: Set flush with or just below surface.

640	TIMBER FOR USE WITH ALUMINIUM WORK

•	 Quality: Planed, free from wane, splits, pitch pockets, decay and insect attack (ambrosia

beetle excepted).

•	 Moisture content: Not more than 22% at time of fixing and covering.

•	 Preservative treatment: Organic solvent as section Z12, and British Wood Preserving and

Damp-proofing Association Manual - Commodity Specification C8.

650	UNDERLAY

•	 Handling: Prevent tears and punctures.

•	 Laying: Butt jointed onto a dry substrate.

-	Fixing edges: With aluminium or galvanized steel staples or 20 x 3 mm extra large head

clout nails.

-	Do not lay over eaves and drip/ step aluminium underlaps.

•	 Ventilation paths: Do not obstruct.

•	 Protection: Keep dry and cover with aluminium at the earliest opportunity.

FIXING

710	FIXINGS FOR CLIPS

•	 Nails to timber substrates: Aluminium to BS 1202-3 for aluminium clips. Stainless steel

(austenitic) for stainless steel clips.

-	Shank type: Annular ringed or helical threaded.

-	Shank diameter: Not less than 2.65 mm.

-	Head: Flat.

-	Length: Not less than 25 mm or equal to substrate thickness.

•	 Screws to concrete/ masonry substrates:  Sherardized or zinc plated steel to BS 1210,

table 2, or aluminium to BS 1210, table 5 for aluminium clips. Stainless steel (austenitic) to

BS 1210, table 4 for stainless steel clips.

-	Diameter: Not less than 3.35 mm.

-	Length: Not less than 25 mm.

-	Washers and plastic plugs: Compatible with screws.

•	 Screws to composite metal decks: Self tapping, as recommended by the deck and

aluminium manufacturer/ supplier for aluminium or stainless steel clips.

720	STANDING SEAM FIXED CLIPS

•	 Aluminium clips: Cut from same alloy and thickness of metal as that being secured.

•	 Stainless steel (austenitic) clips: Cut from same thickness of metal as the aluminium being

secured.

•	 Dimensions:

-	Width: Not less than 50 mm.

-	Base length: Not less than 20 mm.

-	Upstand: To suit standing seam profile.

•	 Fixing: Secure each clip to substrate with two fixings.

725	STANDING SEAM SLIDING CLIPS

•	 Aluminium clips: Cut from same alloy and thickness of metal as that being secured.

•	 Stainless steel (austenitic) clips: Cut from same thickness of metal as the aluminium being

secured.

•	 Dimensions:

-	Fixed component:

Width: Not less than 90 mm.

Base length: Not less than 20 mm.

Upstand: 20 mm, with slot for locating sliding component.

-	Sliding component:

-  Width: Not less than 35 mm.

-  Upstand: To suit standing seam profile.

•	 Fixing: Secure each clip to substrate with three fixings.

760	CONTINUOUS CLIPS

•	 Material: Cut from same alloy and thickness as that being secured.

•	 Dimensions:

-	Width: Sufficient to suit detail.

-	Length: Not more than 1.8 m.

•	 Fixing: To substrate at 150 mm centres. Welt edge of strip/ sheet being fixed to continuous

clip and dress down.

JOINTING

810	FORMING DETAILS

•	 Folds and welts: Form without thinning or splitting the strip/ sheet.

•	 Thermal movement: Form details  with appropriate allowance for movement, without

impairment of security at full expansion or contraction.

860	DRIP/ STEP JOINTS

•	 Strip/ sheet from below step: Fold up full height of upstand and fix to top edge.

•	 Form aluminium underlap/ continuous clip:

-	Cover to roof slope: Not less than 100 mm with anticapillary welt at top edge.

-	Projection: 25 mm for forming into drip welt.

-	Downstand: Not less than 40 mm with welt at bottom edge.

-	Fixing: To roof slope at 100 mm centres, avoiding through fixings at longitudinal joint

positions.

•	 Strip/ sheet from above step: Fold around underlap projection and single welt to form a

drip.

880	SINGLE LOCK WELT JOINTS

•	 Joint allowances: 100 mm overlap and 50 mm underlap.

•	 Underlap: Welt and secure with clips, two per bay.

•	 Overlap: Welt around underlap and clips and dress down.

•	 Forming: Fold welts lightly to allow freedom of movement.

890	DOUBLE LOCK WELT JOINTS

•	 Joint allowances: 90 mm overlap, 60 mm underlap.

•	 Underlap: Welt and secure with clips, one per bay.

•	 Overlap: Double welt around underlap and clips, and dress down.

J

Waterproofing

J10

Cementitious mortar tanking/ damp proofing

J10 Cementitious mortar tanking/ damp proofing

TO BE READ WITH PRELIMINARIES/ GENERAL CONDITIONS

TYPES OF TANKING/ DAMP PROOFING

110A	PROPRIETARY MORTARPROPRIETARY DAMP PROOFING 3 (refer to details

•	 Substrate: concrete / concrete / block slab - refer to details.

•	 Manufacturer: Contractor's choice, BBA approved - provide samples and detailed

specification for CA approval.

-	Product reference: A two component flexible cementitious waterproof coating system

designed for the protection of new and existing structures such as basements, swimming

pools, lift pits, concrete tanks, floors, wet areas (kitchens, bathrooms), small tiled

balconies, planter boxes.  Comprising a liquid polymer and special cement based

powder component, the flexible system offers excellent adhesion to correctly prepared

internal or external concrete, masonry and rendered type surfaces.  It is able to resist

both a positive (30m) and negative (15m) hydrostatic pressure and due to its flexibility is

able to bridge drying shrinkage or hairline cracks.

When used in conjunction with Polymer modified  Mortars, the flexible system is suitable

for protection of basement grades 1, 2 and 3 as defined in BS8102: 2009..

•	 Coats: Refer to tanking manufacturers recommendations

-	Number:  	2 coats

-	Thickness  	0.8 – 1.2mm  	each coat  	(Damp Proofing)

1.3 – 1.7mm  	each coat  	(Hydrostatic Pressure)

•	 Finish: Refer to tanking manufacturers recommendations

•	 Other requirements:  	Service penetrations as necessary, sealed in accordance with

manufacturer's recommendations.

•	 Ancillaries:

-	Polymer Mortar – cementitious mortars for repair / levelling of substrates prior to the

application of BETEC Seal

-	Plug System – quick setting, cementitious waterproof plugging compound

-	Reinforcing Mesh – reinforcing mesh for use where substrate cracking is likely to occur

-	Band Strip-  150mm wide elastomeric tape for use at all designed movement joints,

construction joints and horizontal to vertical joints

MATERIALS AND MAKING OF MORTAR

330	MOVEMENT JOINT SYSTEM

•	 Manufacturer: Contractors choice.

-	Product reference: To be BBA approved / third party accredited and fully compatible with

tanking / damp proofing.

-	Application: As section Z22.

350A	MIXING

•	 Factory-made pre-blended constituents: Mix using methods recommended by the coating

manufacturer.

-Shake liquid (component A) well and pour approximately 75% of the contents into clean

plastic bucket.  Slowly add the powder (component B), mixing with paddle stirrer and slow

speed drill (500-600rpm).  Mix until a homogenous slurry, free from all lumps is formed.

Scrape any unmixed material from sides of bucket with a trowel and mix-in.  Finally add

appropriate amount of the remaining liquid (component A) to achieve the required

consistency for application.  Do not part-mix.  Do not add extra water, cement, sand or

other addition to product.

•	 Mixes: Of uniform consistency and free from lumps.

Free-fall drum mixers: Do not use.

360A	COLD WEATHER

•	 General: Do not use frozen materials or apply coatings to frozen or frost-bound substrates.

•	 Air temperature requirements: Do not apply coatings when at or below 5°C and falling, or

below 3°C and rising.

•	 Temperature of work: Maintain above 5°C until coatings have hardened sufficiently.

-	General:  	Do not use if Part A has been exposed to temperatures below 0°C. Do not

apply coatings to frozen or frost-bound substrates.

-	Air temperature requirements:  		Do not apply coatings when at or below 5°C and

falling, or below 3°C and rising. Maintain temperature of work above 5°C until coatings

have hardened sufficiently.

PREPARING SUBSTRATES

410A	SUITABILITY OF SUBSTRATES

•	 Preparation generally:  	To tanking mortar/ admixture manufacturer's recommendations.

Stability and soundness:  		Free from movement, and loose or weak areas that will

cause failure of tanking.

•	 Key: To achieve firm adhesion of tanking.

•	 Contamination: Free from previous coatings and contaminants including dirt, dust,

efflorescence, mould, oil, paint and plaster.  Cracks, porous patches and other defective

areas subject to water pressure and liable to admit water: Control and seal using

waterproof mortar recommended by the tanking mortar manufacturer.

•	 Holes/ Recesses for fixings (where permitted): Prepared to receive fasteners.

•	 Openings and chases:  		Prepared, including sleeves for pipe penetrations and

chases to receive waterproofing compounds/ sealants.

420	PREPARATION OF MORTAR JOINTS AND CAVITIES

•	 Mortar joints: Rake out to a depth of 12 mm (minimum).

-	Debris: Remove and flush out with water.

-	Fill: Repoint with waterproof mortar to the tanking mortar manufacturer's

recommendations.

•	 Blow holes, cavities, cracks, etc: Remove loose material and fill flush using waterproof

mortar recommended by the tanking mortar manufacturer.

430	TANKING INTEGRITY

•	 Penetrations for fixings, services, etc: Not permitted unless otherwise specified by the

manufacturer .

EXECUTION

510	APPLICATION GENERALLY

•	 Application methods and coating sequence: As recommended by the tanking mortar/

admixture manufacturer to achieve a water resistant structure.

520	JOINTS/ JUNCTIONS AND PENETRATIONS

•	 Abutments, joints and active cracks: Sealed and watertight.

-	Movement joints: Centred over joints in substrate and extended through waterproof

coating and finishes.

-	Daywork joints in successive coatings: Staggered and lapped.

-	Angled joints: Not permitted.

•	 Penetrations: Watertight.

530	APPEARANCE OF TANKING

•	 Render/ Screed coatings: Even and consistent. Free from rippling, hollows, ridges, cracks

and crazing.

-	Accuracy: A true plane, to correct line and level. Walls and reveals plumb and square

with neat arrises

•	 Thin slurry coatings: Consistent and free from hollows, cracks and crazing. Suitable to

receive specified finish.

540	FLATNESS/ SURFACE REGULARITY OF TANKING SCREEDS

•	 Measurement method: From the underside of a 3 m straightedge (between points of

contact) placed anywhere on surface and using a slip gauge to BS 8204-1 or -2 (or

equivalent).

•	 Deviation of surface: Sudden irregularities not permitted.

-	Maximum permissible deviation: as per manufacturer’s recommendations.

550	CURING AND DRYING

•	 General: Prevent premature setting, uneven drying and cracking of each coat.

•	 Curing coatings: Prevent evaporation from surface.

-	Curing period (minimum): As recommended by the tanking mortar/ admixture

manufacturer to achieve a water resistant structure.

560	PROTECTION

•	 Mechanical damage: Prevent impact and abrasion.

•	 Application of protective coatings/ linings: After completion of curing.

J40

Flexible sheet tanking/ damp proofing

J40 Flexible sheet tanking/ damp proofing

To be read with Preliminaries/ General conditions.

110	HARDCORE BEDS

•	 Preparation: Blind with soft sand or pulverized fuel ash.

-	Thickness (minimum): 75.

•	 Finish on completion: Smooth, consolidated bed free of sharp projections.

TYPES OF TANKING/ DAMP PROOFING

140A	LOOSE LAID POLYETHYLENE GAS RETARDANT DAMP PROOFING

•	 Substrate: Concrete slab.

•	 Manufacturer: Contractor's choice.

-	Product reference: Contractor's choice, proprietary multi-layer reinforced polyethylene

membrane with an aluminium core, high levels of tear & impact resistance , to be in

accordance with BBA10/4754.

•	 Thickness/ Gauge: 400 micrometres (2000 gauge).

•	 Joints:

-	Surfaces to be joined: Clean and dry beyond full width of joint.

-	Laps (minimum): 150 mm.

-	Sealing: Bonded with manufacturers compatible double sided butyl adhesive tape (min

50mm wide) between & manufacturers lap tape to exposed edge.

•	 Water Permeability BS3177(g/m2/day): 0.03

•	 Tensile Strength BS2782:Part3:320A (N/mm2): 43.7

•	 Methane Permeability (mls/m2/day): 0.001

•	 Tear Strength BS2782:306B (N/mm): 216

•	 Accessories: Manufacturers recommended compatible (with aforementioned product)

bonding & lapping tapes/ damp proof course/preformed 'top hat' units, jubilee clips, liquid

membranes, detailing strips and appropriate system for sealing corner joints, comprising

self-adhesive tapes or preformed corner units. Tanking to be protected against backfill

material by placement of a robust proprietary bitumen board comprising a hard bitumen

compound coated one side with asphaltic paper.

191A	SELF-ADHESIVE BITUMEN DAMP PROOFING/ TANKING PROPRIETARY DAMP

PROOFING 1 (refer to details)

•	 Substrate: Concrete/Concrete block/slab as detailed.

•	 Primer: Required.

•	 Manufacturer: Contractor's choice, Third Party Accredited - provide sample and detailed

specification for CA approval.

Number of layers: One.

•	 Bonding: Full. Smooth out to exclude air.

•	 Performance :Post-applied self-adhesive sheet membrane waterproofing that forms a bond

to concrete using a Non-Bituminous Adhesive for the following applications:

1.  	Vertical Applications:  Membrane applied against cast in-situ concrete or masonry

below grade earth retaining structures

2.  	Horizontal Applications:  Not suitable for below slab applications. See separate

specification for pre-applied membranes.

•	 Submit manufacturer's product data, installation instructions and membrane samples for

approval.

Reference Standards:

The following standards and publications are applicable to the extent referenced in the text.

American Society for Testing and Materials (ASTM):

1.  	C 836 Standard Specification for High Solids, Cold Liquid-Applied Elastomeric

Waterproofing Membrane for Use with Separate Wearing Course

2.  	D 412 Standard Test Methods for Rubber Properties in Tension

3.  	D 570 Standard Test Method for Water Absorption of Plastics

4.  	D 903 Standard Test Method for Peel or Stripping Strength of Adhesive Bonds

5.  	D 1434 Standard Test Method for Determining Gas Permeability Characteristics of

Plastic Film and Sheeting

6.  	1876 Standard Test Method for Peel Release of Adhesives (T-Peel)

7.  	D 1970 Standard Specification for Self-Adhering Polymer Modified Bituminous

Sheet Materials Used as Steep Roofing Underlayment for Ice Dam Protection

8.  	D 3767 Standard Practice for Rubber - Measurements of Dimensions

9.  	D 5385 Standard Test Method for Hydrostatic Pressure Resistance of

Waterproofing Membranes

10.  	1E 96 Standard Test Methods for Water Vapour Transmission of Materials

11.  	E 154 Standard Test Methods for Water Vapour Retarders Used in Contact with

Earth Under Concrete Slabs, on Walls, or as Ground Cover

•	 Quality Assurance :

1.  	Manufacturer: Sheet membrane waterproofing system shall be manufactured and

marketed by a firm with a minimum of 20 years experience in the production and sales of

sheet membrane waterproofing.  Manufacturers shall submit evidence of ability to meet all

requirements specified, and include a list of projects of similar design and complexity

completed within the past 5 years.

2.  	Installer:  A firm which has at least 3 years experience in work of the type required

by this section.

3.  	Materials:  For each type of material required for the work of this section, provide

primary materials which are the products of one manufacturer.

4.  	Pre-Installation Conference:  A pre-installation conference shall be held prior to

commencement of field operations to establish procedures to maintain optimum working

conditions and to coordinate this work with related and adjacent work.  Agenda for meeting

shall include review of special details and flashing.

5.  	Schedule Coordination:  Schedule work such that membrane will not be left

exposed to weather for longer than that recommended by the manufacturer.

•	 Delivery, Storage & Handling:

Deliver materials in labelled packages.  Store and handle in strict compliance with

manufacturer's instructions.  Protect from damage from weather, excessive temperature

and construction operations.  Remove and dispose of damaged material in accordance

with applicable regulations.

•	 Project Conditions:

Perform work only when existing and forecasted weather conditions are within the limits

established by the manufacturer of the materials used.  Proceed with installation only when

the substrate construction and preparation work is complete and in condition to receive

sheet membrane waterproofing.

•	 Warranty: Sheet Membrane Waterproofing:  Provide written minimum ten year material

warranty issued by the membrane manufacturer upon completion of work.

•	 Materials: Vertical Applications

Self-adhesive water, moisture and gas proofing membrane, of HDPE construction. The

membrane shall white/grey layer with a white surface to easily spot damage prior to

placement of overlying construction.  The membrane is specially formulated to allow

application to _green concrete_

Provide membrane with the following minimum physical properties:

Properties  	Typical Values  		Test Method

Colour  		White

Thickness  		0.8mm

Hydrostatic Head Resistance  	 > 70 m (note 1)  		ASTM D5385-93

Water Vapour Transmission Rate  		 465.000-485.000 (µ=sD/d)  	EN1931

Method B

Methane Permeability  		74.2 ml/m2/day (note 2)  		ISO 7229

Tensile Properties (N/6mm)  	Long 50/Trans 55  		EN 12311-2 Method B

Tensile Properties (Elongation %)  		Long 130/Trans 100  	EN 12311-2 Method B

Nail Shank (N)  		Long 155/Trans 180  	EN12310-1

Footnotes:

Note 1: Test carried out on an overlap crossing a post formed crack.

Note 2: Typical value for BRE recommended minimum standard (BRE Report 212) is 360

ml/m2/day..

•	 Accessories:  Waterstop: Hydrophilic non-bentonite for non-moving concrete construction

joints. Welded PVC waterbar (including a co-extruded hydrophilic bulb) for movement

joints.

•	 Miscellaneous Materials: Tape and other accessories specified or acceptable to

manufacturer of post-applied waterproofing membrane.

A suitable and tested primer supplied by the same manufacturer as the membrane shall be

used.

•	 Execution :

-	The installer shall examine conditions of substrates and other conditions under which

this work is to be performed and notify the Contractor, in writing, of circumstances

detrimental to the proper completion of the work.  Do not proceed with work until

unsatisfactory conditions are corrected.

•	 Installation : Vertical Applications

1.  	Substrates shall be smooth and sound.

2.  	Strictly comply with installation instructions in manufacturer's published literature.

3.  	Apply succeeding sheets by overlapping the previous sheet 75 mm (3 in.) along the

uncoated edge of the membrane.  Side laps must be firmly rolled to ensure a tight seal.

4.  	Overlap the ends of the membrane 75 mm (3 in.).  Apply Tape with the same

adhesive layer as the membrane, centred over the end lap and roll firmly to ensure a tight

seal.  Remove release liner.

-	Protection : Protect membrane in accordance with manufacturer's recommendations

Inspect for damage just prior to placement of protection board or drainage layer.

-	Continuity : Materials and ancillaries including any Bitumen based detailing liquid

membrane and cementitous tie-bolt hole sealant should be sourced from a single

manufacturer.

In addition materials should be fully compatible with any adjoining waterproofing or

weatherproofing systems, to ensure continuity and structural protection.

E.g. Substructure waterproofing to superstructure underlayments.  Accessories: Installed

in accordance with manufacturers guidance .

192A	SELF-ADHESIVE BITUMEN DAMP PROOFING/ TANKING PROPRIETARY DAMP

PROOFING 2 (refer to details)

•	 Substrate: Concrete/Concrete block/slab as detailed.

•	 Primer: Required.

•	 Manufacturer: Contractor's choice, Third Party Accredited - provide sample and detailed

specification for CA approval.

Number of layers: One.

•	 Bonding: Full. Smooth out to exclude air.

•	 Performance :BBA Certified for basements Grades 2, 3 to BS8102: 2009.  Below slab

tanking/ gas retardant membrane to be a pre-applied, flexible, multi-layered composite

sheet membrane comprising a thick white HDPE film, highly aggressive pressure sensitive

adhesive and a weather resistant protective coating layer.  The membrane shall provide a

passive protection system that does not rely upon hydration processes or swell in contact

with water.  An intimate bond is to be formed to the poured in-situ structural concrete by

means of a pressure sensitive adhesive preventing lateral water and moisture migration

between the membrane and structure.

The membrane is to be chemically resistant in all types of soil or water and protect the

structure from salt and sulphate attack.  It shall be tested to withstand a 70m head of

water, have a zero permeance to moisture, not activate prematurely due to wet conditions

and be unaffected by ground settlement beneath slabs.  The physical characteristics must

ensure that protection against Methane, CO2 and Radon are in excess of the minimum

requirements stated in BRE Reports 'Construction of new buildings on gas-contaminated

land' (BR 212) and 'Radon: guidance on protective measures for new dwellings' (BR 211).

•  Substrate preparation :  		Substrate must be regular and smooth with no gaps or

voids greater than 12mm.  A sound solid substrate should be created to eliminate

movement during the concrete pour.  Vertically the membrane can be applied to

permanent formwork, rigid insulation and the adjoining structure or as recommended by

the manufacturer.

•  Thickness:  	0.8mm  		ASTM D3767 Method A

•	 Bonding:  	Fully bonds to the poured in-situ structural concrete by means of a pressure

sensitive adhesive.  Apply membrane with disposable plastic release liner uppermost.  End

laps should be staggered to avoid build up of layers.  Plastic release liner to remain in

position until overlap procedure is complete.  Roll all laps to ensure good adhesion

between sheets, in accordance with manufacturers recommendations.

•  Joints:  Side and end laps to be a minimum of 75mm.  Accurately position sheets to

overlap previous sheet along indicated adhesive selvedge, ensure a continuous bond is

achieved without creases and roll firmly.  For roll ends, cut edges and for providing

continuity of waterproofing at penetrations and detailing employ pressure sensitive

adhesive tape.  End laps to be staggered to avoid a build up of layers.

•	 Sealing:  	Not required.

•	 Ancillaries:

-	Detailing Liquid.  Two component elastomeric, cold applied liquid compound, is to cure

to forming a tough seamless rubber-like waterproof layer.  The liquid shall conform to

irregular profiles and be suitable for detailing curved, irregular or stepped profiles, pile

penetrations, internal corners, flashing round drains, gullies, pipe entries and edge

sealing at terminations..

-	Bonding Tape shall have an highly aggressive, pressure sensitive adhesive layer for

over banding cut edges, roll ends, penetrations and detailing continuity.

-	Waterstops To be from the membrane manufacturers range of passive or active

Waterstops for expansion joints and additional protection at construction joints providing

single point responsibility (see section E40 clause 310)

•	 Accessories: Installed in accordance with manufacturers guidance .

WORKMANSHIP

310	WORKMANSHIP GENERALLY

•	 Condition of substrate:

-	Clean and even textured, free from voids and sharp protrusions.

-	Moisture content: Compatible with damp proofing/ tanking.

•	 Air and surface temperature: Do not apply sheets if below minimum recommended by

membrane manufacturer.

•	 Condition of membrane at completion:

-	Neat, smooth and fully supported, dressed well into abutments and around intrusions.

-	Completely impervious and continuous.

-	Undamaged. Prevent puncturing during following work.

•	 Permanent overlying construction: Cover membrane as soon as possible.

320A	INSPECTION

•	 Give notice: Before covering any part of membrane with overlying construction.

Membrane to be inspected for damage before installation of protection board,

reinforcement steel, shuttering, insulation and final placement of concrete.  Check for signs

of rips/tears visible.  Repairs to be in accordance with manufacturers recommendations.

Ensure plastic release liner has been removed from all areas of membrane and Tape prior

to covering.

335A	PRIMERS

•	 Manufacturer: Contractor's choice - provide sample for CA approval.

-	Product : Proprietary BBA approved Primer.

•	 Coverage per coat (minimum): As recommended for the purpose by membrane

manufacturer.

•	 Curing: Allow to dry thoroughly before covering.

345	COLD APPLIED BONDING COMPOUNDS

•	 Type and application: As recommended for the purpose by the membrane manufacturer.

350A	ANGLES IN BONDED DAMP PROOFING/ TANKING

•	 Internal angles may be formed by Bituthene® LM or as recommended by the

manufacturer.

•	 Reinforce all angles with a strip of the specified damp proofing material, not less than

300mm wide, applied before the main sheeting.

•	 Continue main sheeting around angles, extending not less than 150mm on to adjacent

surfaces.

370A	PREFORMED COLLARS FOR PIPES, DUCTS, CABLES, ETC.

•	 Manufacturer: Contractor's choice - provide sample for CA approval.

-	Product : Proprietary BBA approved collars with Liquid Membrane & self-adhesive Tape

as necessary.

-	Sealing: Fully bond to penetrations and sheeting.

•	 Completed junctions: Impervious.

380B	PROTECTION BOARDS FOR DAMP PROOFING/ TANKING GENERALLY

•	 Manufacturer: Contractor's choice - provide sample for CA approval.

-	Product : Proprietary BBA approved Protection Board from a suitable range of boards

and sheets designed for the protection of damp proof membranes compatible with Damp

Proofing types.

•	 Thickness: 3 mm - lightweight, rot resistant membrane protection board printed with the

manufacturers logo to aid identification.  Comprising a hard bitumen compound coated one

side with asphaltic paper and one side with polyethylene film..

•	 Application: Membrane surface clean and free from contaminants.

-	Bonding: Primer as recommended by manufacturer.

-	Board joints: Overlap boards by 75 mm minimum and prime lap with Primer and allow to

dry. Tape joints , 70 mm single sided adhesive tape and roll well to achieve full adhesion.

-	Board contact with membrane: Secure and continuous.

•	 Backfilling: Carry out when tanking, loading and protection are complete

•	 Performance : The System protection boards made from selected aggregates bound with

bitumen, laminated between two rough asphaltic papers.  Designed for use vertically in

deep excavations or protection against abrasive backfill.

A range of high performance closed cell, extruded polystyrene insulation boards with lap

jointed edges to provide both impact protection and thermal insulation to basement and

cavity walls.

•	 Vertical Drainage Sheets externally placed, high flow, rot proof, prefabricated

geocomposite drainage sheets for reducing hydrostatic pressure against basement walls

protected with compatible membrane systems from the same manufacturer.

•	 Protection against backfill material: Cover tanking against which backfill material will be

placed with either Protection Board Insulation or Vertical Drainage Sheets or a combination

of all.

•	 Product reference: Protection Board  Extruded Insulation  Vertical Drainage Sheets

•	 Support: Protection must remain fully in contact with tanking and must not move during

backfilling..

J42

Single layer polymeric sheet roof coverings

J42 Single layer polymeric sheet roof coverings

To be read with Preliminaries/ General conditions.

TYPES OF COVERING

115A	SINGLE PLY WARM ROOF COVERINGEPDM MEMBRANE TO ENTRANCE CONOPIES

AND APARTMENT FLAT ROOF

•	 Substrate: Plywood deck.

-	Preparation: Not required.

-	Lower protective layer (loose laid): Polyester fleece separating layer as recommended

by manufacturer.

-	Vapour control layer: Installed on top of insulation board and compatible with

waterproofing membrane and fitting in accordance with manufacturers recommendations

and instructions.

-	Insulation: Rigid PIR as per 420A .

-	Separating layer (loose laid): To be provided as recommended by manufacturer /

contractor.

-	Waterproof membrane: Ethylene propylene diene monomer (EPDM) - non-penetrating

mechanically attached.  Reinforced mechanically anchored system with proprietary self-

adhesive strip mechanically fixed EPDM seam to accept large EPDM panels. Contractor

to provide proposals in relation to wind loadings and perimeter zone panels & seaming.

Provide additional seams as necessary for protective walkway pads / covering.

Manufacturer: Contractors choice, provide sample for CA approval. Provide 25yr

guarantee.

Thickness: 1.5 mm.

Colour: Medium grey / Black - provide samples for CA approval.

-	Upper protective layer (loose laid): Determined by contractor.

•	 Surface protection: Membrane walkways.

•	 Accessories: Edge trims and pipe collars.

116A	SINGLE PLY MEMBRANE WALKWAYSEPDM PROTECTIVE WALKWAY OVER ROOF

MEMBRANE FOR MAINTENANCE ACCESS

•	 Substrate: EPDM Membrane.

-	Preparation: Clean and prime EPDM membrane using proprietary tools and products in

accordance with manufacturer's recommendations.

-	Walkway membrane: Proprietary non-slip protective ethylene propylene diene monomer

(EPDM) walkway pad / covering compatible with roofing membrane.  Pads to have factor

applied proprietary self-adhesive tape. Contractor to provide proposals in relation to wind

loadings and perimeter zone panels & seaming.

Manufacturer: Contractors choice, provide sample for CA approval. Provide 25yr

guarantee.

Thickness: 7.5 mm.

Pad size: approx. 760x760mm

Colour: Medium grey / Black - provide samples for CA approval.

-	Upper protective layer (loose laid): Determined by contractor.

•	 Other requirement: Pads to be spaced in accordance with manufacturer's

recommendations - min spacing approx.25mm, max spacing approx.150mm.

PERFORMANCE

210	ROOF PERFORMANCE

•	 Roof covering: Secure, free draining and weathertight.

220	VAPOUR CONTROL LAYER

•	 Interstitial condensation risk of roof: Determine as recommended in BS 6229. Modify

calculation method to conform to BS 5250.

•	 Basic design data:

-	Outdoor notional psychrometric conditions, winter:

Temperature: -5°C.

Relative humidity: 90%.

Vapour pressure: 0.36 kPa.

Duration: 60 days.

-	Outdoor notional psychrometric conditions, summer:

Temperature: 18°C.

Relative humidity: 65%.

Vapour pressure: 1.34 kPa.

Duration: 60 days.

-	Indoor notional psychrometric conditions:

Temperature: 20ºC.

Relative humidity: 55%.

Vapour pressure: 1.28 kPa.

•	 Winter interstitial condensate:

-	Calculated amount (maximum): 0.35 kg/m².

-	Calculated annual net retention: Nil.

•	 Vapour control layer: If calculated amounts of condensate exceed allowed amounts,

provide a suitable membrane or sealed deck so that damage and nuisance from interstitial

condensation do not occur.

PRODUCTS

330	TIMBER TRIMS, ETC

•	 Quality: Planed. Free from wane, pitch pockets, decay and insect attack except ambrosia

beetle damage.

•	 Moisture content at time of covering (maximum): 22%.

•	 Preservative treatment: As recommended for purpose by waterproof covering

manufacturer.

345A	PERIMETER TRIMS

•	 Type: 0.6 mm galvanized steel with 0.5 mm unreinforced EPDM membrane laminate.

•	 Manufacturer: Contractors choice, provide samples for CA approval.

-	Product : To PIFA Standard 6/83A or Agrément certified.

•	 Colour: Medium grey.

•	 Size: As detailed and as necessary, refer to details.

355A	MECHANICAL FASTENERS, WASHERS, PRESSURE PLATES, ETC

•	 Type: Class 2 point fastener.

•	 Manufacturer: As roof covering or compatible.

Product: To PIFA Standard 6/83A or Agrément certified.

360A	PLYWOOD OVERLAY TO INSULATION GENERALLY

•	 Plywood: To BS EN 636, section 8 (plywood for use in exterior conditions - Marine grade).

-	Quality: Naturally durable timber, free from preservatives.

•	 Thickness: 18mm.

395A	VAPOUR CONTROL LAYER GENERALLY TO INTERNAL FACE OF ROOF / CEILING

INSULATION

•	 Type: Proprietary BBA approved triple ply breather membrane with with non-woven

polypropylene core and high purity solid corrosion resistant aluminium layer with a thermal

resistance of 0.78W/m2K and a hemispherical emissivity of 0.05. To have Class 1 surface

spread of flame.

•	 Manufacturer: Contractors choice, provide sample for CA approval.

-	Fitting: In accordance with BS5250 & BS9250.  Aluminium foil facing to airpace to create

low emissivity air gap. To be fully lapped and sealed with proprietary compatible tape in

accordance with manufacturers instructions.

•	 Vapour resistance: 589 MNs/g.

420A	RIGID PIR WARM ROOF INSULATION LAID TO FALLS ON TIMBER JOISTS TO FLAT

ROOF CANOPIES

•	 Insulation:  [High performance rigid thermoset polyisocyanurate (PIR) insulant

manufactured with a blowing agent that has zero Ozone Depletion Potential (ODP) and

Global Warming Potential (GWP) of less than 5 in accordance with the requirements of BS

4841-1. ].

-	Standard:  [BS EN 13165].

-	Product certification:  [To be BBA and IAB certified for this application. BS EN ISO 9001:

2000/IS EN ISO9001:2008.  To be installed in accordance with the manufacturer's

instructions].

•	 Manufacturer:  [Contractor's choice, sample to be provided for CA approval].

•	 Face size (length x width):  [1200 x 450 mm].

Thickness (nominal):  [50-60mm].

•	 Thermal conductivity:  [Aged - 0.022 W/mK].

•	 Reaction to fire class:  [Class 1 fire rating on both core and facings, producing less than

5% smoke obscuration when tested to BS 5111-1:1974 low risk].

•	 Additional requirements:  [To be highly resistant to transmission of water vapour (more

than 100MN.s/g) and air movement in accordance with BS EN 12086.  Compressive

strength typically in excess of 125 kPa at 10% compression when tested to BS EN 826: 1996

(Thermal insulating products for building applications. Determination of compression

behaviour) ].

•	 Placement: Secure with no gaps on top of timber joists.

•	 Joints between boards, at closures and penetrations: No gaps and free from debris.

425A	MINERAL WOOL WARM ROOF INSULATION FULL FILL BETWEEN JOISTS OF FLAT

ROOF CANOPIES

•	 Standard: Roofing grade to BS EN 13162.

•	 Manufacturer: Contractor's choice, provide sample for CA approval.

-	Product: Full fill mineral fibre packed between joists to BS EN 13162:2001. To be BBA

and IAB certified for this application. BS EN ISO 9001: 2000/IS EN ISO9001:2008.

Manufactured with a blowing agent that has zero Ozone Depletion Potential (ODP) and

Global Warming Potential (GWP) of less than 5 in accordance with the requirements of

BS 4841-1. To be installed in accordance with the manufacturer's instructions.

•	 Density: 135-180 kg/m³.

•	 Thickness: 100 mm.

•	 Facing: Glass tissue.

426A	RIGID PIR INSULATION TO INTERNAL FACE  INTERNALLY TO UNDERSIDE OF FLAT

ROOF CANOPIES AT BAY WINDOW

•	 Insulation:  [High performance rigid thermoset polyisocyanurate (PIR) insulant

manufactured with a blowing agent that has zero Ozone Depletion Potential (ODP) and

Global Warming Potential (GWP) of less than 5 in accordance with the requirements of BS

4841-1. ].

-	Standard:  [BS EN 13165].

-	Product certification:  [To be BBA and IAB certified for this application. BS EN ISO 9001:

2000/IS EN ISO9001:2008.  To be installed in accordance with the manufacturer's

instructions].

•	 Manufacturer:  [Contractor's choice, sample to be provided for CA approval].

•	 Face size (length x width):  [1200 x 450 mm].

Thickness (nominal):  [25mm].

•	 Thermal conductivity:  [Aged - 0.022 W/mK].

•	 Reaction to fire class:  [Class 1 fire rating on both core and facings, producing less than

5% smoke obscuration when tested to BS 5111-1:1974 low risk].

•	 Additional requirements:  [To be highly resistant to transmission of water vapour (more

than 100MN.s/g) and air movement in accordance with BS EN 12086.  Compressive

strength typically in excess of 125 kPa at 10% compression when tested to BS EN 826: 1996

(Thermal insulating products for building applications. Determination of compression

behaviour) ].

•	 Placement: Secure with no gaps on top of timber joists.

•	 Joints between boards, at closures and penetrations: No gaps and free from debris.

EXECUTION GENERALLY

510	ADVERSE WEATHER

•	 General: Do not lay membrane at temperatures below 5°C or in wet or damp conditions

unless effective temporary cover is provided over working area.

•	 Unfinished areas of roof: Keep dry and protect edges of laid membrane from wind action.

520	INCOMPLETE WORK

•	 End of working day: Provide temporary seal to prevent water infiltration.

•	 On resumption of work: Cut away tail of membrane from completed area and remove from

roof.

SUBSTRATES/ VAPOUR CONTROL LAYERS/ WARM ROOF INSULATION

610	SUITABILITY OF SUBSTRATE

•	 Surfaces to be covered: Firmly fixed, clean, dry, smooth, free from frost, contaminants,

voids and protrusions.

•	 Preliminary work: Complete, including

-	Grading to correct falls.

-	Formation of upstands, kerbs, box gutters, sumps, grooves, chases and expansion

joints.

-	Fixing of battens, fillets and anchoring plugs/ strips.

•	 Moisture content and stability of substrate: Must not impair integrity of roof.

660	JOINTS IN RIGID BOARD SUBSTRATES

•	 Cover strip: Lay centrally over substrate joints before laying vapour control layers or

coverings. Adhere to substrate with bonding compound along edges only.

670	LAYING VAPOUR CONTROL LAYER

•	 Laying: Sheets loose, flat and smooth.

•	 Side and head laps: 150mm. Seal using materials and method recommended by

membrane manufacturer.

•	 Upstands, kerbs and other penetrations: Enclose edges of insulation. Fully seal at

abutment by bonding or taping.

680	LAYING WARM ROOF INSULATION

•	 Setting out:

-	Long edges: Fully supported and running at right angles to structure.

-	End edges: Adequately supported.

-	Joints: Butted together.

-	End joints: Staggered.

•	 Attachment: Not required.

•	 Mechanical fixing: Determined by contractor.

•	 Completion: Boards must be in good condition, well fitting and firmly fixed.

WATERPROOF COVERINGS/ ACCESSORIES

710A	MECHANICAL FIXING OF WATERPROOF MEMBRANE GENERALLY

•	 Setting out: Perpendicular to the deck direction.

•	 Laying: Loose lay, do not wrinkle or stretch.

•	 Installing fasteners:

-	Use manufacturer's recommended methods and equipment.

-	Insertion: Correct and consistent.

•	 Washers/ Pressure plates/ Bars:

-	Distance from fixed edge (minimum): 10 mm.

-	Fixing: Flush with membrane.

•	 Sheet overlaps: Extend beyond washers/ pressure plates by minimum 50 mm.

•	 Surface condition at completion: Fully sealed, smooth, weatherproof and free draining.

730	WELDED JOINTING

•	 Laying: Loose lay, do not wrinkle or stretch.

•	 Side and end joints:

-	Laps (minimum): 50 mm.

-	Preparation: Clean and dry surfaces for full width of joint.

-	Sealing: Weld together.

•	 Condition at completion: Fully sealed, smooth, weatherproof and free draining.

•	 Accessories: Even bead of liquid PVC to each joint.

740	ADHESIVE JOINTING

•	 Side and end joints:

-	Laps (minimum): 50 mm.

-	Preparation: Prime, clean and dry surfaces for full width of joint and lap.

-	Sealing: Apply continuous even coverage of adhesive to both surfaces. Mate and roll

together. Do not wrinkle or stretch membrane.

•	 Condition of membrane at completion: Fully sealed, weatherproof and free draining.

•	 Accessories: As necessary.

750	TAPE JOINTING

•	 Side and end joints:

-	Laps (minimum): 50 mm.

-	Preparation: Prime, clean and dry surfaces for full width of joint.

-	Sealing: Apply self-adhesive tape. Mate and roll together. Do not wrinkle or stretch

membrane.

•	 Condition of membrane at completion: Fully sealed, weatherproof and free draining.

760	PERIMETER OF MEMBRANE

•	 General: Secure membrane at roof edge conditions, changes of plane, curb flashings,

upstands to roof lights, etc. with mechanical fasteners.

SURFACING

810	LAYING INVERTED ROOF INSULATION

•	 Condition of substrate: Clean.

•	 Setting out: Loose lay with staggered joints. Minimize cutting and avoid small cut pieces at

perimeters and penetrations.

-	Joints: Butt together.

•	 Projections, upstands, rainwater outlets, etc: Cut insulation cleanly and fit closely around.

•	 Completion:

-	Boards to be in good condition, well fitting and stable.

Cover to prevent wind uplift and flotation as soon as practicable.

COMPLETION

910	INSPECTION

•	 Interim and final roof inspections: Submit roof covering manufacturer's reports.

940	COMPLETION

•	 Roof areas: Clean.

-	Outlets: Clear.

•	 Work necessary to provide a weathertight finish: Complete.

•	 Storage of materials on finished surface: Not permitted.

•	 Completed membrane: Do not damage. Protect from traffic and adjacent or high level

working.

K

Linings/Sheathing/Dry partitioning

K10

Plasterboard dry linings/ partitions/ ceilings

K10 Plasterboard dry linings/ partitions/ ceilings

To be read with Preliminaries/ General conditions.

TYPES OF DRY LINING

205A	LINING ON TIMBER INTERNAL STUD PARTITIONS GF & FF

•	 Background: Studs at 400 mm centres.

•	 SW timber stud: REFER TO DRAWINGS- 400mm CNTRS.

•	 Linings: 89mmx50mm SW timber studs unless otherwise specified by structural engineer.

Finish with 15mm impact resistant plasterboard 408A and skim finish on both sides.

Internal plasterwork to BS5492 and workmanship generally to BS8000 Pt.10..

-	Fixing: Screws.

•	 Finishing: Skim coat plaster.

-	Primer/ Sealer: Primer to painted areas.

-	Accessories: Metal beads/ stops recommended by board manufacturer .

•	 Other requirements: Fire stopping around service penetrations as section P12. Acoustic

quilt as section P10 to be fixed between studs around kitchens, bathrooms & WC's.

205B	LINING ON TIMBER PARTY WALLS

•	 Background: Studs at 400 mm centres.

•	 SW timber stud: REFER TO PARTY WALL DETAIL- 400mm CNTRS.

•	 Linings: 89 X 50mm SW timber studs unless otherwise specified by structural engineer.

Detail is achieved by a multi-layer of plasterboard and OSB board.

8mm OSB

19mm plasterboard as 401A

Layer of thermal foil

12.5mm plasterboard as 401B

Service zone created by 35 x 50mm SW batten fixed back to timber frame

15mm impact plasterboard refer to clause 408A

- skim finish to both sides. Internal plasterwork to BS5492 and workmanship generally to

BS8000 Pt.10..

-	Fixing: Contractor's choice.

•	 Finishing: Skim coat plaster.

-	Primer/ Sealer: Primer to painted areas.

-	Accessories: Metal beads/ stops recommended by board manufacturer .

•	 Other requirements: Fire stopping around service penetrations as section P12. Acoustic

quilt to be fixed between studs around bathrooms & WC's.

205C	LINING ON TIMBER EXTERNAL WALLS

•	 Background: Studs at 400 mm centres.

•	 SW timber stud: REFER TO EXT WALL DETAIL- 400mm CNTRS.

•	 Linings: 89 X 50mm SW timber studs unless otherwise specified by structural engineer.

Detail is achieved by a multi-layer of plasterboard and OSB board.

From inside of timber frame

Layer of thermal vapour barrier THERMAL RESISTANCE OF 0.64 M²K/W

25mm foil faced PIR insulation - MIN LAMBDA VALUE - 0.022

Service zone created by 35 x 35mm SW batten fixed back to timber frame

15mm impact plasterboard refer to clause 408A

- skim finish. Internal plasterwork to BS5492 and workmanship generally to BS8000 Pt.10..

-	Fixing: Contractor's choice.

•	 Finishing: Skim coat plaster.

-	Primer/ Sealer: Primer to painted areas.

-	Accessories: Metal beads/ stops recommended by board manufacturer .

•	 Other requirements: Fire stopping around service penetrations as section P12..

245A	CEILING LINING ON TIMBERGF Ceiling of all Houses - refer to details

-  	Background: Timber Joists.

-  	Linings: 15mm moisture resistant gypsum plasterboard throughout as 403A -

minimum mass of 10kg/m3.

-  	Fixings: As clause 610 with screws.

-  	Finishing: Taped joints as necessary with 8mm Bonding & 2mm Skim finish.

-  	Primer/ Sealer: ceiling may require to be primed dependant on the board proposed

by the contractor.

-  	Accessories:  Proprietary galvanised steel expanded metal plaster corner beads to

all external corners.

-  	Other requirements: Ceiling and floor construction to achieve minimum 1/2 HR fire

resistance.

245B	CEILING LINING ON TIMBER (NON ENHANCED) FF Ceiling of all 3 storey Houses -

refer to details

-  	Background: Timber Joists. with a Polythene Vapour barrier sealed & taped

-  	Linings: 15mm moisture resistant gypsum plasterboard throughout as 403A -

minimum mass of 10kg/m3.

-  	Fixings: As clause 610 with screws.

-  	Finishing: Taped joints as necessary with 8mm Bonding & 2mm Skim finish.

-  	Primer/ Sealer: ceiling may require to be primed dependant on the board proposed

by the contractor.

-  	Accessories: Proprietary galvanised steel expanded metal cove formers to changes

of warm roof pitches. Proprietary galvanised steel expanded metal plaster corner beads to

all external corners.

-  	Other requirements:  Refer to detail for continuous support required for the future

hoist.

245C	CEILING LINING ON TIMBER (ENHANCED) FF Ceiling of 2 storey Houses & SF Ceiling

of 3 storey Houses - refer to details

-  	Background: Timber Joists. with a Polythene Vapour barrier sealed & taped

-  	25mm foil faced insulation (MIN LAMBDA VALUE - 0.022)

-  	35 x 35mm SW batten to create service zone - screwed back to the ceiling joists

-  	Linings: 12.5mm moisture resistant gypsum plasterboard throughout as 403A.

-  	Fixings: As clause 610 with screws.

-  	Finishing: Taped joints as necessary with 8mm Bonding & 2mm Skim finish.

-  	Primer/ Sealer: ceiling may require to be primed dependant on the board proposed

by the contractor.

-  	Accessories: Proprietary galvanised steel expanded metal cove formers to changes

of warm roof pitches. Proprietary galvanised steel expanded metal plaster corner beads to

all external corners.

Other requirements: Refer to detail continuous support required for the future hoist.

255	ENCASEMENT SYSTEM (METAL FRAMING)AS NECESSARY TO STEEL COLUMNS

AND BEAMS

•	 Manufacturer: Contractor's choice - provide samples for CA approval.

-	Product reference: Gypsum based board suitable for direct finishing.

•	 Structural members: As required.

-	Extent of protection: Throughout.

•	 Fire performance:

-	Protection to structural steel: To BS 476-21, 60 minutes, refer to drawings.

•	 Framing system: Sizes and spacing of framing and fixings as recommended by the board

manufacturer.

•	 Linings: As required.

•	 Finishing: Taped seamless finish, as clause 670 or Skim coat plaster finish as clause 680

refer to finishes schedule.

-	Primer/ Sealer: Refer to finishes schedule.

-	Accessories: Rigid beads/ stops, as clause 692.

•	 Other requirements: Fixing as clause 455.

275	ENCASEMENT ON TIMBER FRAMINGTO STEEL BEAMS

•	 Timber framework: 44 x 44 mm with noggings at 600 mm maximum centres..

•	 Linings: Two layers 15mm fire resisting plasterboard to achieve 1 hr fire protection, with

joints staggered.

-	Fixing: Screws.

•	 Finishing: Skim coat plaster.

-	Primer/ Sealer: Primer to painted areas.

-	Accessories: Metal beads/ stops recommended by board manufacturer .

•	 Other requirements: Plan dimensions of casings to be the same for all columns.

GENERAL/ PREPARATION

305	COMPLIANCE WITH PERFORMANCE REQUIREMENTS

•	 Testing/ Assessment: Submit UKAS accredited laboratory reports for the following: Fire

resistance: Partitions (including deflection heads and doorsets) and suspended ceilings

(including access units)..

•	 Materials, components and details: As used in testing/ assessment reports. If

discrepancies arise, give notice.

335	ADDITIONAL SUPPORTS

•	 Framing: Accurately position and securely fix to give full support to:

-	Partition heads running parallel with, but offset from main structural supports.

-	Fixtures, fittings and service outlets. Mark framing positions clearly and accurately on

linings.

-	Board edges and lining perimeters, as recommended by board manufacturer to suit type

and performance of lining.

375	NEW WET LAID BASES

•	 Dpcs: Install under full width of partitions/ freestanding wall linings.

Material: Bituminous sheet or plastics.

COMPONENTS

401A	GYPSUM DENSE PLASTERBOARD PROPRIETARY ACOUSTIC RATED BOARD

•	 Type: To EN 520:2004, type A.

-	Core density (minimum): 15 kg/m³ - 19mm.

-	Thermal conductivity - 0.19W/mK

-	Class '0' spread of flame

•	 Exposed surface and edge profiles: Suitable to receive specified finish.

403A	GYPSUM PLASTERBOARD (MOISTURE RESISTANT CEILINGS)

•	 Type: To To EN 520:2004, type A, D & H1.

-	Core density (minimum): 8.6 kg/m³ - 12.5mm

-	Core density (minimum): 10.1 kg/m³ - 15mm

-	Core: Moisture resistant.  Suitable for kitchen and bathroom installations.

-	Paper facings: Moisture resistant.

-	Refer to details from thickness required

•	 Exposed surface and edge profiles: Suitable to receive specified finish.

404A	GYPSUM PLASTERBOARD (FOR IMPROVED FIRE PROTECTION)

•	 Type:  To EN 520:2004, type F.

-	Core density (minimum): 9.8 kg/m³ - 12.5mm

-	Core density (minimum): 11.7 kg/m³ - 15mm

-	Core: Including fibres for improved cohesion.

•	 Exposed surface and edge profiles: Suitable to receive specified finish.  Use moisture

resistant fire protection board as necessary in kitchen and bathroom areas.

405	PLASTERBOARD GENERALLY

•	 To BS 1230-1, types 1 to 5 with exposed surface and edge profiles suitable to receive the

specified finish.

408A	GYPSUM PLASTERBOARD (IMPACT RESISTANT)

•	 Type: To EN 15283-2, Part 2.

-	Core density (minimum): 1200kg/m³.

-	Flexural strength >/ 6.7 N/mm2

-	Paper facings: Heavy duty.

•	 Surface hardness: minimum Brinell hardness 35N/mm2.

•	 Exposed surface and edge profiles: Suitable to receive specified finish.

430	ACCESS PANELS Boiler Flue Inspection Panels

•	 Type: 60 minutes fire protection, to BS 476-22 .

-	Sizes: 550 x 550 mm .

•	 Frame: Bead for taping and jointing .

•	 Panel: Metal with powder coated factory finish .

•	 Lock: Tamper proof and operated by castellated key .

INSTALLATION

435	DRY LININGS GENERALLY

•	 General: Use fixing, jointing, sealing and finishing materials, components and installation

methods recommended by board manufacturer.

•	 Cutting plasterboards: Neatly and accurately without damaging core or tearing paper

facing.

-	Cut edges: Minimize and position at internal angles wherever possible. Mask with bound

edges of adjacent boards at external corners.

•	 Fixings boards: Securely and firmly to suitably prepared and accurately levelled

backgrounds.

•	 Finishing: Neatly to give flush, smooth, flat surfaces free from bowing and abrupt changes

of level.

445	CEILINGS

•	 Sequence: Fix boards to ceilings before installing dry lined walls and partitions.

•	 Orientation of boards: Fix with bound edges at right angles to supports and with ends

staggered in adjacent rows.

•	 Two layer boarding: Stagger joints between layers.

465	STAGGERED STUD PARTITIONS

•	 Horizontal frame members (noggins, bearers, etc.) and boards: Fix between alternate

studs and not touching adjacent offset studs.

505	INSTALLING MINERAL WOOL INSULATION

•	 Fitting insulation: Closely butted joints and no gaps. Use fasteners to prevent slumping or

displacement.

•	 Services:

-	Electrical cables overlaid by insulation: Sized accordingly.

-	Ceilings: Cut insulation around electrical fittings, etc.

510	SEALING GAPS AND AIR PATHS

•	 Location of sealant: To perimeter abutments and around openings.

-	Pressurized shafts and ducts: At board-to-board and board-to-metal frame junctions.

•	 Application: To clean, dry and dust free surfaces as a continuous bead with no gaps.

-	Gaps greater than 6 mm between floor and underside of plasterboard: After sealing, fill

with jointing compound.

530	CAVITY FIRE BARRIERS WITHIN PARTITIONS/ WALL LININGS

•	 Metal framed systems:

-	Material: Wire reinforced mineral wool 50 mm (minimum) thick.

-	Installation: Form accurately and fix securely with no gaps to provide a complete barrier

to smoke and flame.

•	 Adhesive fixed wall lining systems:

-	Material: Adhesive compound.

-	Installation: Form in a continuous line with no gaps to provide a complete barrier to

smoke and flame.

555	FIRE STOPPING AT PERIMETERS OF DRY LINING SYSTEMS

•	 Material: Tightly packed mineral wool or intumescent mastic/ sealant.

•	 Application: To perimeter abutments to provide a complete barrier to smoke and flame.

560	JOINTS BETWEEN BOARDS

•	 Tapered edged plasterboards:

-	Bound edges: Lightly butted.

-	Cut/ unbound edges: 3 mm gap.

•	 Square edged plasterboards: 3 mm gap.

•	 Square edged fibre reinforced gypsum boards: 5 mm gap.

565	VERTICAL JOINTS

•	 Joints: Centre on studs.

-	Partitions: Stagger joints on opposite sides of studs.

Two layer boarding: Stagger joints between layers.

570	HORIZONTAL JOINTS

•	 Surfaces exposed to view: Horizontal joints not permitted. Seek instructions where height

of partition/ lining exceeds maximum available length of board.

•	 Two layer boarding: Stagger joints between layers by at least 600 mm.

•	 Edges of boards: Support using additional framing.

-	Two layer boarding: Support edges of outer layer.

575	PLANK PLASTERBOARD

•	 First layer in two layer boarding: Square edged with long edges at right angles to studs.

610	FIXING PLASTERBOARD TO TIMBER

•	 Fixing to timber: Securely at the following centres (maximum):

-	Nails: 150 mm.

-	Screws to partitions/ wall linings: 300 mm. Reduce to 200 mm at external angles.

-	Screws to ceilings: 230 mm.

•	 Position of nails/ screws from edges of boards (minimum):

-	Bound edges: 10 mm.

-	Cut/ unbound edges: 13 mm.

•	 Position of nails/ screws from edges of timber supports (minimum): 6 mm.

FINISHING

650	LEVEL OF DRY LINING ACROSS JOINTS

•	 Sudden irregularities: Not permitted.

•	 Joint deviations: Measure from faces of adjacent boards using methods and straightedges

(450 mm long with feet/ pads) to BS 8212, clause 3.3.5.

-	Tapered edge joints:

Permissible deviation (maximum) across joints when measured with feet resting on

boards: 3 mm.

-	External angles:

Permissible deviation (maximum) for both faces: 4 mm.

-	Internal angles:

Permissible deviation (maximum) for both faces: 5 mm.

670	SEAMLESS JOINTING TO PLASTERBOARDS

•	 Cut edges of boards: Lightly sand to remove paper burrs.

•	 Filling and taping: Fill joints, gaps and internal angles with jointing compound and cover

with continuous lengths of paper tape, fully bedded.

•	 Protection of edges/ corners: Reinforce external angles, stop ends, etc. with specified

edge/ angle bead.

•	 Finishing: Apply jointing compound. Feather out each application beyond previous

application to give a flush, smooth, seamless surface.

•	 Nail/ screw depressions: Fill with jointing compound to give a flush surface.

•	 Minor imperfections: Remove by light sanding.

680	SKIM COAT PLASTER FINISH

•	 Plaster type Impact resisting multifinish.

-	Thickness: 2-3 mm.

•	 Joints: Fill and tape except where coincident with metal beads.

•	 Finish: Tight, matt, smooth surface with no hollows, abrupt changes of level or trowel

marks.

692	RIGID BEADS/STOPS

•	 Type: Galvanized steel to BS 6452-1.

695	INSTALLING BEADS/ STOPS

•	 Cutting: Neatly using mitres at return angles.

•	 Fixing: Securely using longest possible lengths, plumb, square and true to line and level,

ensuring full contact of wings with substrate.

•	 Finishing: After joint compounds/ plasters have been applied, remove surplus material

while still wet from surfaces of beads exposed to view.

K11

Rigid sheet flooring/ sheathing/ decking/ sarking/

linings/ casings

K11 Rigid sheet flooring/ sheathing/ decking/ sarking/ linings/ casings

To be read with Preliminaries/ General conditions.

TYPES OF FLOORING/ SHEATHING/ DECKING/ SARKING/ LINING/ CASINGS

325	PARTICLEBOARD FLOORINGTO UPPER FLOORS GENERALLY IN HOUSES

•	 Substrate: Floor joists at 400 mm centres / compartment floor build up.

-	Additional supports: As clause 930.

•	 Flooring: Particleboard to BS EN 312, Type P5.

-	Thickness: 22 mm.

-	Edges: Tongued and grooved all edges.

-	Other requirements: Minimum density of 15kg/m3.  All flooring to be waterproof.

•	 Setting out: Long edges running across joists. End joints central over joists and staggered.

•	 Fixing to joists:

-	Fasteners: Screwed.

-	Fixing centres (maximum):

Around floor perimeter and along short edges of each board: 200 mm.

Along intermediate supports: 400 mm.

-	Fixing distance from edges: 25 mm from long edges and minimum 10 mm from short

edges.

•	 Joint treatment: PVA to BS EN 204, class D3.  All joints to be over joists or bridging pieces.

•	 Expansion provision:

-	Clear expansion gap around floor perimeter of floor area and any upstands: 1.5 mm per

metre run of floor, with a minimum gap of 10 mm.

-	Intermediate expansion/ movement joints: As recommended by flooring manufacturer.

415A	PLYWOOD WALL SHEATHING GENERALLY AND TO ACCESSIBLE BATH PANELS

•	 Substrate: Soft wood studs / timber framing.

-	Additional supports: As necessary.

•	 Sheathing: Plywood manufactured to the relevant standards and quality control procedures

specified in BS 5268-2, and so marked.

-	Type: American construction and industrial plywood.

-	Grade: Marine.

-	Nominal thickness/ number of plies: 18mm.

-	Other requirements: Smooth outer ply layer, free from imperfections, to be sanded to

receive gloss paint finish.

•	 Setting out: Long edges vertical and centred on supports.

-	Expansion gap between adjacent boards (unless otherwise recommended by

manufacturer): 2-3 mm.

•	 Fixing to supports:

-	Fasteners:  [35 mm x 8 gauge brass countersunk screws and cups].

-	Fixing centres (maximum):

Around board edges:  150 mm.

Along intermediate supports: 300 mm.

-	Fixing distance from edges (minimum): 25 mm from bottom edge of board and 10 mm

from other edges.

435A	ORIENTED STRAND BOARD WALL SHEATHING TIMBER FRAME

•	 Substrate: Contractors designed timber frame.

-	Additional supports: As necessary - contractor's design.

•	 Sheathing: Oriented strand board to BS EN 300, Type OSB/3.

-	Thickness: 9 mm.

-	Other requirements: none.

•	 Setting out: Long edges vertical and centred on supports.

-	Expansion gap between adjacent boards (unless otherwise recommended by

manufacturer): 2-3 mm.

•	 Fixing to supports:

-	Fasteners: 75 x 3.35 mm galvanized annular ringed shank nails x 3.35 mm galvanized

annular ringed shank nails.

-	Fixing centres (maximum):

Around board edges: 75 mm.

Along intermediate supports: 300 mm.

-	Fixing distance from edges (minimum): 25 mm from bottom edge of board and 10 mm

from other edges.

515	PLYWOOD ROOF DECKING

•	 Substrate: Roof / ceiling joists / trusses.

-	Additional supports: As clause 930.

•	 Decking: Plywood manufactured to the relevant standards and quality control procedures

specified in BS 5268-2, and so marked.

-	Type: Contractor's choice - provide sample for CA approval.

-	Grade: Marine.

-	Nominal thickness/ number of plies: 18mm.

-	Edges: Tongued and grooved all edges.

-	Other requirements: none.

•	 Setting out: Long edges running across supports. End joints central over joists and

staggered.

•	 Fixing:

-	Fasteners: 50 mm x 8 gauge wood screws into pilot holes.

-	Fixing centres:

Along each support: 25 mm from each long edge and at maximum 200 mm centres

between.

Around perimeter of roof area: Maximum 150 mm centres.

•	 Expansion provision:

-	Clear expansion gap around perimeter of roof area and upstands: 10 mm.

-	Intermediate expansion/ movement joints: As recommended by decking manufacturer.

690A	RIGID BOARD INSULATION BETWEEN RAFTERS / TRUSSES TO SLOPING ROOF

Generally

•	 Substrate: Contractor designed Trussed Rafters / cut roof as clause G20.

•	 Rigid board insulation:  [High performance rigid thermoset polyisocyanurate (PIR) insulant

manufactured with a blowing agent that has zero Ozone Depletion Potential (ODP) and

Global Warming Potential (GWP) of less than 5 in accordance with the requirements of BS

4841-1. ].

-	Standard:  [BS EN 13165].

-	Product certification:  [To be BBA and IAB certified for this application. BS EN ISO 9001:

2000/IS EN ISO9001:2008.  To be installed in accordance with the manufacturer's

instructions].

•	 Manufacturer:  [Contractor's choice, sample to be provided for CA approval].

Face size (length x width):  [1200 x 450 mm].

•	 Thickness (nominal):  [100 mm].

•	 Thermal conductivity:  [Aged - 0.022 W/mK].

•	 Reaction to fire class:  [Class 1 fire rating on both core and facings, producing less than

5% smoke obscuration when tested to BS 5111-1:1974 low risk].

•	 Additional requirements:  [To be highly resistant to transmission of water vapour (more

than 100MN.s/g) and air movement in accordance with BS EN 12086.  Compressive

strength typically in excess of 125 kPa at 10% compression when tested to BS EN 826: 1996

(Thermal insulating products for building applications. Determination of compression

behaviour) ].

•	 Placement: Secure with no gaps between roof trusses / rafters.

Joints between boards, at closures and penetrations: No gaps and free from debris.

691A	RIGID BOARD INSULATION BELOW RAFTERS / TRUSSES TO SLOPING ROOF

Generally

•	 Substrate: Contractor designed Trussed Rafters / cut roof as clause G20.

•	 Rigid board insulation:  [High performance rigid thermoset polyisocyanurate (PIR) insulant

faced on both sides with a proprietary low emissivity composite foil facing.  To be

manufactured with a blowing agent that has zero Ozone Depletion Potential (ODP) and

Global Warming Potential (GWP) of less than 5 in accordance with the requirements of BS

4841-1. ].

-	Standard:  [BS EN 13165].

-	Product certification:  [To be BBA and IAB certified for this application. BS EN ISO 9001:

2000/IS EN ISO9001:2008.  To be installed in accordance with the manufacturer's

instructions].

•	 Manufacturer:  [Contractor's choice, sample to be provided for CA approval].

Face size (length x width):  [1200 x 450mm, 1200 x 600mm].

•	 Thickness (nominal):  [30 mm].

•	 Thermal conductivity:  [Aged - 0.022 W/mK].

•	 Reaction to fire class:  [Class 1 fire rating on both core and facings, producing less than

5% smoke obscuration when tested to BS 5111-1:1974 low risk].

•	 Additional requirements:  [To be highly resistant to transmission of water vapour (more

than 100MN.s/g) and air movement in accordance with BS EN 12086.  Compressive

strength typically in excess of 125 kPa at 10% compression when tested to BS EN 826: 1996

(Thermal insulating products for building applications. Determination of compression

behaviour).  Joints to be taped with suitable proprietary compatible low emissivity foil faced

tape ].

•	 Placement: Secure with no gaps with suitable proprietary fixings below of roof trusses /

rafters.

Joints between boards, at closures and penetrations: No gaps and free from debris.

816	MARINE PLYWOODGENERALLY

•	 Substrate: As detailed.

-	Additional supports: As clause 930.

•	 Plywood: To BS 1088-1 but excluding plywood made of gabon veneers.

-	Manufacturer/ Supplier: FCS Certified.

Product reference: -.

-	Thickness: 18.

-	Edges: Tongued and grooved long edges.

-	Preservative treatment: -.

-	Other requirements: -.

•	 Setting out: Long edges running across supports.

-	Gap between adjacent boards: -.

•	 Fixing to supports:

-	Fasteners: Screwed.

-	Fixing centres (maximum):

Around board edges: 150 mm.

Along intermediate supports: 300 mm.

-	Fixing distance from edges (minimum): 10 mm.

•	 Joint treatment: Bonded with waterproof adhesive.

•	 Accessories: none.

875A	MEDIUM DENSITY FIBREBOARD (FR)Boxing out to NI meter cupboard / M&E services

•	 Substrate: SW timber 50x50mm or 75x35mm SW studding.

-	Additional supports: As clause 930.

•	 Medium density fibreboard: To BS EN 622-5, Type MDF.FR.

-	Manufacturer/ Supplier: Contractors Choice.

Product reference: Contractors Choice.

-	Formaldehyde class to BS EN 622-1: Class E1.

-	Fire rating: Class 0 performance to Building Regulations.

-	Thickness: 18 mm.

-	Edges: Square.

-	Other requirements: n/a.

•	 Setting out: Long edges running across supports.

-	Gap between adjacent boards: n/a.

•	 Fixing to supports:

-	Fasteners: 35 x 3.5 mm countersunk  woodscrews.

-	Fixing centres (maximum):

Around board edges: 200 mm.

Along intermediate supports: 150 mm.

-	Fixing distance from edges (minimum): 12 mm.

•	 Joint treatment: Bonded with PVA adhesive to BS EN 204, class D3.

•	 Accessories: n/a.

Finish - Meter cupboard to be painted with white gloss as per spec note

875B	MEDIUM DENSITY FIBREBOARD Pipe casings, boxing out, Future shower feeds, Rain

water harvesting supply

•	 Substrate: SW timber 50x50mm or 75x35mm SW studding.

-	Additional supports: As clause 930.

•	 Medium density fibreboard: To BS EN 622-5, Type MDF.H.

-	Manufacturer/ Supplier: Contractors Choice.

Product reference: Contractors Choice.

-	Formaldehyde class to BS EN 622-1: Class E1.

-	Fire rating: Class 0 performance to Building Regulations.

-	Thickness: 18 mm.

-	Edges: Square.

-	Other requirements: n/a.

•	 Setting out: Long edges running across supports.

-	Gap between adjacent boards: n/a.

•	 Fixing to supports:

-	Fasteners: 35 mm x 8 gauge brass countersunk screws and cups.

-	Fixing centres (maximum):

Around board edges: 200 mm.

Along intermediate supports: 150 mm.

-	Fixing distance from edges (minimum): 12 mm.

•	 Joint treatment: Bonded with PVA adhesive to BS EN 204, class D3.

•	 Accessories: n/a.

Finish - Meter cupboard to be painted with white gloss as per spec note

WORKMANSHIP

910	INSTALLATION GENERALLY

•	 Timing: Building to be weathertight before fixing boards internally.

•	 Moisture content of timber supports (maximum): 18%.

•	 Joints between boards: Accurately aligned, of constant width and parallel to perimeter

edges.

•	 Methods of fixing, and fasteners: As section Z20 where not specified otherwise.

915	DRYNESS OF CONCRETE/ SCREED SUBSTRATES FOR FLOATING FLOORS

•	 Relative humidity above substrate when tested with a hygrometer to BS 8201, Appendix A

(maximum): 75%.

-	Test points: All corners, around perimeter, and random points over area being tested.

-	Drying aids: Turned off for not less than 4 days before testing.

925	BATTENS FOR FLOATING FLOORS

•	 Quality of timber: Free from decay, insect attack (except ambrosia beetle damage) and

with no knots wider than half the width of the section.

•	 Preservative treatment: As section Z12 and British Wood Preserving and Damp-proofing

Association Commodity Specification C8.

-	Type/ Desired service life: Organic solvent Type FN/ 30 years .

•	 Moisture content at time of laying (maximum): 16%.

930	ADDITIONAL SUPPORTS

•	 Additional studs, noggings/ dwangs (Scot) and battens:

-	Provision: In accordance with board manufacturer's recommendations and as follows:

Tongue and groove jointed rigid board areas: To all unsupported perimeter edges.

Butt jointed rigid board areas: To all unsupported edges.

-	Size: Not less than 50 mm wide and of adequate thickness.

-	Quality of timber: As for adjacent timber supports.

Treatment (where required): As for adjacent timber supports.

940	BOARD MOISTURE CONTENT AND CONDITIONING

•	 Moisture content of boards at time of fixing: Appropriate to end use.

•	 Conditioning regime: Submit proposals.

950	MOISTURE CONTENT TESTING

•	 Test regime and equipment: Submit proposals.

•	 Test results: Submit record of tests and results.

960	FIXING GENERALLY

•	 Boards/ sheets: Fixed securely to each support without distortion and true to line and level.

•	 Fasteners: Evenly spaced in straight lines and, unless otherwise recommended by board

manufacturer, in pairs across joints.

-	Distance from edge of board/ sheet: Sufficient to prevent damage.

•	 Surplus adhesive: Removed as the work proceeds.

980	OPEN JOINTS

•	 Perimeter joints, expansion joints and joints between boards: Free from plaster, mortar

droppings and other debris.

•	 Temporary wedges and packings: Removed on completion of board fixing.

990A	ACCESS PANELS

•	 Size and position: Agree before boards are fixed.

•	 Additional noggings/ dwangs (Scot), battens, etc: Provide and fix as necessary.

Refer to architectural & M&E dwg's for exact position of same.

K40

Demountable suspended ceilings

K40 Demountable suspended ceilings

To be read with Preliminaries/General conditions.

TYPES OF CEILING SYSTEM

115A	UNIT SUSPENDED CEILING SYSTEMSUSPENDED CEILING(S) TO MAIN

CORRIDORS & COMMUNAL AREAS

-Structural soffits(s) Concrete slabs and Steel/timber roof on top floors.

-  	Ceiling system manufacturer: Contractors choice - samples to be supplied to CA for

approval.

Product reference: Suspended ceiling system with 17mm thick medium density

acoustic mineral tiles with a smooth acoustically transparent, high durability facing.

-  	Grid form: suspension system

-  	Grid exposure: Exposed 24mm Grid

-  	Grid spacings: 600 x 600 mm.

-  	Access: Infill Units Fully Demountable with tool

-  	Ceiling module: 600 x 600 mm.

-  	Ceiling soffit above finished floor level: min. 2400mm unless other wise noted or CA

agreed.

-  	Components: To include all hangers, fixings, main runners, cross members, primary

channels, perimeter trims, splines, noggings, clips, bracing, bridging etc, which are

necessary to complete the installation and achieve the performance specified

-  	Suspension system: As clause 250

-  	Perimeter trim: As clause 260

-  	Timber edge battens: As clause 255 (if required)

-  	Infill units: As clause 265

-  	Access units: As clause 280 Not Required

-  	Insulation: As clause 285 (if required)

-  	Air plenum barriers: As clause 290 (if required)

-  	Integrated services fittings: As Clause 395.

-  	Other requirements: Sound absorption 0.65 aw, Sound attenuation 35 dB.

203	DEFINITIONS

-  	Ceiling: Items collectively constituting the ceiling surface i.e. infill

units/boards/stretched fabric, access units and grid.

-  	Ceiling system: Ceiling plus suspension system and integrated services fittings.

GENERAL/ PERFORMANCE

205	COMPLIANCE WITH PERFORMANCE REQUIREMENTS

•	 Testing/ assessment: Submit UKAS accredited laboratory reports for the following: Fire

performance.

•	 Materials, components and details: Use those used in the test and identified in the

assessment reports. If discrepancies arise, give notice.

205A	COMPLIANCE WITH PERFORMANCE REQUIREMENTS

•	 SUSPENDED CEILINGS GENERALLY: Unless specified otherwise, comply with the

relevant recommendations and performance requirements of BS 8290 for the selection and

assembly of components and materials.

220	STRUCTURAL PERFORMANCE installation of the suspended ceiling will be taken as joint

acceptance by the Main Contractor and Ceiling Contractor of the suitability of the

environmental conditions

•	 Loads: The ceiling system must safely support all anticipated loads, including services

fittings:

-	Class: 1.

-	Additional loads/ pressures to be sustained by ceiling system: uplift.

Ceiling system subject to wind pressure: Yes.

•	 Deflection (maximum) between points of support:

-	Span under 1200 mm: Span/400.

-	Span 1200-1800 mm: Span/500.

-	Span over 1800 mm: Span/600.

•	 Test standard: To BS EN 13964.

COMPONENTS

240	SAMPLES

•	 General: Submit representative samples of the following: Before placing orders submit

representative sample(s) to CA of standard tile and ventilation tile. Ensure that delivered

materials match samples. .

245	STANDARDS

•	 Components: To BS EN 10346.

-	Aluminium sheet, strip and plate: To BS EN 485.

-	Aluminium bars, tubes and sections: To relevant parts of BS EN 515, BS EN 573, BS EN

755 and BS EN 12020.

250A	SUSPENSION SYSTEM

Extent of system: Include hangers, fixings, main runners, cross members, primary

channels, perimeter trims, splines, noggings, clips, bracing, bridging, etc., which are

necessary to complete the ceiling system and achieve performance.

-  	Materials:

-  	Top fixings: As recommended by ceiling contractor

-  	Hangers: suspension wire

-  	Grid type: Exposed 24mm Grid System

-  	Finish: Pre-coated fully polymerized Polyester Finish

-  	Colour: white

255A	EDGE BATTENS (if required - as recommended by ceiling contractor)

-  	Type: Planed softwood to BS EN 942, class J10.

-  	Moisture content at time of fixing: 15% ± 2%.

-  	Finished size: Min. 35x35mm - as per ceiling manufacturers

recommendations, details and spec.

Finish (apply before ceiling grid is installed): Treated.

260A	PERIMETER TRIMS

Type: perimeter angle trim as per ceiling manufacturers recommendations, details and

spec. - submit samples for CA approval. Compatible with ceiling system.

-  	Fixings to perimeters: As recommended by ceiling contractor

Fixing centres (maximum): 450 mm..

265A	INFILL UNITS

Type: 17mm thick medium density acoustic mineral tiles with a smooth acoustically

transparent, high durability facing.

-  	Form: lay in tiles

-  	Sizes: 600 x 600 mm.

-	   Finish: Acoustically Transparent Painted Finish.

-  	Colour: White

EXECUTION

305	SETTING OUT

•	 General: Completed ceiling should present, over the whole of its surface exposed to the

room below, a continuous and even surface, jointed (where applicable) at regular intervals.

•	 Infill and access units, integrated services: Fitted correctly and aligned.

•	 Edge/ perimeter infill units size (minimum): Half standard width or length.

•	 Corner infill units size (minimum): Half standard width and length.

•	 Grid: Position to suit infill unit sizes. Allow for permitted deviations from nominal sizes of

infill unit.

•	 Infill joints and exposed suspension members: Straight, aligned and parallel to walls,

unless specified otherwise.

•	 Suitability of construction: Give notice where building elements and features to which the

ceiling systems relate are not square, straight or level.

310	BRACING

•	 General: Secure, with additional bracing and stiffening to give a stable ceiling system

resistant to design loads and pressures.

315	PROTECTION

•	 Loading: Do not apply loads for which the suspension system is not designed.

•	 Ceiling materials: When necessary, remove and replace correctly using special tools and

clean gloves, etc. as appropriate.

320A	TOP FIXING

•	 Building structure: Verify suitability.

•	 Structural soffit: Concrete slabs and Steel/timber roof on top floors.

-	Suitability to receive specified fixings: Evaluate and confirm.

•	 Fixing generally: In accordance with BS EN 13964.

•	 Fixing to:

-	Concrete: Drill and insert suitable expanding anchors.

-	Aerated concrete: Fix through from the top of concrete units and provide a system of

primary support channels.

-	Structural steel: Drill, or use suitable proprietary clips/ adaptors.

-	Metal roof decking: Fix to sides of liner tray corrugations.

-	Timber: Fix to side of joists at least 50 mm from bottom edge. If ceiling system is

intended for fire protection, fix into top third of joists.

-	Hollow structural members: Submit fixing proposals.

Cartridge or powder activated methods: Do not use.

325	INSTALLING HANGERS

•	 Wire hangers: Straighten and tension before use.

•	 Installation: Install vertical or near vertical, without bends or kinks. Do not allow hangers to

press against fittings, services, or insulation covering ducts/ pipes.

•	 Obstructions: Where obstructions prevent vertical installation, either brace diagonal

hangers against lateral movement, or hang ceiling system on an appropriate rigid sub-grid

bridging across obstructions and supported to prevent lateral movement.

•	 Extra hangers: Provide as necessary to carry additional loads.

•	 Fixing:

-	Wire hangers: Tie securely at top with tight bends to loops to prevent vertical movement.

-	Angle/ strap hangers: Do not use rivets for top fixing.

•	 Spacings: As per ceiling manufactures recommendations, details and spec..

330	INSTALLING TIMBER EDGE BATTENS

•	 Fixing: Firmly to perimeter wall or other building structure.

-	Fasteners: Plugged and screwed to walls.

Fixing centres (maximum): 450 mm.

335A	INSTALLING PERIMETER TRIMS

•	 Jointing: Neat and accurate, without lipping or twisting.

-	External and internal corners: Mitre joints generally. Overlap joints at internal corners are

acceptable.

-	Intermediate butt joints: Minimize. Use longest available lengths of trim. Align adjacent

lengths.

•	 Fixing: Fix firmly to perimeter wall, edge battens or other building structure.

-	Fasteners: As per manufacturers recommendations, details and spec.

-	Fixing centres: 450 mm.

340	EXPOSED GRIDS

•	 Grid fixings: Wire hangers.

•	 Main runners: Install level. Do not kink or bend hangers.

-	Spliced joints: Stagger.

-	Wire hangers passing through main runners: Use sharp bends and tightly wrapped

loops.

-	Angle/ strap hangers: Do not use rivets for bottom fixing.

-	Angular displacement of long axis of one runner in relation to next runner in line with it:

Not visually apparent.

•	 Cross members supported by main runners or other cross members: Install perpendicular

to intersecting runners.

•	 Cross tees: Flat and coplanar with flanges of main runners after panel insertion.

-	Cross tees over 600 mm long, cut and resting on perimeter trim: Provide an additional

hanger.

•	 Holding down clips: Locate to manufacturer's recommendations.

-	Fire protecting/ resisting ceiling systems: Use clip type featured in the fire test/

assessment.

355	INSTALLING INFILL UNITS

•	 General:

-	Perimeter infill units: Trimmed, as necessary, to fully fill space between last grid member

and perimeter trim. Prevent subsequent movement.

-	Deeply textured infill units: Minimize variations in apparent texture and colour. In

particular, avoid patchiness.

•	 Concealed grids: Install infill units uniformly, straight and aligned. Avoid dimension creep.

-	Infill units around recessed luminaires and similar openings: Prevent movement and

displacement.

365	INSTALLING METAL INFILL UNITS

•	 Sound absorbing pads: Fit to prevent upward air movement through infill units. Cut or Fold

pads in cut perimeter infill units to full unit size. Reseal cut pads.

•	 Perimeter infill units: Firmly wedge cut units into perimeter trim, or clip down.

385	UPSTANDS AND BULKHEADS

•	 Vertical ceiling systems: Support and brace to provide alignment and stability.

•	 High upstands: Provide support at base of upstand.

390	OPENINGS IN CEILING MATERIALS

•	 General: Neat and accurate. To suit sizes and edge details of fittings. Do not distort ceiling

system.

395	INTEGRATED SERVICES

•	 General: Position services accurately, support adequately. Align and level in relation to the

ceiling and suspension system. Do not diminish performance of ceiling system.

•	 Small fittings: Support with rigid backing boards or other suitable means. Do not damage or

distort the ceiling.

-	Surface spread of flame rating of additional supporting material: Not less than ceiling

material.

•	 Services outlets:

-	Supported by ceiling system: Provide additional hangers.

-	Independently supported: Provide flanges to support ceiling system.

401	CEILING MOUNTED LUMINAIRES

•	 Support:   	As per manufacturers details and spec..

-	Independently supported luminaires: Suspension adjusted to line and level of ceiling.

-	Ceiling supported luminaires: Modifications and/ or extra support required: To each

luminaire.

•	 Surface mounted luminaires: Units installed so that in event of a fire the designed grid

expansion provision is not affected.

•	 Modular fluorescent recessed luminaires: Compatible with ceiling module. Extension boxes

must not foul ceiling system.

•	 Recessed rows of luminaires: Provide flanges for support of grid and infill units, unless

mounted above grid flanges. Retain in position with lateral restraint.

•	 Fire protecting/ resisting ceiling systems: Luminaires must not diminish protection integrity

of ceiling system.

•	 Access: Provide access for maintenance of luminaires.

406	TRUNKING

•	 Recessed trunking: Provide flanges for support of grid and infill units, unless mounted

above grid flanges. Retain in position with lateral restraint.

411A	MECHANICAL SERVICES

-	Inlet/ Outlet grilles: Trim ceiling grid and infill units to suit.

-	Space beneath: Sufficient for ceiling system components.

-	Suspension and connections: Permit accurate setting out and levelling of units.

•	 Air grilles and diffusers:

-	Setting out: Accurate and level.

-	Linear air diffusers: Retain in place with lateral restraint. Provide flanges for support of

grid and infill units.

-	Grille/ Diffuser ceiling joints: Provide smudge rings and edge seals.

•	 Smoke detectors and PA speakers:

-	Ceiling infill units: Scribe and trim to suit.

-	Independent suspension: Required.

Flexible connections: Required.

415	INSTALLING INSULATION

•	 Fitting: Fit accurately and firmly with butted joints and no gaps.

•	 Insulation within individual infill units: Fit closely. Secure to prevent displacement when infill

units are installed or subsequently lifted.

-	Dustproof sleeving: Reseal, if cut.

•	 Width: Lay insulation in the widest practical widths to suit grid member spacings.

•	 Services: Do not cover electrical cables that have not been sized accordingly. Cut

insulation carefully around electrical fittings, etc. Do not lay insulation over luminaires.

•	 Sloping and vertical areas of ceiling system: Fasten insulation, to prevent displacement.

500	ELECTRICAL CONTINUITY AND EARTH BONDING

•	 Substantial conductive parts of the ceiling system: Electrically continuous and fully earth

bonded to carry prospective earth fault currents.

-	Standard: To BS 7671.

•	 Sequence: Complete earth bonding as soon as possible after completion of each

independent area of suspension system.

•	 Testing: After completion of the ceiling system, associated services and fittings, test

conductive parts of suspension system required to carry earth fault current, or used as

bonding connections. Give notice before testing.

-	Electrical continuity: Measure from various distant conductive points of ceiling system

and to earth bar in distribution board serving the area.

-	Test current: Sufficient to indicate probable electrical performance under fault conditions.

-	Test instrument: Type providing a pulse of about 25 A at safe voltage for safe duration,

and indicating resistance in ranges 0-2 ohms and 0-20 ohms.

-	Resistance of measuring conductors: Deduce from test instrument readings.

-	Test readings: Record and certify. Add results to resistance of other parts of the path

forming the earth fault loop.

COMPLETION

505A	TOOLS

•	 Provide the Main Contractor with duplicate sets of user instructions and access tools

recommended by the suspended ceiling/access panel manufacturer. One for the use of

contractors requiring access to the void and the other for handing over to the CA at

Practical Completion.

520A	USER INSTRUCTIONS

Provide the Main Contractor with two copies; one for the use of contractors requiring

access to the void and the other for handing over to the CA at Practical Completion. The

contents of the instructions to include:

-  	Correct methods for lifting and replacing tiles, panels, etc.

-  	Cleaning methods and materials.

-  	Decoration of tiles and touching up where appropriate.

-  	Limitations placed on subsequent alterations and maintenance procedures

to fire resisting suspended ceilings to ensure that their performance is not impaired.

530	SPARES

•	 General: At Completion supply the following: 15 tiles for ceiling system K40/115A.

L

Windows/Doors/Stairs

L10

Windows/ Rooflights/ Screens/ Louvres

L10 Windows/ Rooflights/ Screens/ Louvres

To be read with Preliminaries/ General conditions.

GENERAL

110	EVIDENCE OF PERFORMANCE

•	 Certification: Provide independently certified evidence that all incorporated components

comply with specified performance requirements.

120	SITE DIMENSIONS

•	 Procedure: Before starting work on designated items take site dimensions, record on shop

drawings and use to ensure accurate fabrication.

•	 Designated items:

All Factory constructed elements.

140	CONTROL SAMPLES

•	 Procedure:

-	Finalise component details.

-	Fabricate one of each of the following designated items as part of the quantity required

for the project.

-	Obtain approval of appearance and quality before proceeding with manufacturer of the

remaining quantity.

•	 Designated items:

Each product type.

150	PHYSICAL SECURITY SECURED BY DESIGN REQUIREMENTS

All windows are to be from a window manufacturer / supplier with a valid Secured By

Design License. Windows are to be successfully tested at an appropriately accredited

UKAS test house or if otherwise tested must be independently authenticated, in writing, by

a test house suitably approved by UKAS.  All windows installed within Secured By Design

developments must be exactly the same specification as that successfully tested.

Windows installed within Secured By Design developments also must meet the following

performance standards:

i.  	BS 4873 (Aluminium)

ii.  	BS 7412 (PVC-U)

iii.  	BS 644 (Timber) or the BWF Timber Window Accreditation Scheme (TWAS)

iv.  	BS  6510 (Steel)

The ALO must be supplied with a copy of the test certificate prior to completion of the

Secured By Design development (the report).  ACPO will continue to support moves

towards product certification by recognised ongoing third party inspection (BSI Kite mark,

BBA Agreement certificate or BM TRADA Q-MARK).  Where products are not certified in

this way, manufacturers declaration that all products supplied are identical to those tested

must accompany the copy of the test certificate supplied.

Windows must be securely fixed to the surrounding structure at a maximum of 600mm

centres, with at least two fixing points per side.

Ground floor windows and those that are easily accessible to entry must have key

operated locks.  Where necessary, opening restrictors or similar built-in mechanisms will

be required.

PRODUCTS

360B	PVC-U WINDOWS	SECURED BY DESIGN ACCREDITED FULLY

REVERSIBLE DOUBLE GLAZED (ALL WINDOWS)

•	 Products & materials are to be in accordance with the following British Standards: refer to

elevations for individual styles of windows.

-	BSEN9001:2008 quality systems for the design, development, production & installation

of windows.

-	BSEN12608:2007 specification for white PVCU extruded hollow profile with heat welded

joints – materials type A

-	Kitemark BS7412:2002 & SBD accreditation and BS7950 for security.

-	BS6375 part 1 & 2 for weathertightness & operational & strength characteristics.

•	 Profiles are 70mm front to back dimension manufactured from an acrylic, high impact

modified, un-plasticized Polyvinyl Chloride compound (PVC-U), formulated to suit the

Central European climate.

•	 Extruded hollow and solid sections to include 4 chambers.

•	 Fusion welded joints. Internal steel reinforcement

•	 PCE weather seals and glazing gaskets.  Window to have double weatherseal to external

environment.

•	 Colour fastness, to EN 513: DE*<5, Db*<3.

•	 All windows must comply with relevant building regulations particularly parts L, B, N, F & K.

•	 Wind resistance to be 2400 pascals, air permeability 600 pascals & water tightness 500

pascals.

•	 Glass to meet BS6262 & be manufactured in accordance with BS5713.

•	 Windows to be WER B rated

•	 Windows to have u-value of 1.4W/m2K - Typical glass spec for U-value of 1.4W/m2K will

be 4mm proprietary thermal coated glass - 20mm Argon filled cavity - 4mm proprietary

thermal coated glass. This is an example of the glazing specification, Contractor can

provide alternative proposals as long as they achieve a u-value of 1.4W/m2K.

•	All windows to be top swing to utilise a fully reversible hinge mechanism.

Contractor to provide 10 year warranty for complete window.  Windows above ground

floor to be fully reversible for safe cleaning from the inside in accordance with Life Time

Homes requirements and current building regulations.

•	 Standard: Manufactured to BS 7412 from PVC-U extruded profiles. Must have fully welded

joints including mullions and transoms. Mechanically jointed systems are not acceptable.

•	 Secured By Design Standard: Tested and Certified.  To comply to BS7950 there necessary

& applicable.

•	 Manufacturer: A firm currently registered under a third party quality assurance scheme.

•	 Exposure category to BS 6375-1/ Design wind pressure: Severe weather rating.

•	 Glazing units to be 'kite marked' and have 10 year guarantees to be provided at

completion. Glass to comply with BS952 and BS6262 including Secured by Design

Standards.

•	 Hinges to have a 10 year guarantee.

•	 All panes with glass below 800mm from floor or ground level to be of clear toughened

safety glass. All panes with glass below 1500mm from floor or ground level to side panels

to doorways to be of toughened clear safety glass. Glazing to all toilets and bathrooms to

be of obscure 'stippled' patterned  glass, sample to be approved by the HA.

•	 Ironmongery/ Accessories: To have twin-cam security espagnolette locking system be

lockable by key except where the window is a designated fire escape window. Childproof

releasable restrictors limit 100mm to all windows. NO TRICKLE VENTS TO BE

INSTALLED TO WINDOWS - Mechanical heat recovery system is to be installed.

-	Operating handles to be maximum 1200mm above FFL to satisfy Life Time Homes

requirements.  Window handles to be lockable (with the exception of fire escape

windows) provide ironmongery samples for approval in SAA/polished chrome, brass and

PPC coloured finish.

•	 Fire escape:  	All windows where noted fire escape must have a minimum clear opening

of 0.33m2, and minimum width of 450mm,  minimum height if 450mm.

•	 Other: Provide a full size fully working sample for CA approval.

•	 SAFETY GLAZING TO COMPLY WITH BS EN356:2000 RATING P2A.

-	Obscure Glazing: PATTERN: Stippled glazing to internal pane to all bathrooms and WC's

and where glazing identified as obscure on window/door schedules.

-	Textured side of pane to be installed to the inner face of the triple glazed units.

-	Double glazed unit to be installed in accordance with manufacturers instruction with

proprietary perimeter seals and preformed butyl strip tape and proprietary filler as

necessary.

•	 Colours:  Contractor to make allowance for provision of dual frame colour (different colour

inside & outside) to all windows and supply internal / external samples in white, grey, black,

and oak timber effect (and other timber effect as requested) for CA approval.  Client / CA's

selected window colours to have no financial or programming implications to the contract -

Contractor to provide samples in good timing to facilitate proper consideration.

460ASUN TUNNELSGENERALLY.

•	 Manufacturer: Contractor's choice, provide sample for CA approval.

-	Product reference: Proprietary rigid sun tunnel with flat rooflight type roof aperture -

rooftile inline flat glazing option with self-cleaning glass. .

•	 Type: 14 inches diameter, to suit roof pitch.

•	 Frame: Integral with rooflight.

-	Finish: Black as delivered, to be factory finished.

-	Colour: Black.

•	 Kerb: Integral with rooflight

•	 Tunnel: Approx.2.0 metres length.

•	 Performance : Sun tunnel to have u-value of 2.0W/m2K

•	 Glazing details: Toughened glass with clear and clean coating.  Rooflight aperture to be

resistant to impact.

•	 Other requirements: Complete with internal circular sealed ceiling aperture installed in

accordance with manufacturers recommendations,

Accessories: - Rigid extension sections as necessary, all other necessary accessories to

be included to ensure complete installation including proprietary flashings, upstands, etc..

•	 Fixing: In accordance with manufacturer's recommendations and details.  Tunnel to be

proprietary insulated type otherwise insulated with minimum 100mm mineral fibre material

held in place with proprietary tape to achieve necessary u-value.

EXECUTION

710	PROTECTION OF COMPONENTS

•	 General: Do not deliver to site components that cannot be installed immediately or placed

in clean, dry floored and covered storage.

•	 Stored components: Stack vertical or near vertical on level bearers, separated with spacers

to prevent damage by and to projecting ironmongery, beads, etc.

730	PRIMING/ SEALING

•	 Wood surfaces inaccessible after installation: Prime or seal as specified before fixing

components.

750	BUILDING IN

•	 General: Not permitted unless indicated on drawings.

-	Brace and protect components to prevent distortion and damage during construction of

adjacent structure.

755	PVC-U WINDOW INSTALLATION

•	 Standard: In accordance with clause 783 and British Plastics Federation 'Code of practice

for the installation of PVC-U windows and doorsets in new domestic dwellings'.

765	WINDOW INSTALLATION GENERALLY

•	 Installation: Into prepared openings.

•	 Gap between frame edge and surrounding construction:

-	Minimum: To window manufacturers recommendation.

-	Maximum: To window manufacturers recommendations.

•	 Distortion: Install windows without twist or diagonal racking.

770	DAMP PROOF COURSES IN PREPARED OPENINGS

•	 Location: Ensure correct positioning in relation to window frames. Do not displace during

fixing operations.

783	FIXING OF PVC-U FRAMES

•	 Standard: As section Z20.

•	 Fasteners: Manufactures straps and recommended anchor systems.

-	Spacing: When not predrilled or specified otherwise, position fasteners 150-250 mm

from ends of each jamb, adjacent to each hanging point of opening lights, but no closer

than 150 mm to a transom or mullion centre line, and at maximum 600 mm centres.

790	FIRE RESISTING FRAMES

•	 Gap between back of frame and reveal: Completely fill with intumescent mastic or tape.

810	SEALANT JOINTS

•	 Sealant:

-	Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

Product reference: -.

-	Colour: Standard colour to be agreed with architect.

-	Application: As section Z22 to prepared joints. Finish triangular fillets to a flat or slightly

convex profile.

820	IRONMONGERY

•	 Fixing: Assemble and fix carefully and accurately using fasteners with matching finish

supplied by ironmongery manufacturer. Do not damage ironmongery and adjacent

surfaces.

•	 Checking/ Adjusting/ Lubricating: Carry out at Completion and ensure correct functioning.

L20

Doors/ shutters/ hatches

L20 Doors/ shutters/ hatches

To be read with Preliminaries/ General conditions.

GENERAL

110	EVIDENCE OF PERFORMANCE

•	 Certification: Provide independently certified evidence that all incorporated components

comply with specified performance requirements.

115	FIRE RESISTING DOORS/ DOORSETS/ ASSEMBLIES

•	 Evidence of fire performance: Provide certified evidence, in the form of a product

conformity certificate, directly relevant fire test report or engineering assessment, that each

door/ doorset/ assembly supplied will comply with the specified requirements for fire

resistance if tested to BS 476-22, BS EN 1634-1 or BS EN 1634-3. Such certification must

cover door and frame materials, glass and glazing materials and their installation, essential

and ancillary ironmongery, hinges and seals.

150	SITE DIMENSIONS

•	 Procedure: Before starting work on designated items take site dimensions, record on shop

drawings and use to ensure accurate fabrication.

•	 Designated items:

All door openings .

180A	PHYSICAL SECURITY SECURED BY DESIGN REQUIREMENTS

A high level of physical security is to be incorporated in the building construction and the

developments to conform to the minimum Secured By Design standards.

All external doorsets (front, rear & apartment doors - communal & main entrance) must

comply with the following in order to be considered suitable for use within a Secured By

Design development:

The Secured By Design Standard for doorsets is BSI PAS 24-1: 1999 `Doors of enhanced

security'.  All doorsets must also be fit for purpose and therefore must comply with BSI

PAS 23-1: 1999 `General performance requirements for door assemblies'.  All security and

performance testing must be undertaken at a United Kingdom Accreditation Service

(UKAS) suitably accredited test house, or if otherwise tested must be independently

authenticated, in writing, by a serving member of a UKAS approved test house.

All security and performance testing must be undertaken at a UKAS suitably accredited

test house or if otherwise tested must be independently authenticated, in writing, by a

serving member of a UKAS approved test house.

All doorsets installed within Secured By Design developments must be exactly the same

specification as that successfully tested.  The ALO must be supplied with a copy of the test

certificate prior to the completion of the Secured By Design development (the developer

should be afforded the opportunity to see a copy of the full test report).  ACPO will continue

to support moves towards product certification by recognised ongoing third party inspection

(BSI Kite mark, BBA Agreement certificate or BM TRADA Q-MARK).  Where products are

not certified in this way the manufacturers declaration that all products supplied are

identical to those tested must accompany the copy of the test certificate supplied.

Refer to 'Design Specification' for additional information.

PRODUCTS

250A	SECURED BY DESIGN EXTERNAL HARDWOOD FRONT & REAR DOORSETSALL

HOUSES

-  	Secured by Design Standard: Tested and Certified as complying to BSI PAS 24-1:

1999 'Doors of enhanced security' and also BSI PAS 23-1: 1999 'General performance

requirements for door assemblies' at an approved UKAS test house.  A valid secure by

design certificate must be produced prior to any doors being installed onsite.

-  	Manufacturer: Contractors choice.

-  	Door leaf: 58mm thick depending upon performance requirements indicated in

schedule.

-  	U-value: Average u-value (front & rear doors) of 1.3W/m2K.

-  	Wood species: Hardwood .

-  	Panel details: Raised and fielded with moulded beading to perimeters.

-  	Finish as delivered: Fully factory finished with micro porous paints and stains and

from RAL colours to be included as colour options

-  	Glazing details: Double Glazing units to be 'kite marked' and have 10 year

guarantees to be provided at completion. Glass to comply with BS952 and BS6262.

-  	Additional Glazing certification: All laminated glass must be certified to BS EN356

2000 rating P2A.

-  	All panes with glass below 1500mm from floor or ground level to side panels to

doorways to be of laminated safety glass. Obscure 'stipple type' patterned glass.

-  	All outer panes to be min. 6.4mm laminated.

-  	Front door glazing to be as per elevations and clearly highlighted on the individual

house types - front glazing to be obscure but can be changed to clear if the client requests

this option

-  	Rear door glazing to be as per elevations and clearly highlighted on the individual

house types - rear glazing to be clear

-	   Safety glazing to comply with BS EN 356 2000 Rating P2A

-  	Frame and architraves:

-  	Wood species: To match doors.

-  	Finish as delivered: Factory finished.

-  	Preservative treatment: Required.

-  	Ironmongery: Multi-point deadlocking system with three or more deadbolts/hooks

with entry by means of key latch withdrawal. Lock cylinders to be to BS EN 1303 Grade

-  	3 incorporating anti-drill and pick resistance.

-  	Provide brass door chain/limiter and door viewer.

-  	Complete with factory fitted letter box with restrictor - Letter plate to be 400mm

away from any locks.

-  	Perimeter seals: Neoprene Weather-stripping located in ploughed grooves.

-  	Other requirements: Integral or proprietary wheelchair level access threshold and

weather drip to bottom of door.

-  	Fixing: As recommended by the manufacturer to meet Secured By Design

standards.

-  	Moisture Content: 13-19%.

-  	Accuracy: To BS 4787:Part 1.

-  	Sample doorset to be presented for approval to architect and client.

-  	Door to come complete with level threshold factory fitted which meets the current

Building Regulations

-  	Protection all doors to be protected during the construction process including -

threshold - jambs - and the actual door

-  	Panelling:  Panels to be either 6no. or 4no.  Contractor to provide full sized working

samples for CA & Client approval.

All front doors to be fitted with door numbers. Style and size to be approved by Client -

colour to match ironmongery.

251B	SELECTED WOOD PANELLED COLONIAL STYLE INTERNAL DOORS GENERALLY

-  	Location refer to floor plans

-  	Manufacturer and reference:Contractors choice moulded panel smooth; Ref. Heavy

Weight

-  	Thickness: 44mm.

-  	All Doors to be ½ Hour fire rated to BS476 PT22.

-  	Sizes: As floor plans.

-  	Core: Solid flax board - min density 350 kg/m3.

-  	Facings: . Moulded smooth panel smooth skin factory primed.

-  	Lippings: To all sides, top and bottom. 6mm lipping exposed two long edges.

-  	Moisture content on delivery: 10-12%

-	   Finish:  Fully factory primed final site finished paint colour to be agreed with client.

-  	All internal door handles must be bolt through type refer to ironmongery clause for

further information.

-  	Panelling:  Panels to be either 6no. or 4no.  Contractor to provide full sized working

samples for CA & Client approval.

254B	WOOD PANELLED COLONIAL STYLE INTERNAL DOORS 1/2HOUR FIRE RATED

DOORS WITH GLAZED PANELS HOUSES - BETWEEN LIVING AREA AND DINING

-  	Manufacturer and reference: Contractors choice; moulded panel smooth; Ref.

Heavy Weight

-  	Thickness: 44mm.

-  	Sizes: As Door Schedule.

-  	Solid timber in redwood or pine to receive stain & varnish finish – ½ hour fire.

-	   Glazing: Clear 4mm single toughened safety glass.

-  	Facings: 2 Moulded smooth bottom 2 No. top glazed panels

-  	Lippings: To all sides, top and bottom. 6mm lipping exposed two long edges.

-  	Moisture content on delivery: 10-12%

-	   Finish:  Fully factory primed final site finished paint colour to be agreed with client.

-  	All internal door handles must be bolt through type refer to ironmongery clause for

further information.

-  	Panelling:  Panels to be either 6no. or 4 no. Contractor to provide full sized working

samples for CA & Client approval.

630A	HATCHES	HOUSES TO ACCESS ROOFSPACE

•	 Manufacturer: Contractor's choice - provide sample for CA approval .

-	Product reference: Proprietary thermoplastic attic hatch system .

•	 -  Min Dimensions:  680X520mm

-	Air-tight, pre-insulated phenolic insulation board infill with PVC back

-	Hinge down trap door

-	Twin latch lockable security bolt

-	Accessories:  complete with Access pole

-

EXECUTION

710	PROTECTION OF COMPONENTS

•	 General: Do not deliver to site components that cannot be installed immediately or placed

in clean, dry, floored and covered storage.

•	 Stored components: Stacked on level bearers, separated with spacers to prevent damage

by and to projecting ironmongery, beads, etc.

730	PRIMING/ SEALING

•	 Wood surfaces inaccessible after installation: Primed or sealed as specified before fixing

components.

750	FIXING DOORSETS

•	 Timing: After associated rooms have been made weathertight and the work of wet trades is

finished and dried out.

760	BUILDING IN

•	 General: Not permitted unless indicated on drawings.

770	DAMP PROOF COURSES ASSOCIATED WITH BUILT IN WOOD FRAMES

•	 Method of fixing: To backs of frames using galvanized clout nails.

780	DAMP PROOF COURSES IN PREPARED OPENINGS

•	 Location: Correctly positioned in relation to door frames. Do not displace during fixing

operations.

790	FIXING OF WOOD FRAMES

•	 Spacing of fixings (frames not predrilled): Maximum 150 mm from ends of each jamb and

at 600 mm maximum centres.

800	FIXING OF LOOSE THRESHOLDS

•	 Spacing of fixings: Maximum 150 mm from each end and at 600 mm maximum centres.

809	FIRE RESISTING/ SMOKE CONTROL DOORS/ DOORSETS

•	 Installation: By a firm currently registered under a third party accredited fire door installer

scheme in accordance with instructions supplied with the product conformity certificate,

test report or engineering assessment.

810A	FIRE RESISTING SMOKE CONTROL DOORS/ DOORSETS

•	 Gaps between frames and supporting construction: Filled as necessary in accordance with

requirements for certification and/ or door/ doorset manufacturer's instructions.

Otherwise pack gap full with mineral wool and point with intumescent mastic prior to fitting

architrave or plastering.

830	FIXING IRONMONGERY GENERALLY

•	 Fasteners: Supplied by ironmongery manufacturer.

-	Finish/ Corrosion resistance: To match ironmongery.

•	 Holes for components: No larger than required for satisfactory fit/ operation.

•	 Adjacent surfaces: Undamaged.

•	 Moving parts: Adjusted, lubricated and functioning correctly at completion.

840	FIXING IRONMONGERY TO FIRE RESISTING DOOR ASSEMBLIES

•	 General: All items fixed in accordance with door leaf manufacturer's recommendations

ensuring that integrity of the assembly, as established by testing, is not compromised.

•	 Holes for through fixings and components: Accurately cut.

-	Clearances: Not more than 8 mm unless protected by intumescent paste or similar.

•	 Lock/ Latch cases for fire doors requiring >  60 minutes integrity performance: Coated with

intumescent paint or paste before installation.

850	LOCATION OF HINGES

•	 Primary hinges: Where not specified otherwise, positioned with centre lines 250 mm from

top and bottom of door leaf.

•	 Third hinge: Where specified, positioned on centre line of door leaf .

•	 Hinges for fire resisting doors: Positioned in accordance with door leaf manufacturer's

recommendations.

L30

Stairs/ ladders/ walkways/ handrails/ balustrades

L30 Stairs/ ladders/ walkways/ handrails/ balustrades

To be read with Preliminaries/ General conditions.

PRELIMINARY INFORMATION/ REQUIREMENTS

110A	DESIGN

•	 Design standard: The following items have been designed to BS 5395 and current Building

Regulations where applicable:

Stairs, balustrades and handrails.

•	 Completion of design: Finalize details to meet structural and safety requirements of BS

5395 and current Building Regulations.

•	 Type of activity/occupancy category to BS 6399-1: A (Domestic and residential activities).

130	SITE DIMENSIONS

•	 Procedure: Before starting work on designated items take site dimensions, record on shop

drawings and use to ensure accurate fabrication.

-	Designated items: To stair & associated elements.

140	SAMPLES

•	 Provide samples of the following for approval by the architect before ordering: Stair

handrails, balustrading, support brackets, newels, infill panels and such like.

COMPONENTS

210A	WOOD STAIRS TO HOUSES TO BE CONTRACTOR DESIGNED

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Components:

-	Treads: 25 mm S/W or MDF.

-	Risers: 19 mm moisture resistant plywood.

-	Strings: S/W Redwood (min density 470 kg/m3).

-	Newels: S/W Redwood (min density 650-725 kg/m3).

-	Guarding: Balusters - S/W Redwood (min density 470 kg/m3).

-	Handrails: S/W Redwood (min density 650-725 kg/m3).

•	 Moisture content at time of installation: 9-13%.

•	 Finish as delivered: Sanded for clear staining / varnish finish.

•	 Other requirements: Newel post to be one piece with half-newels at wall returns.  Newels

and stair assembly to be protected during the works as necessary - damaged timbers will

not be acceptable on completion.

For details and dimensions refer to architects drawings.

3 SAMPLES TO BE PROVIDED OF THE HANDRAIL AND BALUSTRADES FOR

APPROVAL

460	WALKWAYSTO ALL ATTIC SPACES TO GAIN ACCESS TO AND AROUND THE

WATER TANK SAFELY

•	 Component material, grade and finish as delivered:

-	Flooring: 18mm plywood fixed on required supporting timbers and floor joists

accordingly. Min 1m wide strip to full length of attic space..

-	Guarding: 50x50mm timber battens fixed to roof trusses to act as guarding.

-	Handrails: Softwood, class J10 to BS EN 942.

•	 Workmanship:

-	Joinery: To section Z10 .

-	Metalwork: Not applicable .

•	 Other requirements: Refer to drawings to ascertain extent required .

510A	WOOD BALUSTRADES Houses

•	 Timber: Generally to BS EN 942.

-	Wood species: Softwood as National annex, table NA.1 - Redwood.

-	Appearance class: J20.

-	Moisture content at time of installation: 9–13%.

•	 Adhesive: Contractor's choice.

•	 Finish as delivered: Prepared and sealed, as section M60.

•	 Workmanship: To section Z10.

•	 Other requirements: None.

•	 Fixing: Through fixing to timber.

-	Main Contractor to provide 3 No. samples for approval by the HA

INSTALLATION

610	MOISTURE CONTENT

•	 Temperature and humidity: Monitor and control internal conditions to achieve specified

moisture content in wood components at time of installation.

620	PRIMING/SEALING/PAINTING

•	 Surfaces inaccessible after assembly/installation: Before fixing components, apply full

protective/decorative treatment/coating system.

630	CORROSION PROTECTION OF DISSIMILAR MATERIALS

•	 Components/ substrates/ fasteners of dissimilar materials: Isolate using washers/ sleeves

or other suitable means to separate materials to avoid corrosion and/ or staining.

640	INSTALLATION GENERALLY

•	 Fasteners and methods of fixing: To section Z20.

•	 Structural members: Do not modify, cut, notch or make holes in structural members, except

as indicated on drawings.

•	 Temporary support: Do not use stairs, walkways or balustrades as temporary support or

strutting for other work.

L40

General glazing

L40 General glazing

To be read with Preliminaries/ General conditions.

GENERAL REQUIREMENTS

111	PREGLAZING

•	 Pre-glazing of components: Permitted.

•	 Prevention of displacement: Submit details of precautions to be taken to protect glazing

and compound/ seals during delivery and installation.

•	 Defective/ displaced glazing/ compound/ seals: Re-glaze components in situ.

140	MATERIAL SAMPLES

•	 Representative samples of designated materials: Submit before cutting panes.

-	Sample size (minimum): Designated materials: Patterned Glass 600x600mm;

Toughened Glass 1000x1000mm.

Designated materials: -.

150	WORKMANSHIP GENERALLY

•	 Glazing generally: To BS 6262.

•	 Integrity: Glazing must be wind and watertight under all conditions with full allowance made

for deflections and other movements.

•	 Dimensional tolerances: Panes/ sheets to be within ± 2 mm of specified dimensions.

•	 Materials:

-	Compatibility: Glass/ plastics, surround materials, sealers, primers and paints/ clear

finishes to be used together to be compatible. Avoid contact between glazing panes/

units and alkaline materials such as cement and lime.

-	Protection: Keep materials dry until fixed. Protect insulating glass units and plastics

glazing sheets from the sun and other heat sources.

152	PREPARATION

•	 Surrounds, rebates, grooves and beads: Clean and prepare before installing glazing.

155A	GLASS GENERALLY

•	 Standards: To BS 952 and relevant parts of:

-	BS EN 572 for basic soda lime silicate glass.

-	BS EN 1096 for coated glass.

-	BS EN 1748-1 for borosilicate glass.

-	BS EN 1748-2 for ceramic glass.

-	BS EN 1863 for heat strengthened soda lime silicate glass.

-	BS EN 12150 for thermally toughened soda lime silicate safety glass.

-	BS EN 12337 for chemically strengthened soda lime silicate glass.

-	BS EN 13024 for thermally toughened borosilicate safety glass.

-	BS EN ISO 12543 for laminated glass and laminated safety glass.

-  ALL SAFETY GLAZING TO COMPLY WITH BS EN 356 2000 RATING P2A

•	 Panes/ sheets: Clean and free from obvious scratches, bubbles, cracks, rippling, dimples

and other defects.

-	Edges: Generally undamaged. Shells and chips not more than 2 mm deep and

extending not more than 5 mm across the surface are acceptable if ground out.

180	BEAD FIXING WITH PINS

•	 Pin spacing: Regular at maximum 150 mm centres, and within 50 mm of each corner.

•	 Exposed pin heads: Punched just below wood surface.

181	BEAD FIXING WITH SCREWS

•	 Screw spacing: Regular at maximum 225 mm centres, and within 75 mm of each corner.

TYPES OF GLAZING

370	BEAD FIXED INSULATING GLASS UNITSREFER TO SECTIONS L10, L20

•	 Pane material: Insulating glass units to BS EN 1279  and Kitemark certified.

-	Inner pane: Toughened/Float insulating glass as detailed in schedules.

-	Outer pane: Toughened/Float insulating glass as detailed in schedules.

-	Spacer: Glass manufacturers guidance.

-	Perimeter taping: Do not use.

•	 Surround/ bead: Hardwood frame with hardwood beads.

-	Preparation: Priming & sealing.

-	Bead location: Inside.

-	Bead fixing: Proprietary clip fixing.

•	 Glazing system: Preformed gasket sections supplied by window manufacturer.

•	 Glazing installation:

-	Insulating unit: Located centrally in surround using setting and location blocks.

-	Gaskets and beads: Installed as recommended by frame manufacturer.

Gasket fit at corners: Tight, without gaps.

Drainage and ventilation holes: Unobstructed.

550B	GLASS MIRRORS TO BATHROOMSALL DWELLINGS - bathroom & wc's

-  	Mirror material: Float glass, silvered to give maximum reflection, free from

tarnishing, discoloration, scratches and other defects visible in the designed viewing

conditions.

-  	Thickness: 6MM.

-  	Edge treatment: Bevelled and polished.

-  	Background: Plastered wall.

-  	Fixing method: Through mirror fixings using proprietary gaskets and chrome dome

head cover caps.

-  	Installation: Fixed accurately and securely without over tightening fasteners, to

provide a flat surface giving a distortion free reflection.

-  	MC to provide sample for approval - height to be agreed with the COW prior to

fitting onsite.

610A	WINDOW FILM MANIFESTATION WHERE REQUIRED FOR SAFETY MARKINGS

-  	Manufacturer/reference: 3M dusted crystal or other equal and approved.

-  	Design: To provide marking to large sheets of glass for safety in accordance with

building regulations where indicated on the drawings. Design as indicated on the

drawings.

-  	Application: Carried out by a firm approved by the film manufacturer in accordance

with manufacturer's recommendations.

-  	Evidence of applicator's competence and experience: Submit on request.

-  	Sample area: Complete as part of the finished work, in an approved location and

obtain approval of appearance before proceeding.

-  	Ambient air temperature at time of application: Above 5°C.

-  	Installed film: Fully adhered to the glass with no peeling, and free from bubbles,

wrinkles, cracks or tears.

-  	Further contact with applied films: Avoid until bonding adhesive has cured.

Cleaning and maintenance instructions: Submit copies.

M

Surface finishes

M10

Cement based levelling/ wearing screeds

M10 Cement based levelling/ wearing screeds

To be read with Preliminaries/General conditions.

TYPES OF SCREED

115A	CEMENT:SAND LEVELLING SCREEDSTO GROUND FLOORS OF ALL DWELLINGS

•	 Substrate:  Floor insulation board on pre-cast / insitu concrete slab as to structural

engineers specification.

•	 Screed construction: Floating, as clause 290.

-	Reinforcement for crack control: Steel fabric, as clause 392. Refer to structural

engineers specification.

•	 Thickness .

-	Nominal: 100 mm.

-	Minimum: 95 mm.

•	 Mix:

-	Proportions (cement: sand): To BS 8204-1.

•	 In situ crushing resistance (ISCR) category: To BS 8204-1.

-	Mass of test weight: 4 kg.

•	 Flatness/ Surface regularity: Maximum permissible deviation: SR1.

•	 Finish: Smooth floated, as clause 530.

-	To receive: Varies, as schedule drawing.

•	 Other requirements: Movement joints as required. Provide proprietary surface sealer as

clause 680A.

GENERALLY/PREPARATION

210	SUITABILITY OF SUBSTRATES

•	 General:

-	Suitable for specified levels and flatness/ regularity of finished surfaces. Consider

permissible minimum and maximum thicknesses of screeds.

-	Sound and free from significant cracks and gaps.

•	 Concrete strength: To BS 8204-1, Table 2.

•	 Cleanliness: Remove plaster, debris and dirt.

•	 Moisture content: To suit screed type. New concrete slabs to receive fully or partially

bonded construction must be dried out by exposure to the air for minimum six weeks.

215	SURFACE HARDNESS OF SUBSTRATES TO RECEIVE POLYMER MODIFIED

WEARING SCREEDS

•	 General: Substrates must restrain stresses that occur during setting and hardening of

wearing screeds.

•	 Test for surface hardness: To BS EN 12504-2 using a rebound hammer with compliance

values selected from the following:

Screed thickness  		Rebound hammer value

_______________________________________________

15 mm or less  		Greater than 25

Greater than 15 mm  		Greater than 30

_______________________________________________

•	 Report: Submit details of areas where substrates surface hardness does not comply with

these values.

220	PROPRIETARY LEVELLING/WEARING SCREEDS

•	 General: Materials, mix proportions, mixing methods, minimum/maximum thicknesses and

workmanship must be in accordance with recommendations of screed manufacturer.

•	 Standard: To BS 8204-3.

251	CONDUITS CAST INTO OR UNDER SCREEDS

•	 Reinforcement: Overlay with reinforcement selected from:

-	500 mm wide strip of steel fabric to BS 4483, reference D49, or

-	Welded mesh manufactured in rolls from mild steel wire minimum 1.5 mm diameter to

BS 1052, mesh size 50 x 50 mm.

•	 Placing reinforcement: Mid depth between top of conduit and the screed surface.

Screed cover over conduit (minimum): 25 mm.

255	PIPE DUCTS/ TRUNKING

•	 Preformed access ducts: Before laying screed, fix securely to substrates and level

accurately in relation to finished floor surface.

290A	FLOATING CONSTRUCTION

•	 Insulation:  [High performance rigid thermoset polyisocyanurate (PIR) insulant

manufactured with a blowing agent that has zero Ozone Depletion Potential (ODP) and

Global Warming Potential (GWP) of less than 5 in accordance with the requirements of BS

4841-1. ].

-	Standard:  [BS EN 13165].

-	Product certification:  [To be BBA and IAB certified for this application. BS EN ISO 9001:

2000/IS EN ISO9001:2008.  To be installed in accordance with the manufacturer's

instructions].

Manufacturer:  [Contractor's choice, sample to be provided for CA approval].

Face size (length x width):  [1200 x 450 mm].

Thickness (nominal):  [200 mm].

Thermal conductivity:  [Aged - 0.022 W/mK].

Reaction to fire class:  [Class 1 fire rating on both core and facings, producing less than

5% smoke obscuration when tested to BS 5111-1:1974 low risk].

Additional requirements:  [To be highly resistant to transmission of water vapour (more

than 100MN.s/g) and air movement in accordance with BS EN 12086.  Compressive

strength typically in excess of 125 kPa at 10% compression when tested to BS EN 826:

1996 (Thermal insulating products for building applications. Determination of

compression behaviour) ].

Placement: Secure with no gaps between studs of external timber frame walls.

Joints between boards, at closures and penetrations: No gaps and free from debris.

Separating layer:

-	Type: Polyethylene sheet  minimum 125 micrometres thick (500 gauge)..

-	Installation: Lay over insulation and turn up at perimeter abutments. Lap 100 mm at

joints.

BATCHING/MIXING

302	CEMENTS

•	 Cement types: In accordance with BS 8204-1, clause 5.1.3.

305	AGGREGATES

•	 Sand: To BS EN 13139.

-	Grading limits: In accordance with BS 8204-1, Table B.1.

•	 Coarse aggregates for fine concrete levelling screeds:

-	Standard: To BS EN 12620.

-	Designation: 4/10.

•	 Lightweight aggregates: To BS 8204-1, Annex A.

307	ADMIXTURES

•	 Standard: In accordance with BS 8204-1, Table 1.

•	 Calcium chloride: Do not use in admixtures.

310	BATCHING WITH DENSE AGGREGATES

•	 Mix proportions: Specified by weight.

•	 Batching: Select from:

-	Batch by weight.

-	Batch by volume: Permitted on the basis of previously established weight: volume

relationships of the particular

materials. Use accurate gauge boxes. Allow for bulking of damp sand.

311	BATCHING WITH LIGHTWEIGHT AGGREGATES

•	 Standard: To BS 8204-1, Annex A.

•	 Mix proportions: Specified by volume.

•	 Batching: Use accurate gauge boxes.

330	MIXING

•	 Water content: Minimum necessary to achieve full compaction, low enough to prevent

excessive water being brought to surface during compaction.

•	 Mixing: Mix materials thoroughly to uniform consistency. Mixes other than no-fines must be

mixed in a suitable forced action mechanical mixer. Do not use a free fall drum type mixer.

•	 Consistency: Use while sufficiently plastic for full compaction.

•	 Ready-mixed retarded screed mortar: Use within working time and site temperatures

recommended by manufacturer. Do not re-temper.

335	IN SITU CRUSHING RESISTANCE (ISCR)

•	 Standards and category: To BS 8204-1, table 4.

-	Testing of bonded and unbonded screeds: To Annex D.

-	Testing of floating levelling screeds: To Annex E.

340	ADVERSE WEATHER

•	 Screeds surface temperature: Maintain above 5°C for a minimum of four days after laying.

•	 Hot weather: Prevent premature setting or drying out.

LAYING

345	LEVEL OF SCREED SURFACES

•	 Permissible deviation: (allowing for thickness of coverings) ±5 mm from datum.

350	SCREEDING TO FALLS

•	 Minimum screed cover: Maintain at the lowest point.

•	 Falls: Gradual and consistent.

-	Gradient (minimum): As drawings .

351	SCREEDING TO RAMPS

•	 Screed cover: Maintain consistent screed depth to graduated substrate.

•	 Falls: Gradual and consistent.

355	FLATNESS/ SURFACE REGULARITY OF FLOOR SCREEDS

•	 Standard: To BS 8204-1, Table 5.

•	 Test: To BS 8204-1, Annex C.

•	 Sudden irregularities: Not permitted.

375	COMPACTION OF SCREEDS

•	 General: Compact thoroughly over entire area.

•	 Screeds over 50 mm thick: Lay in two layers of approximately equal thickness. Roughen

surface of compacted lower layer then immediately lay upper layer.

392	GENERAL REINFORCEMENT

•	 Steel fabric: To BS 4483, table 1.

-	Type: To manufacturers & Structural Engineers recommendations.

•	 Installation: In accordance with BS 8204-1.

405	JOINTS IN LEVELLING SCREEDS GENERALLY

•	 Laying screeds: Lay continuously using 'wet screeds' between strips or bays. Minimize

defined joints.

•	 Daywork joints: Form with vertical edge.

440	CRACK INDUCING GROOVES IN LEVELLING SCREEDS

•	 Groove depth: At least half the depth of screed.

•	 Cutting grooves: Straight, vertical and accurately positioned. Select from the following:

-	Trowel cut as screed is laid.

-	Saw cut sufficiently early after laying to prevent random cracking.

450A	SEALANT FOR JOINTS IN SCREEDS

•	 Type: Gin applied two part polysulfide-based, colour to approval.

•	 Preparation and application: As section Z22.

FINISHING/CURING

510	FINISHING GENERALLY

•	 Timing: Carry out all finishing operations at optimum times in relation to setting and

hardening of screed material.

•	 Prohibited treatments to screed surfaces:

-	Wetting to assist surface working.

-	Sprinkling cement.

530	SMOOTH FLOATED FINISH

•	 Finish: Even texture with no ridges or steps.

650	CURING

•	 General: Prevent premature drying. Immediately after laying, protect surface from wind,

draughts and strong sunlight. As soon as screed has set sufficiently, closely cover with

polyethylene sheeting.

•	 Curing period (minimum): Keep polyethylene sheeting in position for: period recommended

by screed manufacturer.

•	 Drying after curing: Allow screeds to dry gradually. Do not subject screeds to artificial

drying conditions that will cause cracking or other shrinkage related problems.

680A	SURFACE SEALER TO SCREEDS

•	 Manufacturer: Contractor's choice, provide sample for CA approval .

-	Product: Proprietary  surface applied sealer to PIFA Standard 6/83A or Agrément

certified.

•	 Preparation: Clean cured screed surface to remove dirt, grease, oil and other surface

contaminants.

•	 Moisture content of screed: As recommended by sealer manufacturer. Test relative

humidity to BS 8203, Annex A if required to verify suitability to receive sealer.

•	 Application: Evenly to dry surfaces using sufficient coats to form an effective seal but

without a glossy finish.

M20

Plastered/ Rendered/ Roughcast coatings

M20 Plastered/ Rendered/ Roughcast coatings

To be read with Preliminaries/ General conditions.

TYPES OF COATING

160B	PROPRIETARY CEMENT GAUGED RENDERON EXTERNAL MASONRY WALL LEAFS

AS DETAILED ON THE SITE PLAN, ELEVATIONS & SECTIONS

•	 MANUFACTURER: Contractors choice, provide details and samples for approval. 10year

warranty required.

•	 PRODUCT: Proprietary BBA approved acrylic based composite external decorative render

system. Even textured finish with 1.5mm aggregate size. Product to exactly match

similar render product applied on built up walls in relation to finish and colour .

Provide surface applied primer as necessary in accordance with manufacturers

recommendations between coats.

" Location: To specified wall areas as identified on Architect's drawings or other Contract

Documents.

" Background: Masonry suitable to take a designation III (1:1:6) mix (should be confirmed

by block manufacturer).

•	 Preparation: The nature and condition of the background is a prime consideration in

deciding the preparatory treatment prior to the application of the render. Substrate must

provide suitable key/suction. Guidance in respect to movement joints and bed joint

reinforcement should be obtained from block manufacturer and MUST be adhered to. The

recommendations detailed in BS5628 : Part 3 and BS5262 should be observed.

All surfaces other than concrete blockwork must receive a preparation coat  to allow

surface keying to manufacturers recommendations.

•	 Colour: As detailed on site layout.  Contractor to allow for any colour from any price band

of colours available, provide samples for Client & CA approval.

•	 Thickness: min 16mm (finished excluding dubbing out and keys) - ONE COAT - ONE

PASS

•	 Finish: Smooth even textured finish with trowel in accordance with manufacturers

recommendations.  Application Process to be in accordance with manufacturers

recommendations.

•	 Accessories: Proprietary compatible movement joints, stop beads, etc to be installed as

detailed and  additionally required by the system or product chosen by contractor.  All

required accessories shall be of appropriate design, gauge and material as approved by

manufacturer. Beads to be located and fixed as detailed on Architect's drawings or System

Manufacturer's details (this may involve bedding RO beads in mortar).

Angles – as per manufacturers recommended products, details and instructions: form

external angles using clean, straight chamfered timber battens.

Where meshcloth is being incorporated as treatment to areas of potential high stress it

shall be proprietary compatible mesh suitable for purpose - standard duty, balanced, open

weave, glass fibre meshcloth, coated for alkaline resistance as necessary.

All beads and stops shall be coloured to match render.

Substrate must provide suitable key / suction and incorporate movement joints and / or bed

joint reinforcement as required by the brick / block manufacturer. The recommendations

detailed in BS5628 : Part 3 and BS5262 should be observed.

Fit render only base (drip), stop and corner beads, where required, with fixings as

approved by Manufacturer

-	Mix and apply render to  thickness necessary to meet performance required.  Rule off

with a straight edge to achieve satisfactory in-plane surface. Remove all trowel marks to

develop the final colour and texture required.

General: Pre-bagged mortar must be stored completely dry and used in strict rotation of

delivery. Stack tubs of wet mixed products not more than 2 high. Do not apply any

formless wet materials in temperatures below 5ºC. Do not work in high temperatures

when flash setting of materials may occur. Provide adequate protection from frost, high

winds and precipitation during application and curing. Apply all materials in accordance

with full, detailed printed instructions.

160C	PROPRIETARY CEMENT GAUGED RENDER ON EXTERNAL BUILT UP PANEL AS

DETAILED ON THE SITE PLAN, ELEVATIONS & SECTIONS

•	 MANUFACTURER: Contractors choice, provide details and samples for approval. 10year

warranty required.

•	 PRODUCT: Proprietary BBA approved external decorative render system suitable for use

on a built up panel with acrylic based even textured finish with 1.5mm aggregate size. Product to exactly match similar render product applied on masonry walls in relation to

finish and colour . Provide surface applied primer as necessary in accordance with

manufacturers recommendations between coats.

" Location: To specified wall areas as identified on Architect's drawings or other Contract

Documents.

" Background: Proprietary calcium silicate board and built up proprietary low density

polymer modified cement based mortar render system in layers complete with proprietary

cloth mesh and primers as necessary and recommended by contractor. All products to be

compatible and tested and accredited accordingly, contractor to provide 10 year warranty

for whole construction build up.

•	 Preparation: The nature and condition of the background is a prime consideration in

deciding the preparatory treatment prior to the application of the render. Substrate must

provide suitable key/suction.

All surfaces other than concrete blockwork must receive a preparation coat  to allow

surface keying to manufacturers recommendations.

•	 Colour: As detailed on site layout.  Contractor to allow for any colour from any price band

of colours available, provide samples for Client & CA approval.

•	 Thickness: min 10mm (finished excluding dubbing out and keys)

•	 Finish: Smooth even textured finish with trowel in accordance with manufacturers

recommendations.  Application Process to be in accordance with manufacturers

recommendations.

•	 Accessories: Proprietary compatible movement joints, stop beads, etc to be installed as

detailed and additionally required by the system or product chosen by contractor.  All

required accessories shall be of appropriate design, gauge and material as approved by

manufacturer. Beads to be located and fixed as detailed on Architect's drawings or System

Manufacturer's details (this may involve incorporating beads in built up wall construction

and jointing accordingly.

Angles – as per manufacturers recommended products, details and instructions: form

external angles using clean, straight chamfered timber battens.

Where meshcloth is being incorporated as treatment to areas of potential high stress it

shall be proprietary compatible mesh suitable for purpose - standard duty, balanced, open

weave, glass fibre meshcloth, coated for alkaline resistance as necessary.

All beads and stops shall be coloured to match render.

Substrate must provide suitable key / suction and incorporate movement joints and / or bed

joint reinforcement as required by the brick / block manufacturer. The recommendations

detailed in BS5628 : Part 3 and BS5262 should be observed.

Fit render only base (drip), stop and corner beads, where required, with fixings as

approved by Manufacturer.

-	Mix and apply render to  thickness necessary to meet performance required.  Rule off

with a straight edge to achieve satisfactory in-plane surface. Remove all trowel marks to

develop the final colour and texture required.

General: Pre-bagged mortar must be stored completely dry and used in strict rotation of

delivery. Stack tubs of wet mixed products not more than 2 high. Do not apply any

formless wet materials in temperatures below 5ºC. Do not work in high temperatures

when flash setting of materials may occur. Provide adequate protection from frost, high

winds and precipitation during application and curing. Apply all materials in accordance

with full, detailed printed instructions.

280A	GYPSUM PLASTER SKIM COAT  GENERALLY ON BOARDED WALLS & BONDED

CEILINGS

•	 Plasterboard: Impact resistant board as per K10 .

-	Preparation: Bonding agent recommended by plaster / board manufacturer .

•	 Plaster: Board finish/ finish plaster to BS 1191-1, class B.

-	Manufacturer: Contractors choice, provide sample for CA approval .

Product: Proprietary multipurpose retarded hemihydrate premixed gypsum plaster to EN

13279-1 type B1/20/2.  To be suitable for substrate .

-	Thickness: minimum 2 mm .

-	Finish: Smooth.

•	 Accessories:  Beads/ stops, as clause 634.

285A	GYPSUM PLASTER BONDING COAT  GENERALLY ON BOARDED CEILINGS

•	 Plasterboard: Ceiling plasterboard and moisture resistant board as per K10 .

-	Preparation: Bonding agent recommended by plaster / board manufacturer .

•	 Plaster: Board finish/ finish plaster to BS 1191-1, class B.

-	Manufacturer: Contractors choice, provide sample for CA approval .

Product: Proprietary multipurpose retarded hemihydrate premixed gypsum undercoat

plaster to EN 13279-1 type B4/20/2 and C3/20.  To be suitable for substrate .

-	Thickness: minimum 8 mm .

-	Finish: Smooth.

•	 Accessories:  Beads/ stops, as clause 634.

•	 Other requirements: To accept skim plaster finish as clause 280A.

GENERAL

421	SCAFFOLDING

•	 General: Prevent putlog holes and other breaks in coatings.

MATERIALS AND MARKING OF MORTAR

430	READY-TO-USE CEMENT GAUGED RENDER MORTARS

•	 Time and temperature limitations: Use within limits prescribed by mortar manufacturer

-	Retempering: Restore workability with water only within prescribed time limits.

438	CEMENTS FOR MORTARS

•	 Cement: To BS EN 197-1 and CE marked.

-	Types:  		Portland cement, CEM I.

Portland slag cement, CEM II.

Portland fly ash cement, CEM II.

-	Strength class: 32.5, 42.5 or 52.5.

•	 White cement: To BS EN 197-1 and CE marked.

-	Type: Portland cement, CEM1.

-	Strength class: 52.5.

•	 Sulphate resisting Portland cement: To BS 4027 and Kitemarked.

-	Strength class: 42.5.

•	 Masonry cement: To BS EN 998-1 and Kitemarked.

440	SAND FOR CEMENT GAUGED MORTARS

•	 Standard: To BS EN 13139.

-	Grading: 0/2 or 0/4 (CP or MP); Category 2 fines.

•	 Colour and texture: Consistent. Obtain from one source.

443	LIME FOR CEMENT GAUGED MORTARS

•	 Standard: To BS EN 459-1.

-	Type: CL 90S.

445	PIGMENT FOR COLOURED MORTARS

•	 Standard: To BS EN 12878.

449	ADMIXTURES FOR CEMENT GAUGED MORTARS

•	 Suitable admixtures: Select from:

-	Air entraining (plasticizing) admixtures: To BS EN 934-2 and compatible with other

mortar constituents.

-	Other admixtures: Submit proposals.

•	 Prohibited admixtures: Calcium chloride and any admixture containing calcium chloride.

450	CHLORIDE CONTENT OF MORTARS

•	 Chloride content (maximum): 0.1% by dry mass.

495	MIXING

•	 Render mortars (site prepared):

-	Batching: By volume. Use clean and accurate gauge boxes or buckets.

-	Mix proportions: Based on damp sand. Adjust for dry sand.

-	Lime:sand: Mix thoroughly. Allow to stand, without drying out, for at least 16 hours

before using.

•	 Mixes: Of uniform consistence and free from lumps. Do not retemper or reconstitute mixes.

•	 Contamination: Prevent intermixing with other materials.

497	COLD WEATHER

•	 General: Do not use frozen materials or apply coatings on frozen or frost bound substrates.

•	 External work: Avoid when air temperature is at or below 5°C and falling or below 3°C and

rising. Maintain temperature of work above freezing until coatings have fully hardened.

•	 Internal work: Take precautions to enable internal coating work to proceed without

detriment when air temperature is below 3°C.

PREPARING SUBSTRATES

510	SUITABILITY OF SUBSTRATES

•	 Soundness: Free from loose areas and significant cracks and gaps.

•	 Cutting, chasing, making good, fixing of conduits and services outlets and the like:

Completed.

•	 Tolerances: Permitting specified flatness/ regularity of finished coatings.

•	 Cleanliness: Free from dirt, dust, efflorescence and mould, and other contaminants

incompatible with coatings.

527	RAKING OUT FOR KEY

•	 Joints in existing masonry: Rake out to a depth of 13 mm (minimum).

Dust and debris: Remove from joints.

531	ROUGHENING FOR KEY

•	 Substrates: Roughen thoroughly and evenly.

Depth of surface removal: Minimum necessary to provide an effective key.

541	BONDING AGENT APPLICATION

•	 General:  Apply evenly to substrate to achieve effective bond of plaster/ render coat.

Protect adjacent joinery and other surfaces.

BACKINGS/ BEADS/ JOINTS

600	ADDITIONAL FRAMING SUPPORTS FOR BACKINGS

•	 Framing: Accurately position and securely fix to give full support to fixtures, fittings and

service outlets.

•	 Support board edges and perimeters: As recommended by board manufacturer to suit type

and performance of board.

605	GYPSUM PLASTERBOARD BACKINGS

•	 Type: To BS 1230, type 1.

-	Core density (minimum): 650 kg/m³.

•	 Exposed surface and edge profiles: Suitable to receive specified plaster finish.

610	FIXING PLASTERBOARD BACKINGS TO TIMBERGENERALLY

•	 Fixings, accessories and installation methods: As recommended by board manufacturer.

•	 Fixing: At the following centres (maximum):

-	Nails: 150 mm.

-	Screws to partitions/ walls: 300 mm. Reduce to 200 mm at external angles.

-	Screws to ceilings: 230 mm.

•	 Position of nails/ screws from edges of boards (minimum):

-	Bound edges: 10 mm.

-	Cut/ unbound edges: 13 mm.

•	 Position of nails/ screws from edges of supports (minimum): 6 mm.

•	 Nail/ screw heads: Set below surface. Do not break paper or gypsum core.

612	JOINTS IN PLASTERBOARD BACKINGS

•	 Ceilings:

-	Bound edges: At right angles to supports and with ends staggered in adjacent rows.

-	Two layer boarding: Stagger joints between layers.

•	 Partitions/ walls:

-	Vertical joints: Centre on studs. Stagger joints on opposite sides of studs.

Two layer boarding: Stagger joints between layers.

-	Horizontal joints:

Two layer boarding: Stagger joints between layers by at least 600 mm. Support edges of

outer layer.

•	 Joint widths (maximum): 3 mm.

630	BEADS/ STOPS FOR INTERNAL USE

•	 Material: Galvanized steel to BS 6452-1.

640	BEADS/ STOPS GENERALLY

•	 Location: External angles and stop ends except where specified otherwise.

•	 Corners: Neat mitres at return angles.

•	 Fixing: Secure, using longest possible lengths, plumb, square and true to line and level,

ensuring full contact of wings with substrate.

-	Beads/ stops for external render: Fix mechanically.

•	 Finishing: After coatings have been applied, remove surplus material while still wet, from

surfaces of beads/ stops exposed to view.

646	CRACK CONTROL AT JUNCTIONS BETWEEN DISSIMILAR SOLID SUBSTRATES

•	 Locations: Where defined movement joints are not required. Where dissimilar solid

substrate materials are in same plane and rigidly bonded or tied together.

•	 Crack control materials:

-	Isolating layer: Building paper to BS 1521.

-	Metal lathing: Externally: Stainless steel ribbed expanded metal.

•	 Installation: Fix metal lathing over isolating layer. Stagger fixings along both edges of

lathing.

•	 Width of installation over single junctions:

-	Isolating layer: 150 mm.

-	Lathing: 300 mm.

•	 Width of installation across face of dissimilar substrate material (column, beam, etc. with

face width not greater than 450 mm):

-	Isolating layer: 25 mm (minimum) beyond junctions with adjacent substrate.

Lathing: 100 mm (minimum) beyond edges of isolating layer.

659	PLASTERBOARD JOINTS

•	 Joints and angles (except where coincident with metal beads). Reinforce with continuous

lengths of jointing tape.

673	PLASTERING OVER CONDUITS/ SERVICE CHASES

•	 General: Prevent cracking over conduits and other services.

•	 Services chased into substrate: Isolate from coating by covering with galvanized metal

lathing, fixed at staggered centres along both edges.

INTERNAL PLASTERING

710	APPLICATION GENERALLY

•	 Application of coatings: Firmly and in one continuous operation between angles and joints.

Achieve good adhesion.

•	 Appearance of finished surfaces: Even and consistent. Free from rippling, hollows, ridges,

cracks and crazing.

-	Accuracy: Finish to a true plane, to correct line and level, with angles and corners to a

right angle unless specified otherwise, and with walls and reveals plumb and square.

•	 Drying out: Prevent excessively rapid or localized drying out.

715	FLATNESS/ SURFACE REGULARITY

•	 Sudden irregularities: Not permitted.

•	 Deviation of plaster surface: Measure from underside of a straight edge placed anywhere

on surface.

-	Permissible deviation (maximum) for plaster not less than 13 mm thick: 3 mm in any

consecutive length of 1800 mm.

720	DUBBING OUT

•	 General: Correct substrate inaccuracies.

•	 New smooth dense concrete and similar surfaces: Dubbing out prohibited unless total

plaster thickness is within range recommended by plaster manufacturer.

•	 Thickness of any one coat (maximum): 10 mm.

•	 Mix: As undercoat.

•	 Application: Achieve firm bond. Allow each coat to set sufficiently before the next is

applied. Cross scratch surface of each coat.

725	UNDERCOATS GENERALLY

•	 General: Rule to an even surface. Cross scratch to provide a key for the next coat.

•	 Undercoats on metal lathing: Work well into interstices to obtain maximum key.

•	 Undercoats gauged with Portland cement: Do not apply next coat until drying shrinkage is

substantially complete.

742	THIN COAT PLASTER

•	 Preparation for plasters less than 2 mm thick: Fill holes, scratches and voids with finishing

plaster.

747	PROJECTION PLASTER

•	 Application: Evenly and in one continuous operation between angles and joints.

•	 Finish: A level open textured surface before finishing manually.

777	SMOOTH FINISH

•	 Appearance: A tight, matt, smooth surface with no hollows, abrupt changes of level or

trowel marks. Avoid water brush, excessive trowelling and over polishing.

M40

Stone/ concrete/ quarry/ ceramic tiling/ mosaic

M40 Stone/ concrete/ quarry/ ceramic tiling/ mosaic

To be read with Preliminaries/ General conditions.

TYPES OF TILING/ MOSAIC

110A	TILING TO WALLS3 NO. ROWS OF SPASHBACKS ABOVE WASH HAND BASINS IN

TOILETS & BATHROOMS AND ABOVE KITCHEN WORKTOPS (FULL HEIGHT TO

2100mm AT COOKER & EXTRACTOR LOCATIONS

•	 Tiles: Ceramic wall tiles to BS EN 14411.

-	Manufacturer/ Supplier: Contractors choice, provide 3no. samples for CA approval.

Product: To be confirmed by CA.

-	Colour: Contractor to provide plain colour samples, CA to choose colour.

-	Finish: Glazed.

-	Size: 150 x 150 mm.

-	Thickness: 6mm minimum.

-	Slip potential:

Slip resistance value (SRV) (minimum)/ Pendulum test value (PVT) (minimum) to BS

7932: Not applicable.

Surface roughness (Rz) (minimum) to BS 1134: Not applicable.

•	 Background/ Base: Impact resistant plasterboard as K10. Tiling must not be applied to a

skim finish.

-	Preparation: Not applicable.

•	 Intermediate substrate: Not required.

•	 Bedding: Thin bed adhesive - solid, as clause 651.

-	Reinforcement: Not applicable.

-	Adhesive: Contractor's choice, to be proprietary waterproof ready-made adhesive

suitable for purpose, background and specific installation.

•	 Joint width: As spacer lugs.

•	 Grout: Contractor's choice, to be proprietary waterproof ready-made adhesive suitable for

purpose, background and specific installation.  To be compatible with tile

manufacturer/supplier recommendations. Contractor to provide plain colour samples, CA to

choose colour.

-	Type/ classification: RG.

•	 Movement joints: At all internal corners and in accordance with tile manufacturer/supplier

recommendations.

•	 Accessories: PVC tile edge trims throughout to tiling perimeter.

110B	TILING TO WALLSFULL HEIGHT TO CEILING ABOVE BATHS

•	 Tiles: Ceramic wall tiles to BS EN 14411.

-	Manufacturer/ Supplier: Contractors choice, provide 3no. samples for CA approval.

Product: To be confirmed by CA.

-	Colour: Contractor to provide plain colour samples, CA to choose colour.

-	Finish: Glazed.

-	Size: 150 x 150 mm.

-	Thickness: 6mm minimum.

-	Slip potential:

Slip resistance value (SRV) (minimum)/ Pendulum test value (PVT) (minimum) to BS

7932: Not applicable.

Surface roughness (Rz) (minimum) to BS 1134: Not applicable.

•	 Background/ Base: Impact resistant plasterboard as K10. Tiling must not be applied to a

skim finish.

-	Preparation: Not applicable.

•	 Intermediate substrate: Not required.

•	 Bedding: Thin bed adhesive - solid, as clause 651.

-	Reinforcement: Not applicable.

-	Adhesive: Contractor's choice, to be proprietary waterproof ready-made adhesive

suitable for purpose, background and specific installation.

•	 Joint width: As spacer lugs.

•	 Grout: Contractor's choice, to be proprietary waterproof ready-made adhesive suitable for

purpose, background and specific installation.  To be compatible with tile

manufacturer/supplier recommendations. Contractor to provide plain colour samples, CA to

choose colour.

-	Type/ classification: RG.

•	 Movement joints: At all internal corners and in accordance with tile manufacturer/supplier

recommendations.

•	 Accessories: PVC tile edge trims throughout to tiling perimeter.  Proprietary PVC bath

sealant movement strip to maintain waterproof seal where bath meets tiling.

112A	TILING HORIZONTALLYTO TIMBER STUD PANELS TO BOTTOM OF BATHS

•	 Tiles: Ceramic wall tiles to BS EN 14411.

-	Manufacturer/ Supplier: Contractors choice, provide 3no. samples for CA approval.

Product: To be confirmed by CA.

-	Colour: Contractor to provide plain colour samples, CA to choose colour.

-	Finish: Glazed.

-	Size: 150 x 150 mm.

-	Thickness: 6mm minimum.

-	Slip potential:

Slip resistance value (SRV) (minimum)/ Pendulum test value (PVT) (minimum) to BS

7932: Not applicable.

Surface roughness (Rz) (minimum) to BS 1134: Not applicable.

•	 Background/ Base: Marine grade plywood.

-	Preparation: Not applicable.

•	 Intermediate substrate: Not required.

•	 Bedding: Thin bed adhesive - solid, as clause 651.

-	Reinforcement: Not applicable.

-	Adhesive: Contractor's choice, to be proprietary waterproof ready-made adhesive

suitable for purpose, background and specific installation.

•	 Joint width: As spacer lugs.

•	 Grout: Contractor's choice, to be proprietary waterproof ready-made adhesive suitable for

purpose, background and specific installation.  To be compatible with tile

manufacturer/supplier recommendations. Contractor to provide plain colour samples, CA to

choose colour.

-	Type/ classification: RG.

•	 Movement joints: At all internal corners and in accordance with tile manufacturer/supplier

recommendations.

•	 Accessories: PVC tile edge trims throughout to tiling perimeter and corner stop bead to

edge of panel.

GENERAL

210	SUITABILITY OF BACKGROUNDS/ BASES

•	 Background/ base tolerances: To permit specified flatness/ regularity of finished surfaces

given the permissible minimum and maximum thickness of bedding.

•	 New background drying times (minimum):

-	Concrete walls: 6 weeks.

-	Brick/ block walls: 6 weeks.

-	Rendering: 2 weeks.

-	Gypsum plaster: 4 weeks.

•	 New base drying times (minimum):

-	Concrete slabs: 6 weeks.

-	Cement:sand screeds: 3 weeks.

215	FALLS IN THE BASES

•	 General: Give notice if falls are inadequate.

250	SAMPLES

•	 General: Submit representative samples of the following:

Each type of tile.

PREPARATION

380	NEW PLASTER

•	 Plaster: Dry, solidly bedded, free from dust and friable matter.

•	 Plaster primer: Apply if recommended by adhesive manufacturer.

390	PLASTERBOARD BACKGROUNDS

•	 Boards: Dry, securely fixed and rigid with no protruding fixings and face to receive

decorative finish exposed.

460	SMOOTHING UNDERLAYMENT

•	 Type: Recommended by adhesive manufacturer.

•	 Condition: Allow to dry before tiling.

FIXING

510	FIXING GENERALLY

•	 Colour/shade: Unintended variations within tiles for use in each area/room are not

permitted.

-	Variegated tiles: Mix thoroughly.

•	 Adhesive: Compatible with background/base. Prime if recommended by adhesive

manufacturer.

•	 Cut tiles: Neat and accurate.

•	 Fixing: Provide adhesion over entire background/base and tile backs.

•	 Final appearance: Before bedding material sets, make adjustments necessary to give true,

regular appearance to tiles and joints when viewed under final lighting conditions.

•	 Surplus bedding material: Clean from joints and face of tiles without disturbing tiles.

530A	SETTING OUT

•	 Joints: True to line, continuous and without steps.

-	Joints on walls: Horizontal, vertical and aligned round corners.

-	Joints in floors: Parallel to the main axis of the space or specified features.

•	 Cut tiles: Minimize number, maximize size and locate unobtrusively.

•	 Joints in adjoining floors and walls: Align.

•	 Joints in adjoining floors and skirtings: Align.

•	 Movement joints: Where locations are not indicated, submit proposals.

550	FLATNESS/ REGULARITY OF TILING

•	 Sudden irregularities: Not permitted.

•	 Deviation of surface: Measure from underside of a 2 m straightedge placed anywhere on

surface. The straightedge should not be obstructed by the tiles and no gap should be

greater than 3 mm.

560	LEVEL OF TILING ACROSS JOINTS

•	 Deviation (maximum) between tile surfaces either side of any type of joint:

-	1 mm for joints less than 6 mm wide.

-	2 mm for joints 6 mm or greater in width.

578	CRACK CONTROL REINFORCEMENT

•	 Type to BS 4483: To tile manufacturers guidance.

•	 Installation: Place centrally in depth of bed. Lap not less than 100 mm and securely tie

together with steel wire.

•	 Corners: Avoid a four layer build at corners.

651	THIN BED ADHESIVE - SOLID (WALLS)

•	 Application: Apply floated coat of adhesive to dry background in areas of about 1 m². Comb

surface.

•	 Tiling: Apply thin even coat of adhesive to backs of dry tiles. Press tiles firmly onto float

coat.

•	 Finished adhesive thickness (maximum): 3 mm.

MOVEMENT JOINTS/ GROUTING/ COMPLETION

825A	STRIP MOVEMENT JOINTSGENERALLY as required

•	 Manufacturer: Contractors choice, provide sample for CA approval .

-	Product: PVC to BS5385-1 to maintain watertight seal .

-	Colour: Contractor to provide plain colour samples, CA to choose colour .

•	 Joint width: 4mm .

•	 Fixing to base: Bed in adhesive and screw to base .

•	 Joints: Extend through tiles and bedding to base.

875	GROUTING

•	 Sequence: Grout when bed/adhesive has set sufficient to prevent disturbance of tiles.

•	 Joints: 6 mm deep (or depth of tile if less). Free from dust and debris.

•	 Grouting: Fill joints completely, tool to profile, clean off surface. Leave free from blemishes.

-	Profile: Slightly concave.

•	 Polishing: When grout is hard, polish tiling with a dry cloth.

M50

Rubber/ plastics/ cork/ lino/ carpet tiling/ sheeting

M50 Rubber/ plastics/ cork/ lino/ carpet tiling/ sheeting

To be read with Preliminaries/ General conditions.

TYPES OF COVERING

150B	VINYL SHEETING TO COMMUNAL AREAS, KITCHENS, BATHROOMS AND

ENTRANCE LOBBIES - NOT THE FUTURE SHOWER LOCATION heterogeneous vinyl

sheet

A heavy duty 2.0mm thick heterogeneous vinyl sheet available in wood, stone, and

abstract designs in 113 colourways. It must be a low maintenance vinyl flooring with a unique PUR Pearl textured surface and 0.7mm 100% PVC wear layer for a high scratch

resistance with a R10 slip resistance. Print must be an environmentally friendly water-based ink. The product must have on average a 25% recycled content. It can be installed in all general purpose areas requiring an R10 slip resistance, toilets and work areas where foot safety is important. It must also meet the European air quality requirements as defined

by AGBB Dibt.

Base Preparation:

The subfloor to be smooth, clean, free from grease and dirt and in accordance with BS

8203 or DIN 18 365. Pre-Cast stairs may require buffing on filling to get the base to the

required finish for the fixing of the vinyl.

Smoothing underlayment compound:

Under all vinyl apply a smoothing and levelling compound as clause 461a.

Moisture suppressing DPM:

Where necessary with rising or residual moisture apply a 2 coat epoxy primer DPM.

Flooring Material

Flooring roll: R10 Low Maintenance Vinyl Flooring in 113 Colourways with a PUR Pearl

textured surface

BS EN 685 class: 34 / 43 – 2.0mm thick heterogeneous sheet

Manufacturer: Submit proposals

Product reference: submit proposals - R10 - Client should be able to choose from a

complete range of colours & patterns

Width: 2000 mm

Thickness: 2.0mm

Colour/pattern: To be chosen by the Housing Association - stone effect, timber effect & weave effect all to be available

Adhesive (and primer if recommended by manufacturer): Adhesive.

Seam welding: All seams to be correctly grooved out and heat welded with matching weld

rod.  Final finish trimming to be carried out when the weld has cooled

Accessories:

-	SW Timber skirting - a bead of white silicon is to seal the floor and the skirting around

the perimeter of the flooring

-	A flat stainless trim is to be installed at all door openings or where the flooring only

covers half a room to protect exposed edges of the flooring as per clause 740a

Finishing: As clause 820a

150C	VINYL SHEETING THROUGHOUT TO GROUND FLOOR  WC (FOR  FUTURE				SHOWER LOCATION WET AREA)Heterogeneous PVC - R10 Class B required under bare foot in		wet and dry conditions

Base Preparation:

The subfloor to be smooth, clean, free from grease and dirt and in accordance with BS

8203 or DIN 18 365.

Smoothing underlayment compound:

Under all vinyl apply a smoothing and levelling compound as clause 461a.

Moisture suppressing DPM:

Where necessary with rising or residual moisture apply a 2 coat epoxy primer DPM.

Flooring roll: Heterogeneous PVC to BS EN 649.

Manufacturer: Submit proposals - minimum 10 year warranty.

Product reference: submit proposals - R10 Class B with a slip resistance coefficiency

(to slip resistance) of 43 to BS EN 685 required under bare foot in wet and dry

conditions - Client should be able to choose from a complete range of colours.

Width: 2000 mm.

Thickness: 2.0 mm.

Colour/ pattern: As per finishes Schedule

Adhesive (and primer if recommended by manufacturer): A polyurethane resin and

hardener, water-resistant 2-component PU-adhesive.

Seam welding: Hot welding with matching coloured rod.

Accessories: Provide compatible PVC coved skirting to whole perimeter of room.

Transition bars as 740a

Skirtings, as clause 770a.

Finishing: As clause 820a

GENERAL REQUIREMENTS

210	WORKMANSHIP GENERALLY

•	 Base condition after preparation: Rigid, dry, sound, smooth and free from grease, dirt and

other contaminants.

•	 Finished coverings: Accurately fitted, tightly jointed, securely bonded, smooth and free

from air bubbles, rippling, adhesive marks and stains.

220	SAMPLES

•	 Covering samples: Before placing orders, submit representative sample of each type.

230	CONTROL SAMPLES

•	 General: Complete areas of finished work in approved locations as follows, and obtain approval of appearance before proceeding: - .

250	LAYOUT - ROLL MATERIALS

•	 Setting out of seams: Before placing orders agree setting out for sheeting types

251A	LAYOUT - SEAMS IN ROLL MATERIALS

•	 Setting out: Minimise occurrences of seams and cross seams.

•	 Cross seams: Not permitted. -. 
	252	LAYOUT - PATTERNS

•	 Setting out: Before placing orders agree setting out for covering types M50/ - .

270	EXTRA MATERIAL

•	 Provision of extra material: At completion, hand to Employer extra material of each type of

covering to extent of tbc.

330	COMMENCEMENT

•	 Required condition of works prior to laying materials:

-	Building is weathertight and well dried out.

-	Wet trades have finished work.

-	Paintwork is finished and dry.

-	Conflicting overhead work is complete.

-	Floor service outlets, duct covers and other fixtures around which materials are to be cut

are fixed.

•	 Notification: Submit not less than 48 hours before commencing laying.

340	CONDITIONING

•	 Prior to laying: Condition materials by unpacking and separating in spaces where they are

to be laid. Maintain resilient flooring rolls in an upright position. Unroll carpet and keep flat

on a supporting surface.

•	 Conditioning time and temperature (minimum): As recommended by manufacturer with

time extended by a factor of two for materials stored or transported at a temperature of less

than 10°C immediately prior to laying.

350	ENVIRONMENT

•	 Temperature and humidity: Before, during and after laying, maintain approximately at

levels which will prevail after building is occupied.

•	 Ventilation: Before during and after laying, maintain adequate provision.

PREPARING BASES

410	NEW BASES

•	 Suitability of bases and conditions within any area: Commencement of laying of coverings

will be taken as acceptance of suitability.

430	NEW WET LAID BASES

•	 Base drying aids: Not used for at least four days prior to moisture content testing.

•	 Base moisture content test: Carry out in accordance with BS 5325, Annexe A or BS 8203,

Annexe A.

-	Locations for readings: In all corners, along edges, and at various points over area being

tested.

•	 Commencement of laying coverings: Not until all readings show 75% relative humidity or

less.

440	SUBSTRATES TO RECEIVE THIN COVERINGS

•	 Trowelled finishes: Uniform, smooth surface free from trowel marks and other blemishes.

Abrade suitably to receive specified floor covering material.

461A	SMOOTHING/ LEVELLING UNDERLAYMENT COMPOUND

•	 Manufacturer: Contractors Choice .

-	Product reference: Contractors choice .

-	Thickness: Feather edge 1mm to any depth

Floor Coverings:  Linoleum, vinyl, carpet

LAYING COVERINGS

610	SETTING OUT TILES

•	 Method: Set out from centre of area/ room, so that wherever possible:

-	Tiles along opposite edges are of equal size.

-	Edge tiles are more than 50% of full tile width.

620	COLOUR CONSISTENCY

•	 Finished work in any one area/ room: Free from banding or patchiness.

640	ADHESIVE FIXING GENERALLY

•	 Adhesive: Type to be as specified, recommended by covering/ underlay manufacturer or

as approved.

•	 Primer: Use and type as recommended by adhesive manufacturer.

•	 Application: As necessary to achieve good bond.

•	 Finished surface irregularities: Trowel ridges and high spots caused by particles on the

substrate not acceptable.

650	SEAMS

•	 Patterns: Matched.

•	 Joints: Tight without gaps.

680	SEAM WELDING COVERINGS

•	 Commencement: Not before a period of 24 hours after laying, or until adhesive has set.

•	 Joints: Neat, smooth, strongly bonded, flush with finished surface.

720	DOORWAYS

•	 Joint location: On centre line of door leaf.

740A	EDGINGS/ COVER STRIPS

•	 Manufacturer: contractors choice .

-	Product reference: convex transition bar .

•	 Material/ finish: Stainless steel .

Length 2.4m long strips - cut to suit application

•	 Fixing: Secure (using matching fasteners where exposed to view) with edge of covering

gripped.

740B	EDGINGS/ COVER STRIPS - SIDE OF STAIRS

•	 Manufacturer: contractors choice .

-	Product reference: x grip edge .

•	 Material/ finish: Stainless steel .

•	 Fixing: Secure (using matching fasteners where exposed to view) with edge of covering

gripped.

770A	SKIRTINGS TO GF WCs

•	 Types: Self coved skirting, compatible with clause 150A.

•	 Manufacturer: Contractors choice - provide sample for CA approval.

-	Product reference: Homogenous uPVC with proprietary coving support as necessary.

•	 Fixing: Secure with top edge straight and parallel with floor.

-	Cove former: 38mmFold tapered to architraves. Securely bond to base and

background using contact adhesive.

-	Accurately mitre at corners.

-	Top edge trim: HCS48 PVC capping strip to all other areas.

-	Securely bond to background using contact adhesive, with top edge straight and parallel

with floor.

-	Turn flooring material up wall, securely bond to cove former and background using

adhesive specified for fixing to base, and ease top of material into edge trim.

-	Accurately mitre at corners.

-	All joints to be hot welded in accordance with the manufacturer's instructions.

Height: to be 150mm

COMPLETION

820A	FINISHING-

•	 Cleaning operations:

-	Wash floor with water containing neutral (pH 6-9) detergent. If necessary, lightly scrub

heavily soiled areas.

-	Rinse with clean water, removing surplus to prevent damage to adhesive. Allow to dry.

•

880	WASTE

•	 Spare covering material: Retain suitable material for patching. On completion submit

pieces for selection. Hand over selected pieces to Employer.

M60

Painting/clear finishing

M60 Painting/clear finishing

To be read with Preliminaries/General conditions.

COATING SYSTEMS

110A	EMULSION PAINT TO ALL HOUSES CEILINGS

•	 Manufacturer: Contractors choice.

-	Product reference: Submit proposals.

•	 Surfaces: New interior plaster skimmed ceilings.

-	Preparation: All surfaces to be clean, suitably dry, free from plaster fines and anything

that will interfere with the adhesion of the materials to be applied. Remove any loose

material or efflorescence by scraping and dry bristle brushing. Fill any small surface

defects with Trade Ready Mixed Filler or fine surface filler as appropriate. Allow to dry.

Rub down with a fine grade abrasive paper. Remove all dust .

•	 Initial coats: Apply a mist coat of Trade Matt Vinyl Emulsion thinned in accordance with the

manufacturer's instructions, over all areas to be decorated. Allow a minimum drying time of

4 hours in normal drying conditions .

•	 -  Number of coats: One .

•	 Undercoats: As recommended by manufacturer .

•	 Finishing coats: Apply Trade Matt Vinyl Emulsion  .

-	Number of coats: Minimum 2no. full coats.

•	 Colour: Contractor to make any BS & RAL colour available, CA to confirm colour.

Do not apply coatings when the air or substrate temperatures are likely to fall below 5°C

(solvent-borne primer) or 8°C (water-borne primer and finishing coats) or when the relative

humidity is above 80% during application or the drying period .

130B	GLOSS PAINT TO INTERNAL EXPOSED MDF - boxing out, framing, sill boards etc

•	 Manufacturer: Contractors Choice .

-	Product reference: Acrylic Gloss System .

•	 Surfaces: Preprimed and sealed .

-	Preparation: Primed or base stained smooth planed joinery:

All surfaces to be sound, clean and free from anything that will interfere with the

adhesion of the materials to be applied. Prior to painting, the moisture content should not

exceed 18%. Denib using a fine grade Scotch Brite Pad (grey) or a fine grade abrasive

paper. Do not break the surface of the base coating. Remove all dust.

Localised damage or deterioration due to exposure of factory base coating for longer

than 4 months to be treated with one coat of Trade Exterior Primer-Undercoat,

by brush. Allow a minimum drying time of 16 hours in normal drying conditions .

•	 Initial coats: Prime all areas to be decorated with one coat of Primer-Undercoat, by brush.

Ensure end grain is well coated. The wet film thickness must not be less than 67

micrometres. Allow a minimum drying time of 3 hours in normal drying conditions.

Denib using a fine grade abrasive paper. Do not break the surface of the coating. Remove

all dust .

-	Number of coats: 1 .

•	 Undercoats: As recommended by manufacturer .

-	Number of coats: - .

•	 Finishing coats: Acrylic Gloss .

-	Number of coats: Apply by fine, soft long filament bristle brush to an even thickness. Stir

well before use. Maintain a wet edge. On timber, lay off in the direction of the grain.

Ensure end grain is well coated. The wet film thickness of each coat must not be less

than 63 micrometres. Allow a minimum drying time of 6 hours between coats in normal

drying conditions.

Do not apply coatings when air or substrate temperatures are likely to fall below 5°C

(initial and preparatory coats) or 8°C (finishing coats) or when the relative humidity is

above 80% during application or the drying period.

Apply a suitable exterior capping sealant to cover the joint between glass, glazing

system and decorated beads to prevent water ingress. Do not overcoat.

Apply a suitable approved perimeter sealant to window and door frames to prevent water

ingress. Do not overcoat .

160	DECORATIVE WOODSTAIN/ VARNISH/ PRESERVATIVETO EXTERNAL TIMBER

WHERE REQUIRED

•	 Manufacturer: Contractors Choice - provide samples for CA approval .

-	Product reference: Stain finish - to be highly durable, medium build, solvent-borne

woodstain that provides a highly translucent, satin finish.  Stain to have resistance to UV

radiation and be micro porous and water-repellent .

•	 Surfaces: External wood-  canopies .

-	Preparation: Ensure surfaces are sound, dry and free from all defective or poorly

adhering material, dirt, grease, wax or oil. Avoid damaging factory applied coatings.

Carefully scrape back to a firm edge all areas of poorly adhering or defective coatings

and rub down to 'feather' broken edges. Completely remove all incompatible, blistered or

failed existing coatings - where flaking has occurred or coatings are defective, the entire

member or section should be stripped back to the nearest joint. Open-up all joints which

are not tight fitting and rake out thoroughly. Cut out and replace areas of rotten wood

and replace with suitably preservative treated wood. Abrade in the direction of the grain

to remove any grey denatured timber, raised grain and round all sharp edges to a 3 mm

Fold, to produce a smooth, clean surface, taking care not to damage the timber, and

dust off.

Wash down with a suitable detergent solution to remove dirt, chalking paint, corrosion

products and other contaminants. Rinse off with clean water and ensure all surfaces are

fully dry before proceeding

Wash down previously coated surfaces with soap and water, detergent solution or

suitable solvent. Whilst wet rub down the surfaces with a suitable abrasive working in the

direction of the grain to produce the necessary 'key' for good adhesion. Finally rinse

down and allow to dry.

Remove oils from surface by wiping with White Spirit.

Note Dulux Trade Thinner Number 41 is described as Harmful and Dangerous for the

Environment. Read the Safety, Health & Environmental Information on the container

before using this product

Carefully remove any plaster or mortar deposits.

Remove all mould or organic growth by careful scraping and brushing using a stiff fibre

brush and then apply Multi-Surface Fungicidal Wash by brush (do not spray). Mix

thoroughly by shaking the container. Leave for 24 hours and then thoroughly rinse and

scrub with clean water to remove residues and dead growth. Failure to remove residues

may result in discolouration of subsequently applied coatings. Repeat the process if

necessary. On badly affected areas or where lichen is present, the use of high pressure

water-hosing may be necessary to remove all organic growth completely. Do not apply

when the temperature is below 10°C or when there is a likelihood of rain, fog or frost.

Note this product is described as Irritant. Read the Safety, Health & Environmental

Information on the container before using this product

Make good all nail holes and open joints with a suitable stopper/ filler designed for use

with a woodstain system. Allow the material to set before rubbing down and dusting off.

Glazing should be carried out with a suitable flexible glazing compound following the

manufacturers instructions. Bead glazing: Base coated beads should be set down onto a

suitable flexible glazing compound/ mastic (following the manufacturer’s instructions)

before fixing down firmly .

•	 Initial coats: Preservative Basecoat as necessary. Note this product is described as

Harmful. Read the Safety, Health & Environmental Information on the container before

using this product .

-	Number of coats: 1 coat .

•	 Finishing coats: As recommended by manufacturer .

Number of coats: As recommended by manufacturer. Minimum 2no full coats .

161A	DECORATIVE WOODSTAIN/ VARNISH/ PRESERVATIVETO INTERNAL TIMBER

DOORS & JOINRY AS DETAILED

•	 Manufacturer: Contractors Choice - provide samples for CA approval .

-	Product reference: Hard wearing natural timber stain (oil based) with protective clear

varnish finish .

•	 Surfaces: Internal timber doors, skirtings, architraves, and staircases etc .

-	Preparation: Ensure surfaces are sound, dry and free from all defective or poorly

adhering material, dirt, grease, wax or oil. Avoid damaging factory applied coatings.

Carefully scrape back to a firm edge all areas of poorly adhering or defective coatings

and rub down to 'feather' broken edges. Completely remove all incompatible, blistered or

failed existing coatings - where flaking has occurred or coatings are defective, the entire

member or section should be stripped back to the nearest joint. Open-up all joints which

are not tight fitting and rake out thoroughly. Cut out and replace areas of rotten wood

and replace with suitably preservative treated wood. Abrade in the direction of the grain

to remove any grey denatured timber, raised grain and round all sharp edges to a 3 mm

Fold, to produce a smooth, clean surface, taking care not to damage the timber, and

dust off.

Wash down with a suitable detergent solution to remove dirt, chalking paint, corrosion

products and other contaminants. Rinse off with clean water and ensure all surfaces are

fully dry before proceeding

Carefully remove any plaster or mortar deposits.

Remove all mould or organic growth by careful scraping and brushing using a stiff fibre

brush and then apply Multi-Surface Fungicidal Wash by brush (do not spray). Mix

thoroughly by shaking the container. Leave for 24 hours and then thoroughly rinse and

scrub with clean water to remove residues and dead growth. Failure to remove residues

may result in discolouration of subsequently applied coatings. Repeat the process if

necessary. On badly affected areas or where lichen is present, the use of high pressure

water-hosing may be necessary to remove all organic growth completely. Do not apply

when the temperature is below 10°C or when there is a likelihood of rain, fog or frost.

Note this product is described as Irritant. Read the Safety, Health & Environmental

Information on the container before using this product

Make good all nail holes and open joints with a suitable stopper/ filler designed for use

with a woodstain system. Allow the material to set before rubbing down and dusting off.

Glazing should be carried out with a suitable flexible glazing compound following the

manufacturers instructions. Bead glazing: Base coated beads should be set down onto a

suitable flexible glazing compound/ mastic (following the manufacturers instructions)

before fixing down firmly .

•	 Initial coats: Preservative Basecoat as necessary. Note this product is described as

Harmful. Read the Safety, Health & Environmental Information on the container before

using this product .

-	Number of coats: 1 coat .

•	 Finishing coats: As recommended by manufacturer .

Number of coats: As recommended by manufacturer. Minimum 2no full coats .

GENERALLY

215	HANDLING AND STORAGE

•	 Coating materials: Deliver in sealed containers, labelled clearly with brand name, type of

material and manufacturer's batch number.

•	 Materials from more than one batch: Store separately. Allocate to distinct parts or areas of

the work.

220	COMPATIBILITY

•	 Coating materials selected by contractor:

-	Recommended by their manufacturers for the particular surface and conditions of

exposure.

-	Compatible with each other.

-	Compatible with and not inhibiting performance of preservative/fire retardant

pre-treatments.

240	SURFACES NOT TO BE COATED

•	 Radiator valves and stop valves.

280	PROTECTION

•	 'Wet paint' signs and barriers: Provide where necessary to protect other operatives and

general public, and to prevent damage to freshly applied coatings.

320	INSPECTION BY COATING MANUFACTURERS

•	 General: Permit manufacturers to inspect work in progress and take samples of their

materials from site if requested.

PREPARATION

400	PREPARATION GENERALLY

•	 Standard: To BS 6150, Section 4.

•	 Preparation materials: Types recommended by their manufacturers and the coating

manufacturer for the situation and surfaces being prepared.

•	 Substrates: Sufficiently dry in depth to suit coating.

•	 Efflorescence salts: Remove.

•	 Dirt, grease and oil: Remove. Give notice if contamination of surfaces/ substrates has

occurred.

•	 Surface irregularities: Abrade to a smooth finish.

•	 Joints, cracks, holes and other depressions: Fill with stoppers/ fillers. Work well in and

finish off flush with surface. Abrade to a smooth finish.

•	 Dust, particles and residues from abrasion: Remove.

-	Fill with stoppers/ fillers. Work well in and finish off flush with surface.

-	Abrade to a smooth finish.

•	 Water based stoppers and fillers:

-	Apply before priming unless recommended otherwise by manufacturer.

-	If applied after priming: Patch prime.

•	 Oil based stoppers and fillers: Apply after priming.

•	 Doors, opening windows and other moving parts:

-	Ease, if necessary, before coating.

-	Prime resulting bare areas.

420	FIXTURES AND FITTINGS

•	 Removal: Before commencing work remove: Coverplates, grilles, wall clocks, and other

surface mounted fixtures.

•	 Replacement: Refurbish as necessary, refit when coating is dry.

425	IRONMONGERY

•	 Removal: Before commencing work: Remove ironmongery from surfaces to be coated.

•	 Hinges: Do not remove.

•	 Replacement: Refurbishment as necessary; refit when coating is dry.

471	PREPRIMED WOOD

•	 Areas of defective primer: Abrade back to bare wood and reprime.

481	UNCOATED WOOD

•	 General: Abrade to a smooth, even finish with arrises and moulding edges lightly rounded

or eased.

•	 Heads of fasteners: Countersink sufficient to hold stoppers/fillers.

•	 Resinous areas and knots: Apply two coats of knotting.

500	PREPRIMED STEEL

•	 Areas of defective primer, corrosion and loose scale: Abrade back to bare metal. Reprime

as soon as possible.

511	GALVANIZED, SHERARDIZED AND ELECTROPLATED STEEL

•	 White rust: Remove.

•	 Pretreatment: Apply one of the following:

-	'T wash'/ mordant solution to blacken whole surface.

Etching primer recommended by coating system manufacturer.

521	UNCOATED STEEL - MANUAL CLEANING

•	 Oil and grease: Remove.

•	 Corrosion, loose scale, welding slag and spatter: Abrade to remove.

•	 Residual rust: Treat with a proprietary removal solution.

•	 Primer: Apply as soon as possible.

541	UNCOATED ALUMINIUM/ COPPER/ LEAD

•	 Surface corrosion: Remove and lightly abrade surface.

•	 Pretreatment: Etching primer if recommended by coating system manufacturer.

552	UNCOATED PVC-U

•	 Dirt and grease: Remove. Do not abrade surface.

570	UNCOATED MASONRY/ RENDERING

•	 Loose and flaking material: remove.

580	UNCOATED PLASTER

•	 Nibs, trowel marks and plaster splashes: Scrape off.

•	 Overtrowelled 'polished' areas: Abrade lightly.

590	UNCOATED PLASTERBOARD

•	 Depressions around fixings: Fill with stoppers/ fillers

601	UNCOATED PLASTERBOARD - TO RECEIVE TEXTURED COATING

•	 Joints: Fill, tape and feather out with materials recommended by textured coating

manufacturer.

APPLICATION

711	COATING GENERALLY

•	 Application standard: To BS 6150, Section 5.

•	 Conditions: Maintain suitable temperature, humidity and air quality during application and

drying.

•	 Surfaces: Clean and dry at time of application.

•	 Thinning and intermixing of coatings: Not permitted unless recommended by manufacturer.

•	 Overpainting: Do not paint over intumescent strips or silicone mastics.

•	 Priming coats:

-	Thickness: To suit surface porosity.

-	Application: As soon as possible on same day as preparation is completed.

•	 Finish:

-	Even, smooth and of uniform colour.

-	Free from brush marks, sags, runs and other defects.

Cut in neatly.

720	PRIMING JOINERY

•	 Preservative treated timber: Retreat cut surfaces with two flood coats of a suitable

preservative before priming.

•	 End grain: Coat liberally allow to soak in, and recoat.

730	WORKSHOP COATING OF CONCEALED JOINERY SURFACES

•	 General: Apply coatings to all surfaces of components.

751	STAINING WOOD

•	 Primer: Apply if recommended by stain manufacturer.

•	 Application: Apply in flowing coats and brush out excess stain to produce uniform

appearance.

760	VARNISHING WOOD

•	 First coat:

-	Thin with white spirit.

-	Brush well in and lay off avoiding aeration.

•	 Subsequent coats: Rub down lightly along the grain between coats.

770	EXTERNAL DOORS

•	 Bottom edges: Prime and coat before hanging doors.

780	BEAD GLAZING TO COATED WOOD

•	 Before glazing: Apply first two coats to rebates and beads.

800	GLAZING

•	 Etched, sand blasted and ground glass: Treat or mask edges before coating to protect

from contamination by oily constituents of coating materials.

810	WATER REPELLENT

•	 Application: Liberally flood surface, giving complete and even coverage.

M61

Intumescent coatings for fire protection of steelwork

M61 Intumescent coatings for fire protection of steelwork

To be read with Preliminaries/General conditions

PROTECTIVE COATING SYSTEMS

110	ON SITE COATING TO PRIMED STEELGENERNALLY

•	 Use/ location: Exposed internal faces of columns, beams and purlins, but excluding

cladding rails.

•	 Fire resistance to BS 476-21: 60 minutes.

•	 Preparation and priming: By steelwork contractor, as section G10.

-	Primer: Contractors choice - proprietary high build brushing aluminium primer.

•	 Intumescent coat:

-	Manufacturer: Contractors choice.

Product reference: Contractors choice.

-	Finish: Visible areas: Normal decorative, as clause 450.

•	 Top sealer coat: Type recommended by intumescent coating manufacturer.

-	Dry film thickness: As recommended by manufacturer.

-	Colour: Colour to be confirmed by CA from manufacturers colour selection.

•	 Bolt head/ nut protection: As main steelwork.

GENERAL REQUIREMENTS

205	VALIDATION OF MATERIALS

•	 Project specific evaluation of intumescent coating materials:

-	Standard: To BS 8202-2, clause 4.

-	Test results: Submit on request.

210	WORKING PROCEDURES

•	 Standard: To BS 8202-2.

•	 Give notice: Before commencing surface preparation and coating application.

•	 Quality control: Record project specific procedures for surface preparation and coating

application.

215	WORKING CONDITIONS

•	 General: Maintain suitable temperature, humidity and air quality during coating application

and drying.

•	 Surfaces to be coated: Clean and dry at time of coating application.

220	APPLICATOR'S PERSONNEL

•	 Operatives: Trained/ experienced in anticorrosive and intumescent coatings.

•	 Evidence of training/ experience: Submit on request.

260	CONTROL SAMPLES

•	 General: Carry out sample areas of finished work as follows:

Contractor's choice.

•	 Approval of appearance: Obtain before commencement of general coating application.

270	INSPECTION

•	 Permit intumescent coating manufacturer to:

-	Inspect work in progress.

-	Inspect quality control records.

-	Take dry film thickness and other measurements.

-	Take samples of coating products.

•	 Intumescent coating manufacturer's inspection reports: Submit without delay.

280	OFF SITE COATED STEEL

•	 Handling and erection: Use methods and devices designed to minimise damage to

intumescent coatings.

PREPARATION OF SURFACES

315	NEW STEEL - BLAST CLEANING

•	 Preparation: Remove oil and grease.

•	 Blast cleaning:

-	Atmospheric condition: Dry.

-	Abrasive: Suitable type and size, free from fines, moisture and oil.

-	Finish: To BS EN ISO 8501-1, preparation grade SA2½, with an average profile of

approximately 75 micrometres.

-	Abrasive residues and moisture: Remove.

•	 Primer: Apply as soon as possible after cleaning and before gingering or blackening

appears.

APPLICATION OF COATINGS

410	INTUMESCENT DRY FILM THICKNESS (DFT)

•	 Required dft: Determine for every steel member to give specified period of fire resistance.

Use intumescent coating manufacturer's current published loading tables.

-	Special sections and partial fire exposure conditions: Obtain required dft in writing from

manufacturer.

•	 Schedule and drawings: Submit at least two weeks before starting work.

-	Schedule content: Member sizes, weights/thicknesses, loading conditions, etc. showing,

for each variant, the exposed perimeter/ sectional area (Hp/A) ratio and required dft.

-	Drawing content: Steelwork drawings marked in colour to show required dft for each

member.

420	MEASUREMENT OF INTUMESCENT DFT

•	 Primer dft: Determine average dft (for deduction from total dft after application of

intumescent).

•	 Intumescent dft: Determine at:

-	500 mm centres along each coated plane of universal sections (8 planes), and

rectangular hollow sections (4 planes).

-	125 mm centres along coated circular hollow sections, spread evenly around

circumference.

•	 Acceptance standard:

-	Average intumescent dft: Not less than required dft (exclusive of primer and top sealer).

-	Local intumescent dft: Not less than 80% of required dft. Areas greater than 100 mm

equivalent diameter with a dft of less than 80% of required dft must be brought up to

thickness.

440	BASIC FINISH

•	 Definition: Reasonably smooth and even. Orange peel, other texture, minor runs and

similar minor defects are acceptable.

490	TOP SEALER COAT

•	 Application: To achieve dft recommended by manufacturer and to give an even, solid,

opaque appearance, free from runs, sags and other visual defects.

520	COMPLETION OF OFF SITE COATED STEEL

•	 Exposed unprotected areas, including fixings: Following erection of steelwork, apply

intumescent coating locally.

•	 Unscheduled additional connections to erected steelwork: Remove and reinstate

intumescent coating locally.

530	RECORDS OF COATED STEEL

•	 On completion of intumescent coating work, submit:

-	Accurate surface preparation and coating application records.

-	Fire resistance certificates.

N

Furniture/Equipment

N10

General fixtures/ furnishings/ equipment

N10 General fixtures/ furnishings/ equipment

To be read with Preliminaries/General conditions.

GENERAL

All furniture must be Kitemarked certified to BS 6222: Part 2: Level "H" Domestic Kitchen

Equipment, part 2 specification for strength requirements and methods of test for fitted

kitchen units. Test level "G" is not acceptable. Units are to be marked accordingly (to

comply with BSI requirements)

Samples of typical units must be provided within the first 2 months of contract on site date

and adequate time allowed for their approval prior to manufacture and installation on site.

PRODUCTS

109	SUSTAINABILITY

Contractor shall select timbers for carpentry and finished joinery, plywood and particle

boards with certification from the following schemes where appropriate. Certificate

evidence to be provided to CA.

CSA     Canadian Standards Association

FSC     Forest Stewardship Council Certification Scheme

MTCC  Malaysian Timber Certification Scheme

PEFC   Programme for the Endorsement of Forest Certification

Programmes.

SFI      Sustainable Forestry Initiative

150A	FITTED KITCHEN UNITS (All Houses & Apartments)

•	 Standard: To BS 6222 Part 2 Level H.

•	 Manufacturer: Contractors choice - Must be registered to BS EN ISO 9002.

-	Product reference: by reference to manufacturer's instructions.

•	 Structural performance: To BS 6222-2, grade H.

•	 Dimensions: To BS EN 1116.

•	 Surface finishes: To BS 6222-3.

•	 Doors/ Drawer fronts:

-	Material: Plastics laminate.

-	Finish/ Colour: To an approved colour, finish and pattern.

-	Edges: 3mm think lipping.

•	 Side panels/ Plinths/ Shelves: As required. Provide minimum 1 no. mid shelf and supports

to all base unit cupboards.

-	Material: Plastics laminate.

-	Finish/ Colour: To an approved colour, finish and pattern.

-	Edges: Plastics strip.

•	 Worktops:

-	Classification: To BS 6222-3, type: colour and pattern to be confirmed.

-	Material: 40mm thick with Plastics laminate finish.

-	Finish/ Colour: To an approved colour, finish and pattern.

-	Exposed edges: Plastics strip.

•	 Accessories: Kick plate at base to match door finish.

•	 Other requirements:

1) 1 No cutlery tray  to be provided to top drawer

2) 1 No. wall mounted fire blanket to be fixed to wall - position to be agreed on site- in

close proximity to the cooker.

Refer to kitchen drawings accordingly.

3) Cupboard to be dedicated as Medical Cupboard with suitable proprietary cylinder lock

(provide 2no keys), refer to kitchen layout for position.

Unit Construction

-	Base units to be 900mm high x 600mm deep, plastic laminate finish to be selected.

Worktops to be 40mm thick with plastic laminate finish to be approved. Wall units to be

750mm high x 300mm deep. Edges of worktops, cupboard doors and drawer fronts shall

be finished in plastic laminate. All to an approved colour, finish and pattern. Ensure a

minimum of 458mm space between worktop units and high level units is left to

accommodate 3 No. rows of 150mm square tiles.

- All furniture to meet HAOM insurance life assessment of 25 years. All furniture to be

kite marked and certified to BS 6222 Part 2 level H @domestic Kitchen Equipment Part 2

for specification strength requirements & methods of test for fitted kitchen units: note:

test level G is not acceptable.

-	Units including plinths which shall be sealed as recommended by manufacturers shall be

factory formed for site installation by an approved.

-	All components shall be finished in plastic laminate to approved colours and patterns.

-	Cleat/secret fix all units to floor and walls and neatly silicone seal to leave a watertight,

robust stable and durable assembly.

-	All melamine-faced chipboard should be manufactured from BS EN 312 P3 (2003) Core

board and all carcase edging is to be lipped with 0.45mm PVC.

-	Comply with the requirements of BS EN 942:(2007): Part 1 Grade 1 and supplied from

ecologically managed forests. On double base units the rear mounting should be inset

100mm to accommodate pipework.

-	All structural carcase joints should be achieved without screwing directly into or through

chipboard. Standard knock down blocks are not acceptable.

-	All carcase components must be replaceable without any adjacent units being removed.

-	Backs should be inset on all base units and should not be grooved into the carcase.

The sink base unit should have a 100mm upstand to mid level shelving.

-	All base units must have adjustable feet.

-	All gable ends must match units.

-	All plinths should be removable and the plinth cut out sealed.

-	All shelves over 600mm long should be supported centrally and at both ends with a total

of 6 fixing posts. All shelves should be adjustable in height.

-	Sink and base units must support all edges of the sink and worktop.

-	Wall units over 600mm are to have 6 wall fixings.

-	Corner base unit shall be double opening doors without a front corner post.

-	Plastic sealer fascias should be fitted to kicker boards.

-	Space must be left for a standard cooker and fridge freezer (min space 600mm wide).

Back to back proprietary metal edging strips to be installed where removable section of

worktop is required for fridge.

-	All structural rails and mountings to be manufactured from high quality HARDWOOD

complying with requirements of BS1186: 1986 Part1 Grade 1 and supplied from

ecological managed forests on double base units the rear mounting should be inset by

68mm to accommodate pipework.

Doors and Drawers

-	The drawer should be a metal box with metal sides and a metal back with 15mm MFC

base manufactured to BS EN312 P3 (2003)& BS EN312 P5 (2003). Base to be lipped on

all edges.

-	Drawer fronts should not be grooved for the drawer base.

-	All doors are to be hung on 180-degree BLUM hinges SELF CLOSING - serial number

86/610 and have 3mm thick lipping and metal handles, samples of which must be

provided for approval.

-	All door and drawer fronts must either be 18mm Chipboard P5 Grade to EN 312 (2003)

bonded coloured laminate/vinyl wrapped of post formed to match carcasses.

-	All drawer and door handles to be 98mm 'D' type handle in stainless steel.

Worktops

-	Worktops should be manufactured from improved moisture resistant chipboard

complying with BS EN 312 (2003). Laminates should be of post forming grade to BS

EN348. A backing laminate is to be utilised incorporating polythene barrier.

-	Worktops must be manufactured with the front edge seal and high heat and moisture

resistant adhesive.

-	Worktops must be 40mm V313 chipboard bonded and with coloured laminate on the top.

The kick plate at the bottom of the cupboard must match the door finish.

-	Where worktops are jointed, dog bone joints must be used.

Additional Requirements for Wheelchair Unit Kitchens

-	Refer to wheelchair kitchen drawings for tiling details - MORE TILING REQUIRED IN

THES KITCHENS.

-	Adjustable units, worktops etc. supplied as indicated on wheelchair kitchen drawing.

-	All adjustable brackets are to be proprietary 5 point white polyester powder coated steel,

to be suitable for care assisted living

-	Provide proprietary extending carousel storage systems to any corner base units to allow

ease of access.

6no. door and drawer fronts, 6no. different types of handles and 6 no. colours/

designs of worktop to be provided for approval by the HA in the first quarter of the

contract for approval by the HA.

Refer to individual kitchen layouts for further information and layout of each type.

160A	SHELVING WITHIN STORES-

•	 Manufacturer: -.

-	Product reference: -.

•	 Shelves: 3 no. rows of solid TIMBER shelving within stores. Heights to be confirmed by

architect.

-	Material: Plywood refer to P20/240.

-	Finish/ Colour: Painted colour to be approved.

•	 Other components: metal support brackets.

161	SHELVING WITHIN HOT PRESSES REMOVABLE SHELVING

•	 Manufacturer: -.

-	Product reference: -.

•	 Shelves:3 no. rows of slatted TIMBER shelves to all hot presses

-	Material: Solid wood.

-	Finish/ Colour: Painted colour to be approved.

•	 Other components: metal support brackets.

-	Front edging strip to be installed on the front edge of the shelving fitted to cover the

battens under.

188	BATHROOM AND WASHROOM EQUIPMENT

•	 Item: MEDICAL CABINET.

•	 Manufacturer: Contractors choice.

-	Product reference: Submit proposals.

•	 Finish/ Colour: white melamine.

•	 Fixing: Plugged and screwed to wall.

•	 Other requirements: mirrored front door, internal shelf & lockable.

210A	HAT & COAT HOOKSTO ENTRANCE HALL/ STORE OF EACH HOUSE AND

APARTMENT

•	 Manufacturer: Contractors choice .

-	Product reference: - .

•	 Material: SAS ALUMINIUM .

-	Finish/ Colour: SAS ALUMINIUM to be approved by CA .

•	 Fittings: 6 no hooks per dwelling appropriately spaced. Hook shape and spacing to be

approved by CA .

Hooks to be securely screw fixed to walls at locations to be agreed with CA.

270A	MIRRORSBATHROOMS & TOILETS

•	 Material: Class C safety glass to BS 6206 .

•	 Quality: Free from tarnishing, discoloration, scratches and other defects visible in the

designed viewing conditions. Reflection undistorted.

•	 Size: 600 X 400.

•	 Backing: Aluminium foil.

•	 Edges: BEVELLED.

•	 Fixing: CP dome top wood screws with polyethylene sleeves and washers.

Installation: Accurately with sides vertical -  position to be agreed onsite with.

1 per bathroom / wc / washroom

EXECUTION

710	MOISTURE CONTENT OF WOOD AND WOOD BASED BOARDS

•	 Temperature and humidity: During delivery, storage, fixing and to handover maintain

conditions to suit specified moisture contents of timber components.

•	 Testing: When instructed, test components with approved moisture meter to

manufacturer's recommendations.

720	INSTALLATION GENERALLY

•	 General: As Preliminaries section A33.

•	 Fixing and fasteners: As section Z20.

•	 Services: As Engineering Services specification.

740	TAPS

•	 Fixing: Secure, watertight seal with the appliance.

•	 Positioning: Hot tap to left of cold tap as viewed by user of appliance.

750	WASTES AND OVERFLOWS

•	 Bedding: Waterproof jointing compound.

•	 Fixing: With resilient washer between appliance and backnut.

760	SEALANT POINTING

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice .

•	 Material: Silicone based to BS 5889, type B with fungicide.

•	 Colour: White.

•	 Application: As section Z22.

770	TRIMS

•	 Lengths: Wherever possible, unjointed between angles or ends of runs.

•	 Running joints: Where unavoidable, obtain approval of location and method of jointing.

•	 Angle joints: Mitred.

COMPLETION

910	GENERAL

•	 Doors and drawers: Accurately aligned, not binding. Adjusted to ensure smooth operation.

•	 Ironmongery: Checked, adjusted and lubricated to ensure correct functioning.

920	APPLIANCES

•	 Test: Ensure that all functions and features work correctly.

•	 Documentation: Submit guarantees, instruction manuals, etc.

N14

General signage systems

N14 General signage systems

To be read with Preliminaries/ General conditions.

GENERAL

110	SIGNAGE SYSTEMFOR ASSOCIATION COMPANY LOGO AND ADDRESS DETAILS

•	 System manufacturer: Submit proposals .

-	Product reference: Submit proposals in accordance with Association Design Guide All

signs should be free standing on powder coated aluminium legs unless otherwise

agreed. All signs must be anti-vandal type if at all possible. System manufacturer. TO BE

SUITABLE IN AN EXTERNAL ENVIRTONMENT .

•	 Layout and dimensions:  3 No. steel posts - triangular sign with 3 No. sides - each side

1.5x2metres .

•	 Lettering:

-	Language: English & Irish .

-	Font: Helvetica medium .

-	Colour: Company logo  .

-	Size: Manufacturer's standard range .

•	 Symbols and graphics: Logo .

-	Colour: Manufacturer's standard range .

-	Size: logo size tbc .

•	 Background colour: Manufacturer's standard range .

•	 Sign type: Aluminium plate .

-	Inserts: Manufacturer's standard .

-	Manufacturing process: Manufacturer's standard .

•	 Supports/ Fixings: On steel posts in concrete sockets, strictly installed in accordance with

manufacturers recommendations  .

•	 Accessories: Not required .

111	DIRECTIONAL AND POSTAL EXTERNAL SIGNAGE-Postal signs must be provided and

incorporate the HA logo. All signs should be free standing on powder coated STEEL legs

unless otherwise agreed. All signs must be anti-vandal type.

•	 System manufacturer: Contractor's choice, submit proposals .

-	Product reference: Submit proposals in accordance with Association Design Guide TO

BE SUITABLE IN AN EXTERNAL ENVIRONMENT .

•	 Layout and dimensions: To be confirmed .

•	 Lettering:

-	Language: English & Irish .

-	Font: To be confirmed .

-	Colour: To be confirmed .

-	Size: Manufacturer's standard range .

•	 Symbols and graphics: HA logo .

-	Colour: HA corporate colours .

-	Size: In proportion to sign .

•	 Background colour: Manufacturer's standard range .

•	 Sign type: Aluminium plate .

-	Inserts: Submit proposals .

-	Manufacturing process: Embossed .

•	 Supports/ Fixings: TO BE FIXED INTO THE GROUND IN ACCORDANCE WITH THE

MANUFACTURERS RECOMMENDATIONS. Submit proposals .

•	 Accessories: Not required .

130A	EXTERNAL GRANITE SIGNAGE TO FEATURE ENTRANCES WALLS

•	 Manufacturer:  [Contractor's choice, provide sample for CA approval] .

-	Product reference:  [Black granite plaque to incorporate the Associations details and

development name.  Minimum requirements to include new street name, association

name and logo].

•	 Layout and dimensions:  [Approx. 1500x750mm, including minimum 50mm bevelled

surround as indicated].

-	Product reference:  [Submit proposals in accordance with Association Design Guide -

TO BE SUITABLE IN AN EXTERNAL ENVIRONMENT] .

•	 Lettering:

-	Language:  [English & Irish] .

-	Font:  [To be confirmed. Contractor to submit proposals] .

-	Colour:  [To be confirmed. Contractor to submit proposals] .

-	Size:  [Contractor to submit proposals, sign to be legible from 10m from the main road] .

-	Manufacturing process:  [Recessed / engraved lettering with suitable coloured paint

lettering suitable for prolonged / permanent weather exposure in an external

environment] .

•	 Supports/ Fixings:  [Wall mounted and recessed into brickwork.  Contractor to provide

suitable proprietary adhesive-fixing with stainless steel dowels in accordance with their

manufacturers recommendations].

SYSTEM PERFORMANCE

210	GENERAL REQUIREMENTS

•	 Signage system: Complete to BS 559, including facing information, components, inserts,

accessories and fixings necessary to complete the system.

-	Comply with the requirements of: - .

•	 Geometric shapes, colours and layout: In accordance with BS 8501.

•	 Design standard for the disabled: In accordance with BS 8300.

•	 Proposals: Submit drawings, schedules, technical information, calculations and

manufacturer's literature.

220	ROAD SIGNAGE REQUIREMENTS

•	 Signage system: Complete in accordance with relevant parts of BS 12899-1 and the

Department for Transport 'Traffic signs manual'.

•	 Product testing standard: To BS 873-1.

•	 Proposals: Submit drawings, schedules, technical information, calculations and

manufacturer's literature.

230	STRUCTURAL PERFORMANCEOF EXTERNAL SIGNAGE SYSTEM

•	 Wind loads:

Standard: To BS 6399-2 .

280	DESIGN LIFEOF SIGNAGE SYSTEM

•	 Duration: 10 years  .

-	Subject to reasonable wear and tear.

•	 Environment: External .

•	 Condition of use: Subject to regular maintenance.

295	SIGNAGE SAMPLES BOARD

•	 Samples board: Submit.

-	Content: Selected labelled signs, showing methods of fixing.

-	Conformity: Retain samples on site for the duration of the contract or until instructed to

remove.

Delivered product: To conform with labelled samples.

PRODUCTS

305	PRODUCTS GENERALLY

•	 Standard: To BS 559.

320	ALUMINIUMPLATES GENERALLY

•	 Manufacturer: Submit proposals .

-	Product reference: Submit proposals .

•	 Component thickness: 6 mm, 2 mm facing on 4 mm backing panel .

•	 Finish: Manufacturer's standard .

•	 Perimeters: Manufacturer's standard .

350	PLASTICSSHEETS

•	 Material: Acrylic .

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified .

-	Product reference: Contractor's choice .

•	 Component thickness: 2 mm .

•	 Finish: Manufacturer's standard .

•	 Perimeters: Folded corners .

410	POSTS FOR EXTERNAL SIGNS

•	 Manufacturer: Contractor's choice .

-	Product reference: Contractor's choice .

•	 Material: Steel structural hollow sections to BS EN 10210 grade S275J Aluminium porthole

extruded tubes to BS EN 755-8  grade 6063-T4  .

•	 Size: 75 mm diameter 1500 mm long .

•	 Finish: Plastics coated .

•	 Colour: Grey .

•	 Base: Galvanized steel plates secured by collar and bolts .

EXECUTION

610	FIXING SIGNS GENERALLY

•	 Installation: To BS 559.

-	Secure, plumb and level.

•	 Strength of fasteners: Sufficient to support all live and dead loads.

•	 Fasteners and or adhesives: As section Z20.

•	 Fasteners for external signs: Corrosion resistant material or with a corrosion resistant

finish. Isolate dissimilar metals to avoid electrolytic corrosion.

•	 Fixings showing on surface of sign: Must not detract from the message being displayed.

630	FIXING ROAD SIGNS

•	 Protrusion of post top above sign: Not permitted unless supporting a luminaire.

•	 Drilling of components:

-	Ferrous components: Drilled before the application of any finish.

-	Plastics sheeting: Apply clear lacquer recommended by plastics sheet manufacturer to

edges of holes to prevent ingress of moisture damaging the lamination.

•	 Erection: In accordance with the DFT 'Traffic signs manual,' Chapter 1.

•	 Fixing: Austenitic stainless steel fasteners recommended for the purpose by the sign

manufacturer.

640	FOUNDATIONS FOR EXTERNAL POSTS

•	 Type: Mass concrete block with 50 mm square x 200 mm deep post hole  .

•	 Size: 300 x 300 x 300 mm deep with top 100 mm below finished ground surface .

•	 Concrete: To BS 8500-2.

-	Designated type: - .

-	Admixtures: Submit proposals.

-	 Prohibited: Calcium chloride and admixtures containing calcium chloride.

•	 Consistence class: Contractor's choice.

•	 Other requirements: None .

660	EXPOSED CONCRETE FOUNDATIONS TO POSTS

•	 Finish: Compact until air bubbles cease to appear on the upper surface, then weather to

shed water and trowel smooth.

670	ELECTRICAL AND DATA SERVICES

•	 Services connection required: Power for lighting .

•	 Standard: To BS 7671.

•	 Coordinate with services trades.

COMPLETION

910	DOCUMENTATION

•	 Submit:

-	Manufacturer's maintenance instructions.

Guarantees, warranties, test certificates, record schedules and log books.

N15

Fire and safety signage systems

N15 Fire and safety signage systems

To be read with Preliminaries/ General Conditions.

GENERAL

SYSTEM PERFORMANCE

210	GENERAL REQUIREMENTS

•	 Signage system design:

-	Complete to: BS 559 and BS ISO 16069.

-	Comply with the requirements of: Building Operation Report and Fire Strategy Report .

•	 Proposals: Submit drawings, schedules, technical information, calculations and

manufacturer's literature.

240	SIGNAGE SYSTEM SPECIFICATION

•	 Content: Signs including facing information, components, inserts, accessories and fixings

necessary to complete the system.

•	 Geometric shapes, colours and layout: To BS 5499-1.

-	Font: Helvetica medium.

•	 Escape route: In accordance with BS 5499-4 and BS ISO 16069

•	 Safety meaning: In accordance with BS 5499-5.

•	 Water safety: In accordance with BS 5499-11.

270	FIRE REACTION 	OF FIRE SIGNAGE SYSTEM

•	 Non flammable surface:

-	Standard: Class 1 to BS 476-7 .

280	DESIGN LIFE 	OF FIRE SIGNAGE SYSTEM

•	 Duration: 7 years .

-	Subject to reasonable wear and tear.

•	 Environment: Internal .

•	 Condition of use: Subject to regular maintenance.

PRODUCTS

305	SIGNAGE PRODUCTS GENERALLY

•	 Standard: To BS 559.

•	 Colorimetric and photometric properties: To BS 5378-2.

320	ALUMINIUM PLATE 	FOR ESCAPE ROUTE SIGNS

•	 Manufacturer: Contractor's choice .

-	Product reference: Submit proposals .

•	 Component thickness: To BS 559 .

•	 Finish: Manufacturer's standard .

•	 Perimeters: Folded corners .

410	SELF-LUMINOUS SIGNS

•	 Standard: To BS 5499-2

•	 Manufacturer: Contractor's choice .

-	Product reference: Contractor's choice .

•	 Case material: Plastics sheet .

•	 Component thickness: BS 559:1998 .

•	 Finish: BS 559:1998 .

•	 Perimeters: Not required .

EXECUTION

610	FIXING SIGNS GENERALLY

•	 Installation: To BS 559.

-	Secure, plumb and level.

•	 Fasteners and adhesives: As section Z20.

•	 Strength of fasteners: Sufficient to support live and dead loads.

•	 Fasteners for external signs: Corrosion resistant material or with a corrosion resistant

finish. Isolate dissimilar metals to avoid electrolytic corrosion.

•	 Fixings showing on surface of sign: Must not detract from the message being displayed.

COMPLETION

910	DOCUMENTATION

•	 Submit:

-	Manufacturer's maintenance instructions.

-	Guarantees, warranties, test certificates, record schedules and logbooks.

930	SPECIALIST TOOLS

•	 Supply as follows: 1 set suspension adjustment tools .

N17

Portable fire fighting systems

N17 Portable fire fighting systems

To be read with Preliminaries/ General Conditions.

GENERAL

150	FIRE BLANKET SYSTEM FOR ALL KITCHENS

•	 Type: Light duty.

•	 Size: 1.2 x 1.2 m.

•	 Supports: Mounting brackets.

SYSTEM PERFORMANCE

210	DESIGN

•	 Design: Complete the design of the portable fire fighting system.

-	Basis: To Fire Officer's requirements.

•	 Proposals: Submit drawings, technical information, calculations and manufacturers'

literature.

220	COLOUR CODING

•	 Portable fire extinguishers: Colour code in accordance with BS 7863.

PRODUCTS

410A	FIRE BLANKETS - LIGHT DUTY TO BE INSTALLED IN KITCHENS

•	 Standard: To BS EN 1869.

•	 Manufacturer: Contractor's choice, provide sample for CA approval.

-	Product reference: Submit proposals.

EXECUTION

610	INSTALLING PORTABLE FIRE EXTINGUISHERS

•	 Mounting height above finished floor level: Bracket fixed at 1 m.

650	INSTALLING FIRE BLANKETS

•	 Mounting height above finished floor level: Submit proposals.

COMPLETION

910	CLEANING

•	 Protective wrappings: Remove.

•	 Cleaning: Clean off and wipe down container finishes.

940	MAINTENANCE

•	 Servicing: Arrange the first annual service of the portable firefighting systems.

•	 Maintenance standard: To BS 5603-0.

N25

Permanent access and safety equipment

N25 Permanent access and safety equipment

To be read with Preliminaries/ General conditions.

TYPES OF SYSTEM/ EQUIPMENT

200A	PROPRIETARY ROOF WALKWAY AND ACCESS SYSTEM TO STANDING SEAM

METAL ROOF OF APARTMENTS

•	 Manufacturer: Contractor's choice, provide samples for CA approval.

-	System reference: 3rd Party accredited proprietary roof walkway / access system

consisting of anti-slip uPVC planks stepped and levelled to falls as necessary to suit roof

slope.  System to be fully compatible with type of roofing construction and surface affixed

in a non-penetrative manner.

•	 Anchorage device: Standing seam non-penetrative fixing clamps with min. 50mm uPVC

cushion bearer.

•	 Overall system width: min. 430mm.

•	 Accessories/ Other requirements: Provide suitable testing and loading certification.

•	 Installation: In accordance with the system manufacturer's recommendations or a

contractor approved by the system manufacturer.

•	 Structural anchors: Type recommended by the system manufacturer to suit the structure/

fabric into which they will be fixed.

210A	GUIDED TYPE FALL ARREST SYSTEM TO METAL ROOF & FLAT ROOF OF

APARTMENTS

•	 Manufacturer: Contractor's choice, provide samples for CA approval.

-	System reference: Proprietary fall arrest system fully compatible with type of roofing

construction.

•	 Anchorage device: Horizontal stainless steel cable.

•	 Overall system length: As required to specialist design.

•	 Intermediate support spacing: As necessary to specialist design - Complete with all bends

and curves in rigid rails, corner units for flexible cable systems, turntables, rotary exit units

as necessary.

•	 Accessories/ Other requirements: As necessary to specialist design.

•	 Installation: To BS 7883 by the system manufacturer or a contractor approved by the

system manufacturer.

•	 Structural anchors: Type recommended by the system manufacturer to suit the structure/

fabric into which they will be fixed.

220A	SINGLE POINT ANCHORAGE DEVICESTO METAL & FLAT ROOF OF APARTMENTS

•	 Standard: To BS EN 795 - Class A1.

•	 Manufacturer: Contractor's choice, provide sample for CA approval.

-	Product reference: Proprietary metal eye bolt anchors suitable for restraint. Provide 1no

at each location suitably fixed securely back to solid structural member / element.

•	 Type: Eyebolt (removable) with fixed socket.  Both tested to 10kN.

•	 Material/ Finish: RAL coloured to suit wall / ceiling finish.

•	 Locations: As indicated on drawings.

•	 Installation: To BS 7883.

•	 Other requirements: Provide with each anchor:

-	A backing disc giving the manufacturer's name and telephone number and the date of

installation.

A certificate of compliance with testing and examination requirements of BS EN 365.

420	WIND LOADING

•	 General: Design the access/ safety system to withstand specified wind loads with

equipment in position of maximum exposure and in parked position.

•	 Wind loads:

Calculate to BS 6399-2, Standard Method..

440	DESIGN LIFE/ MAINTENANCE PROGRAMME

•	 Design life of access/ safety system: Not less than 60 years.

•	 Schedule for maintenance and for replacement of components: Submit.

460	ASSESSMENT/ TESTING OF FIXING POINTS FOR ANCHOR DEVICES

•	 Design and installation of fixings in steelwork or timber: Verified by calculation to be

capable of sustaining the relevant static and dynamic test forces specified in BS EN 795,

clause 4.3.

•	 Fixings in other materials: Verify suitability by carrying out a test in a sample of the

material. The sample must be capable of sustaining the relevant static and dynamic test

forces specified in BS EN 795, clause 4.3. Thereafter, each structural anchor installed in

that material must be subjected to an axial pull out force of 5 kN to confirm the soundness

of the fixing. The structural anchor must sustain the force for a minimum of 15 seconds.

FABRICATION, ASSEMBLY AND INSTALLATION

510	FABRICATION AND ASSEMBLY GENERALLY

•	 Machine cutting, drilling and assembly: Carry out as much as possible in the workshop.

Obtain approval for any reassembly on site.

•	 Dissimilar metal surfaces of assembly components/ supports/ fixings: Isolate to prevent

electrolytic corrosion.

520	PROTECTION

•	 General: Do not deliver to site any components or assemblies that cannot be installed

immediately or unloaded into a suitable well protected storage area.

530	SUITABILITY OF STRUCTURE/ FABRIC

•	 Visual and geometric survey of supporting structure and fabric: Carry out before

commencing installation of access/ safety system. Report immediately if structure/ fabric

will not allow required accuracy/ security of erection/ fixing.

540	MECHANICAL FIXINGS

•	 Materials: Unless otherwise recommended by equipment manufacturer:

-	Connecting bolts and other fixings fully accessible for inspection: Mild steel hot dip

galvanized to BS 7371-6.

Nuts: Tapped after galvanizing.

-	Cast-in anchors and other fixings not accessible for routine inspection: Austenitic

stainless steel, grade 1.4401 (316) to BS EN 10088-1.

550	FASTENERS, INSERTS AND BOLTS FOR BUILDING IN

•	 Supplier: Equipment manufacturer/ supplier.

560	FIXINGS FOR SECURING EQUIPMENT

•	 Adjustment capability: Adequate three dimensional adjustment to accommodate building

structure/ fabric irregularities.

570	FIXING ANCHOR INSTALLATION

•	 Site drilling or cutting into structure/ fabric: Permitted only in approved locations.

•	 Distance between all fixing devices and edges of supporting material: Not less than

recommended by fixing manufacturer.

640	MARKING OF ANCHOR DEVICES

•	 Provision: Provide on or near each anchor device a label or other clear marking giving:

-	Manufacturer's name and telephone number.

-	Serial number and year of manufacture of device.

-	Maximum number of personnel that may be attached to the device at any one time.

-	Requirements for energy absorbers, ground clearance, etc.

•	 Anchor devices intended solely for use with personal protective equipment: Indicate

restriction of use by pictogram or other suitable marking on or near the device.

810	SERVICE/ MAINTENANCEGENERALLY

•	 General: Following acceptance of the completed installation, service and maintain the

equipment for the period stated below as and at intervals recommended by the

manufacturer. Such maintenance to include a 'call-out' service during normal working

hours to maintain the equipment in an acceptable and safe condition.

•	 Service/ Maintenance period: 12 months.

820	OPERATING INSTRUCTIONS

•	 Equipment and accessories: Where appropriate, mark in such a way that it is possible to

identify the correct mode of operation for their safe use.

830	OPERATING AND MAINTENANCE MANUAL

•	 General: Provide, for inclusion in the Building Manual, printed instructions and

recommended procedures to be established by the Employer for operating and routinely

maintaining the equipment. Provide diagrams where appropriate.

•	 Content:

-	Instructions for assembling/ erecting equipment for use.

-	Comprehensive operating instructions, including safety and emergency procedures, for

all motions including upward, downward and lateral travel, and slew.

-	Servicing and planned maintenance procedures, including assembly instructions where

maintenance necessitates dismantling of machinery parts.

-	List of replacement parts, with references.

-	Recommended procedures for testing equipment.

P

Building fabric sundries

P10

Sundry insulation/ proofing work

P10 Sundry insulation/ proofing work

SUNDRY INSULATION/ PROOFING WORK

To be read with Preliminaries/ General conditions.

TYPES OF INSULATION

120A	MINERAL WOOL INSULATION LAID BETWEEN AND ABOVE TIES/ JOISTS TO

CEILINGS/ ROOF TRUSSES GENERALLY.

•	 Standard: Roofing grade to BS EN 13162, Kitemark certified.

•	 Material: Rock / mineral fibre wool .

•	 Manufacturer: Contractor's choice, BBA certified. Provide sample for CA approval .

Thickness: 350mm unless otherwise indicated on drawings and/or SAP calculations.

200mm between joists and 150mm on top of joists to achieve U-value of 0.12w/msqk MIN

LAMBDA VALUE - 0.044 Refer to drawings & SAP Calculations report .

•	 Density:  [135-180 kg/m³].

•	 Installation: To BS 5803-5.

•	 Installation requirements:

-	Joints: Butted, no gaps.

-	Extent of insulation: Over wall plates.

-	Service holes: Sealed, and debris removed before laying insulation.

-	Eaves ventilation: Unobstructed.

-	Electric cables overlaid by insulation: Sized accordingly.

-	Water cistern platforms: To be raised to allow continuous insulation underneath .

Standard: Roofing grade to BS EN 13162.

Manufacturer:  [Contractor's choice, provide sample for CA approval].

-	Product:  [Full fill mineral fibre packed between joists to BS EN 13162:2001. To be BBA

and IAB certified for this application. BS EN ISO 9001: 2000/IS EN ISO9001:2008.

Manufactured with a blowing agent that has zero Ozone Depletion Potential (ODP) and

Global Warming Potential (GWP) of less than 5 in accordance with the requirements of

BS 4841-1. To be installed in accordance with the manufacturer's instructions].

122A	FLOOR INSULATION TO CONCRETE GROUND FLOORS

Insulation:  Cohesively bonded low emissivity composite foil faced both sides, CFC

free rigid polyisocyanurate (PIR) insulation core with zero ozone depletion suitable for floor

installation.

-  Standard:  BS EN 13163.

-  Product certification:  BBA Certified / IAB Certified for this application. BS EN ISO 9001:

2000/IS EN ISO9001:2008.

Manufacturer:  Contractor's Choice, BBA certified - provide sample for CA approval.

Thickness (nominal):  200 mm.

Thermal conductivity:  Aged - 0.022 W/mK.

Reaction to fire class:  Class O fire rating on both phenolic core and facings, producing

less than5% smoke obscuration when tested to BS 5111-1:1974 low risk.

Additional requirements:  To be highly resistant to transmission of water vapour (more than

100MN.s/g) and air movement, with a compressive strength typically in excess of 100 kPa

at 10% compression when tested to BS EN 826: 1996 (Thermal insulating products for

building applications. Determination of compression behaviour) .

Joints between boards, at closures and penetrations: No gaps and free from mortar and

debris. .

- .

123A	EXTRUDED POLYSTYRENE INSULATION: TO VENTILATED VOIDS OF SPLIT LEVEL

CONSTRUCTION

Insulation:  Water and moisture resistant extruded polystyrene board insulation.

-  Standard:  BS EN 13163.

-  Product certification:  BBA Certified / IAB Certified for this application. BS EN ISO 9001:

2000/IS EN ISO9001:2008.

Manufacturer:  Contractor's Choice, BBA certified - provide sample for CA approval.

Thickness (nominal):  100 mm.

Thermal conductivity:  Aged - 0.034 W/mK.

Reaction to fire class:  Insulation to contain a flame retardant additive and achieve a

Euroclass E (reaction to fire) BS EN 13164 + BS EN 13501  Boards to be unaffected by

fluctuations in temperature and repeated freeze/thaw cycles.

Additional requirements:  Boards to be shiplap jointed with smooth homogenous skin on

both sides and to be fixed to concrete / concrete block wall / soffits using proprietary

insulation clips.  BS EN 120086 Water vapour diffusion resistance factor - 80-200 .

124A	ACOUSTIC MINERAL WOOL INSULATION BETWEEN STUDS INTERNAL WALLS

GENERALLY.

•	 Standard: Acoustic grade to BS EN 13162, Kitemark certified.

•	 Material: Rock / mineral fibre wool .

•	 Manufacturer: Contractor's choice, BBA certified. Provide sample for CA approval .

Thickness: 50mm unless otherwise indicated on drawings and/or SAP calculations .

•	 Density:  [24 kg/m³].

•	 Installation: To BS 5803-5.

•	 Installation requirements:

-	Joints: Butted, no gaps.

-	Extent of insulation: Over wall plates.

-	Service holes: Sealed, and debris removed before laying insulation.

-	Eaves ventilation: Unobstructed.

-	Electric cables overlaid by insulation: Sized accordingly.

-	Product:  [To be BBA and IAB certified for this application. BS EN ISO 9001: 2000/IS EN

ISO9001:2008.   Manufactured with a blowing agent that has zero Ozone Depletion

Potential (ODP) and Global Warming Potential (GWP) of less than 5 in accordance with

the requirements of BS 4841-1. To be installed in accordance with the manufacturer's

instructions].

124B	ACOUSTIC MINERAL WOOL INSULATION BETWEEN JOISTS INTERNAL FLOORS

GENERALLY.

•	 Standard: Acoustic grade to BS EN 13162, Kitemark certified.

•	 Material: Rock / mineral fibre wool .

•	 Manufacturer: Contractor's choice, BBA certified. Provide sample for CA approval .

Thickness: 100mm unless otherwise indicated on drawings and/or SAP calculations .

•	 Density:  [minimum 10 kg/m³].

•	 Installation: To BS 5803-5.

•	 Installation requirements:

-	Joints: Butted, no gaps.

-	Extent of insulation: Over wall plates.

-	Service holes: Sealed, and debris removed before laying insulation.

-	Eaves ventilation: Unobstructed.

-	Electric cables overlaid by insulation: Sized accordingly.

-	Product:  [To be BBA and IAB certified for this application. BS EN ISO 9001: 2000/IS EN

ISO9001:2008.   Manufactured with a blowing agent that has zero Ozone Depletion

Potential (ODP) and Global Warming Potential (GWP) of less than 5 in accordance with

the requirements of BS 4841-1. To be installed in accordance with the manufacturer's

instructions].

125A	ACOUSTIC MINERAL WOOL INTERSTUD INSULATION TO PARTY WALLS PARTY

WALL TIMBER FRAME.

•	 Standard: Acoustic grade to BS EN 13162, Kitemark certified.

•	 Material: Rock / mineral fibre wool batts or quilt .

•	 Manufacturer: Contractor's choice, BBA certified. Provide sample for CA approval .

Thickness: 90mm unless otherwise indicated on drawings and/or SAP calculations .

•	 Density:  [10-60 kg/m³ - to full stud depth].

•	 Installation: To BS 5803-5 in accordance with robust detail E-WT-1.

•	 Installation requirements:

-	Joints: Butted, no gaps.

-	Extent of insulation: Over wall plates.

-	Service holes: Sealed, and debris removed before laying insulation.

-	Eaves ventilation: Unobstructed.

-	Electric cables overlaid by insulation: Sized accordingly.

-	Product:  [To be BBA and IAB certified for this application. BS EN ISO 9001: 2000/IS EN

ISO9001:2008.   Manufactured with a blowing agent that has zero Ozone Depletion

Potential (ODP) and Global Warming Potential (GWP) of less than 5 in accordance with

the requirements of BS 4841-1. To be installed in accordance with the manufacturer's

instructions].

126A	ACOUSTIC MINERAL WOOL INTERFRAME INSULATION TO PARTY WALLS FULLY

FILLED PARTY CAVITY.

•	 Standard: Acoustic grade to BS EN 13162, Kitemark certified.

•	 Material: Rock / mineral fibre wool batts or quilt .

•	 Manufacturer: Contractor's choice, BBA certified. Provide sample for CA approval .

Thickness: 70-75mm unless otherwise indicated on drawings and/or SAP calculations .

•	 Density:  [18-60 kg/m³ - to full stud / cavity depth].

•	 Installation: To BS 5803-5 in accordance with robust detail E-WT-1.

•	 Installation requirements:

-	Joints: Butted, no gaps.

-	Extent of insulation: Over wall plates.

-	Service holes: Sealed, and debris removed before laying insulation.

-	Eaves ventilation: Unobstructed.

-	Electric cables overlaid by insulation: Sized accordingly.

-	Product:  [To be BBA and IAB certified for this application. BS EN ISO 9001: 2000/IS EN

ISO9001:2008.   Manufactured with a blowing agent that has zero Ozone Depletion

Potential (ODP) and Global Warming Potential (GWP) of less than 5 in accordance with

the requirements of BS 4841-1. To be installed in accordance with the manufacturer's

instructions].

256	A HIGH PERFORMANCE INSULATION TO COMBAT COLD BRIDGINGTO

EXTERNAL WINDOW AND DOOR REVEALS

•	 Material: Waterproof high performance laminated foil and aerogel composite insulation self

adhesive strip with integrated vapour control layer .

•	 Manufacturer: Contractor's choice, independently certified. Provide sample for CA approval

.

-	Product: Proprietary high performance laminate insulation to be certified for application.

Manufactured with a blowing agent that has zero Ozone Depletion Potential (ODP) and

Global Warming Potential (GWP) of less than 5 in accordance with the requirements of

BS 4841-1. To be installed in accordance with the manufacturer's instructions .

•	 Thickness: 6mm.

•	 Properties: Thermal conductivity 0.014W/mK.  Vapour resistance 0.37MNs/g.  Reaction to

fire Classification to EN13501-1 -  E.  Compression Resistance (at 10% deflection) 55kPa .

•	 Installation requirements:

-	To be installed to full width of all external window and external door reveals prior to

installing impact resistant plasterboard, beading and skim finish all in accordance with

manufacturer's instructions.

Joints: Butted, no gaps, use proprietary suitable tape over joint.

325A	AIR PERMEABILITY CONTROL JOINTS AND JUNCTIONS IN AIR & VAPOUR

CONTROL LAYERS ETC

•	 Material: Proprietary tapes, sealant strips and sealants to maintain airtightness .

•	 Manufacturer: Contractor's choice provide samples for CA approval .

-	Product reference: Products to be compatible with specified vapour barriers, breather

membranes, substrates etc .

•	 Requirements:

-	Overlap joints (& tears) : Either solvent free double sided adhesive mounting tape or

single sided solvent free adhesive tape with high performance reinforced paper carrier

as necessary.

-	Wall/floor junctions and penetrations (services etc)  : Single sided solvent free adhesive

tape with stretchable and armoured special PE carrier min.60mm wide.

-	Window & door junctions : Full surface solvent free self-adhesive tape with pre-Folded

paper backing (c. 12mm / 48mm wide) to seal between window frame and window reveal

prior to final finish.

•	 Installation requirements:

-	Lapped joints: 150 mm minimum.

-	Openings: Lap over and fix to reveals.

-	Joints and edges: Sealed with double sided tape of vapour resistivity not less than the

vapour control layer.

-	Substrates: Primed as necessary.

-	Penetrations/Tears etc: Taped / sealed appropriately.

430	WIRED MINERAL WOOL SMALL CAVITY BARRIERS

•	 Material: Wire reinforced mineral wool minimum 50 mm thick.

•	 Installation requirements:

-	Fasteners: Staples at maximum 150 mm centres, Fold if necessary to ensure a tight fit.

Joints and intersections: Butted, no gaps.

P12

Fire stopping systems

P12 Fire stopping systems

To be read with Preliminaries/ General conditions.

GENERAL

160A	MOVEMENT JOINTS 	IN FIRE RESISTING WALLS GENERALLY

•	 Soffit profiles: Flat soffit.

•	 Joint width or height (minimum): 10 mm.

•	 Joint filler: Proprietary BA certified  Intumescent Movement Joint Board.

•	 Sealant: One-part fire resisting acrylic .

Colour: Grey.

170	EXTERNAL WALLS 	GENERALLY

•	 Panel material or joint filler: Boards - exfoliated vermiculite.

•	 Sealant: One-part fire resisting acrylic .

-	Colour: Black.

SYSTEM PERFORMANCE

210	DESIGN

•	 Design: Complete the design of the fire stopping system.

•	 Proposals: Submit drawings, technical information, calculations and manufacturers'

literature.

PRODUCTS

305	PRODUCT CERTIFICATION

•	 Certification: For products specified generically, submit evidence of compliance with the

specification.

•	 Acceptable evidence: Fire test certificate from NAMAS laboratory.

335A	INTUMESCENT FOAMS

•	 Manufacturer: Contractor's choice, BBA certified - provide sample for CA approval.

-	Product reference: Submit proposals.

350A	INTUMESCENT PUTTIES

•	 Manufacturer: Contractor's choice, BBA certified - provide sample for CA approval.

-	Product reference: Submit proposals.

390	SEALANTS - FIRE RESISTING SILICONE

•	 Standard: To BS 5889 Type A.

•	 Manufacturer: Contractor's choice, BBA certified - provide sample for CA approval .

Product reference: Contractor's choice to BS EN 11600, class F20LM.

395	SEALANTS - ONE-PART FIRE RESISTING ACRYLIC

•	 Manufacturer: Contractor's choice, BBA certified - provide sample for CA approval .

Product reference: Contractor's choice to BS EN 11600, class F20LM.

410	SEALANTS - TWO-PART FIRE RESISTING POLYSULFIDE

•	 Manufacturer: Contractor's choice, BBA certified - provide sample for CA approval .

Product reference: Contractor's choice to BS EN 11600, class F20LM.

EXECUTION

620	WORKMANSHIP GENERALLY

•	 Gaps: Seal gaps between building elements and services, to provide fire resistance and

resist the passage of smoke.

•	 Adjacent surfaces: Prevent overrun of sealant or mortar on to finished surfaces.

640	INSTALLING BOARDING

•	 Position of boarding: Within opening.

•	 Framing: Provide trimming around openings.

•	 Bedding: Bed boarding on fire resisting silicone.

•	 Double layers of board: Staggered butt joints.

-	Joints: Seal with board adhesive.

•	 Fixing: Manufacturers guidance.

660	INSTALLING INTUMESCENT FOAM

•	 New joints: Remove builder's debris, mortar droppings, grease, and the like.

•	 Old joints: Clean and remove existing sealant from the joint.

•	 Priming: Lightly moisten substrate with water.

•	 Application: Fill joint to approximately half its depth, allowing foam to expand to face of

joint.

•	 Trimming: Do not trim or cut the face of the cured foam.

670	APPLYING INTUMESCENT MORTAR

•	 Sequence: Install mortar after services are permanently installed.

•	 Loose dust and combustible materials: Remove from the opening.

•	 Shuttering: Install suitable shuttering panels to the faces of the opening.

•	 Temperature: Do not apply mortar when it could be damaged by frost.

•	 Powder: water ratio: Manufacturers guidance.

•	 Mortar cure: Do not disturb mortar before final set has taken place.

•	 Shuttering: Remove after mortar has cured.

710	INSTALLING BATTS

•	 Installing batts: Fit tight into void between the floor or wall and the penetrating services.

•	 Face of batts: Flush with the surface of wall, floor or soffit.

•	 Joints: Sealed with fire resisting sealant.

•	 Gaps between services and bulkhead: Seal with fire resisting sealant.

730	FIXING PIPE COLLARS

•	 Collar fixing: Self-tapping screws.

•	 Gap around collar: Seal with intumescent foam.

•	 Length of wraps: Project 50 mm from each side of the element.

740	INSERTING SEALANT BACKING MATERIAL

•	 New joints: To full depth of joint leaving sufficient depth to apply sealant.

•	 Old joints: Remove existing sealant, backing tape and joint filler.

750	APPLYING SEALANT TO JOINTS

•	 De-greasing: Cleaner by sealant manufacturer.

•	 Priming: Primer by sealant manufacturer.

•	 Depth of sealant: As required.

•	 Temperature: Do not apply water based sealants when they could be damaged by frost.

COMPLETION

910	CLEANING

•	 Masking tapes: Remove.

•	 Cleaning: Clean off splashes and droppings. Wipe down finishes.

920	INSPECTION

•	 Notice for inspection (minimum): 4 days.

P20

Unframed isolated trims/ skirtings/ sundry items

P20 Unframed isolated trims/ skirtings/ sundry items

To be read with Preliminaries/ General conditions

110	SOFTWOODSKIRTINGS GENERALLY

•	 Quality of wood and fixing: To BS 1186-3.

-	Species: FSC certified European redwood.

-	Class: 1.

•	 Moisture content at time of fixing: 9-13%.

•	 Preservative treatment: Not required.

•	 Fire rating: Not applicable.

•	 Profile: Moulded.

-	Finished size: 19 x 100 mm.

•	 Finish as delivered: Prepared and primed, as section M60.

•	 Fixing: Plugged, screwed and pelleted at 450 centres.

111	SOFTWOODARCHITRAVES GENERALLY

•	 Quality of wood and fixing: To BS 1186-3.

-	Species: FSC certified European redwood.

-	Class: 1.

•	 Moisture content at time of fixing: 9-13%.

•	 Preservative treatment: Not required.

•	 Fire rating: Not applicable.

•	 Profile: Moulded.

-	Finished size: 19 x 75 mm.

•	 Finish as delivered: Prepared and primed, as section M60.

•	 Fixing: Plugged, screwed and pelleted at 450 centres.

200	MEDIUM DENSITY FIBREBOARDWINDOW SILL BOARDS

•	 Manufacturer:   	Contractor's choice, provide sample for CA approval.

-	Product reference: Board to receive gloss paint finish.

•	 Standard: To BS EN 622-5.

-	Type: MDF.H.

-	Formaldehyde class: To BS EN 622-1, Class E1.

•	 Fire rating: Not applicable.

•	 Thickness: 25 mm.

Edges: Quarter rounded.

•	 Finish: Prepared and primed as section M60 .

•	 Support/ Fixing: Fix to softwood grounds with lost head nails at 600 mm centres..

270B	PLASTICS VENEERED BOARDDUCT & PIPE COVERS WHERE REQUIRED

•	 Standard: To BS 4965.

-	Durability class: D2.

-	Laminate grade: VG.

-	Fire rating: Not applicable.

•	 Colour/Finish: White/smooth.

•	 Balancing veneer: Non-decorative.

•	 Finished thickness: -.

•	 Edges: Matching plastics strip.

•	 Support/ Fixing: Screw fixed.

EXECUTION

510	INSTALLATION GENERALLY

•	 Joinery workmanship: As section Z10.

•	 Metal workmanship: As section Z11.

•	 Methods of fixing and fasteners: As section Z20 where not specified.

•	 Straight runs: To be in one piece, or in long lengths with as few joints as possible.

•	 Running joints: Location and method of forming to be agreed where not detailed.

•	 Joints at angles: Mitre, unless shown otherwise.

•	 Position and level: To be agreed where not detailed.

P21

Door/ window ironmongery

P21 Door/ window ironmongery

To be read with Preliminaries/ General conditions.

PRE-TENDER

10A	DETAILS AND LOCATIONS

•	 Details and locations of ironmongery : REFER TO DEVELOPERS PROPOSALS.

•	 Fixing: As sections L10 and L20.

GENERAL

120A	IRONMONGERY RANGE SELECTED BY CONTRACTOR

•	 Source: Contractor's choice from a single co-ordinated range.

•	 Guarantee: Contractor to provide 5 year guarantee for all ironmongery.

•	 Notification: Submit details of selected range, manufacturer and/ or supplier.

•	 Principal material/ finish: Polished stainless steel, grade 1.4301 (304) .

•	 Items unavailable within selected range: Submit proposals.

140	SAMPLES

•	 General: Before placing orders with suppliers submit labelled samples of the following: All

ironmongery, towel rails, coat hooks etc .

-	Conformity: Retain samples on site for the duration of the contract. Ensure conformity of

ironmongery as delivered with labelled samples.

170	IRONMONGERY FOR FIRE DOORS

•	 Relevant products: Ironmongery fixed to, or mortised into, the component parts of a fire

resisting door assembly.

•	 Compliance: Ironmongery included in successful tests to BS 476-22 or BS EN 1634-1 on

door assemblies similar to those proposed.

-	Certification: Submit evidence of successful testing by UKAS accredited laboratory .

•	 Melting point of components (except decorative non-functional parts): 800°C minimum.

P30

Trenches, pipeways and pits for buried engineering services

P30 Trenches, pipeways and pits for buried engineering services

To be read with Preliminaries/ General conditions.

GENERALLY

140	BURIED ENGINEERING SERVICES SYSTEMS GENERALLY

•	 Positions and dimensions: To be highlighted on M&E drawings & confirmed by architect.

•	 Service routes and enclosures: Surface ducts with covers (internal), as section P31.

-	Support and backfill: Concrete, as section E10.

-	Accessories: Submit proposals.

•	 Access points: To be specified by M&E consultants.

EXECUTION

625	TRENCHES

•	 Trench width: As small as practicable.

•	 Trench sides: Vertical..

•	 Trench bottoms: Remove mud, rock projections, boulders and hard spots. Trim level.

•	 Give notice: To inspect trench for each section of the work.

655	CONCRETE SURROUND FOR PIPEDUCTS

•	 Concrete blinding: 25 mm thick over full width of trench. Allow to set.

•	 Pipe ducts:

-	Temporary support: Folding wedges of compressible board. Prevent flotation.

-	Height above blinding (minimum): 100 mm.

•	 Surround, to full width of trench:

-	Depth: To 150 mm above crown of pipe duct or as shown on drawings.

-	Vertical construction joints: At face of flexible pipe duct joints using 18 mm thick

compressible board pre-cut to pipe duct profile.

-	Socketed pipe ducts: Fill gaps between spigots and sockets with resilient material to

prevent entry of concrete.

660	CONCRETE SURROUND FOR SHALLOW PIPEDUCTS UNDER BUILDINGS

•	 Locations: Where pipe duct crowns are less than 300 mm below underside of slab.

•	 Timing: Excavate trench after hardcore has been laid and compacted.

•	 Concrete blinding: 25 mm thick over full width of trench. Allow to set.

•	 Pipe ducts:

-	Temporary support: Folding wedges of compressible board. Prevent flotation.

-	Height above blinding (minimum): 100 mm.

•	 Surround: Cast integral with slab. Extend surround to within 150 mm of nearest flexible

joint.

665	PIPE DUCT RUNS NEAR FOUNDATIONS

•	 Concrete surround: Provide in locations where bottom of trench is lower than bottom of

foundation. Measurements are horizontal clear distances between nearest edges of

foundations and pipe trenches.

-	Trenches less than one metre from foundations: Top of concrete surround not lower than

bottom of foundation.

-	Trenches more than one metre from foundations: Top of concrete surround not lower

than D mm below bottom of foundation, where D mm is horizontal distance of trench

from foundation, less 150 mm.

670	BEDDING OF FRAMES FOR ACCESS COVERS AND SURFACE BOXES

•	 Bedding: Solidly in mortar, centrally over opening and level with surrounding finishes.

-	In road or pavement finishes: Flush, and square with block or slab joints.

-	In grassed areas: Set 30 mm below soil surface. Haunch back edge of bedding so that it

is not visible.

675	BACKFILLING GENERALLY

•	 Backfill from top of pipe duct surround: Material excavated from the trench.

•	 Backfilling: Lay and compact in 300 mm maximum layers. Do not use heavy compactors

before backfill is 600 mm deep.

710	TEMPORARY BRIDGES

•	 Construction traffic: After backfilling, provide temporary bridges over trenches to prevent

damage to pipe ducts or services.

720	WARNING MARKER BOARDS, TAPES AND TILES

•	 Installation: During backfilling.

•	 Depth: Continuously, 200–300 mm above service pipe or cable or to requirements of

service undertaker if different.

-	Pipelines deeper than 2 m lay additional marker 600 mm above the top of the pipeline or

to requirements of service undertaker if different.

COMPLETION

910	INSPECTION

•	 Inspection of pipe ducts: Before backfilling.

-	Inspection by: Service undertakers representative.

930	DOCUMENTATION

•	 Record drawings: Submit.

P31

Holes, chases, covers and supports for services

P31 Holes, chases, covers and supports for services

To be read with Preliminaries/ General conditions.

EXECUTION

610	COORDINATION

•	 Locations and dimensions of holes and chases for services: Submit details to M&E details

And requirements

620	HOLES AND CHASES IN IN SITU CONCRETE

•	 Cast in: Holes larger than 10 mm diameter and chases.

•	 Cutting and drilling:

-	Permitted for holes not larger than 10 mm diameter.

Not permitted for holes larger than 10 mm diameter except as indicated on drawings.

630	HOLES AND CHASES IN PRECAST CONCRETE

•	 Cutting and drilling: Not permitted except as indicated on drawings.

640	HOLES IN STRUCTURAL STEELWORK

•	 Cutting and drilling: Not permitted except as indicated on drawings.

650	HOLES, RECESSES AND CHASES IN MASONRY

•	 Locations: To maintain integrity of strength, stability and sound resistance of construction.

•	 Sizes: Minimum needed to accommodate services.

-	Holes (maximum): 300 x 300 mm.

•	 Walls of hollow or cellular blocks: Do not chase.

•	 Walls of other materials:

-	Vertical chases: No deeper than one third of single leaf thickness, excluding finishes.

-	Horizontal or raking chases: No longer than 1 m. No deeper than one sixth of the single

leaf thickness, excluding finishes.

•	 Chases and recesses: Do not set back to back. Offset by a clear distance at least equal to

the wall thickness.

•	 Cutting: Do not cut until mortar is fully set. Cut carefully and neatly. Avoid spalling, cracking

and other damage to surrounding structure.

660	PREFORMED HOLES IN MASONRY

•	 Width of holes without bridging over (maximum): one block.

-	Holes requiring bridging: Submit proposals.

670	NOTCHES AND HOLES IN STRUCTURAL TIMBER

•	 General: Avoid if possible.

•	 Sizes: Minimum needed to accommodate services.

•	 Position: Do not locate near knots or other defects.

•	 Notches and holes in same joist: Minimum 100 mm apart horizontally.

•	 Notches in joists: Locate at top. Form by sawing down to a drilled hole.

-	Depth (maximum): 0.125 x joist depth.

-	Distance from supports: Between 0.07 and 0.25 x span.

•	 Holes in joists: Locate on neutral axis.

-	Diameter (maximum): 0.25 x joist depth.

-	Centres (minimum): 3 x diameter of largest hole.

-	Distance from supports: Between 0.25 and 0.4 of span.

•	 Notches in roof rafters, struts and truss members: Not permitted.

•	 Holes in struts and columns: Locate on neutral axis.

-	Diameter (maximum): 0.25 x minimum width of member.

-	Centres (minimum): 3 x diameter of largest hole.

Distance from ends: Between 0.25 and 0.4 of span

690	INSTALLING PIPE SLEEVES

•	 Sleeves: Fit to pipes passing through building fabric.

•	 Material: Match pipeline.

•	 Size: One or two sizes larger than pipe to allow clearance.

•	 Finish: Install sleeves flush with building finish. In areas where floors are washed down,

install protruding 100 mm above floor finish.

•	 Masking plates: Fit at visible penetrations, including through false ceilings of occupied

rooms.

710	SEALING OPENINGS IN MASONARY & FLOORS

•	 Service: All.

•	 Location: Walls and floors.

•	 Sealing material: Proprietary intumescent sealant.

•	 Method: Gun applied.

•	 Performance requirement: Moisture vapour and airtight.

740	INSTALLING METER CABINETS

•	 Fixing: Heavy duty masonry fixing bolts.

•	 Keys: Hand over to Employer at completion.

Q

Paving/Planting/Fencing/Site furniture

Q28

Topsoil and growing media

Q28 Topsoil and growing media

To be read with Preliminaries/ General conditions.

200	GRADING SUBSOIL

•	 General: Grade to smooth flowing contours to achieve specified finished levels of topsoil.

•	 Areas of thicker topsoil: Excavate locally.

250	SUBSOIL SURFACE PREPARATION

•	 General: Excavate and/ or place fill to required profiles and levels, as section D20.

•	 Loosening:

-	Light and non-cohesive subsoils: When ground conditions are reasonably dry, loosen

thoroughly to a depth of 300 mm.

-	Stiff clay and cohesive subsoils: When ground conditions are reasonably dry, loosen

thoroughly to a depth of 450 mm.

-	Rock and chalk subgrades: Lightly scarify to promote free drainage.

•	 Stones: Immediately before spreading topsoil, remove stones larger than 50 mm.

•	 Remove Arisings, contaminants and debris and Builders rubble.

260	INSPECTING FORMATIONS

•	 Give notice: Before spreading topsoil for lawn areas and planting beds.

•	 Notice period: 14 days.

310	PREPARATION OF UNDISTURBED TOPSOIL

•	 Standard: In accordance with BS 4428

-	Grading and cultivation: To suit cultivation operations specified in Q30 & Q31.

•	 Hard ground: Break up thoroughly.

•	 Clearing: Remove visible roots and large stones with a diameter greater than 50 mm.

•	 Areas covered with turf or thick sward: Plough or dig over to full depth of topsoil.

•	 Fallow period (minimum): One month.

•	 Weed control: At appropriate times re-cultivate at fortnightly intervals to suppress weed

growth.

335	SURPLUS TOPSOIL TO BE REMOVED

•	 Generally: Remove from site topsoil remaining after completion of all landscaping work.

340	IMPORTED TOPSOIL TO BS 3882

•	 Quantity: Provide as necessary to make up any deficiency of topsoil existing on site and to

complete the work.

•	 Standard: To BS 3882.

•	 Grade: Multipurpose.

•	 Source: Contractor's choice.

•	 Submit: Declaration of analysis including information detailing each of the relevant

parameters given in BS 3882, clause 6 and table 2.

•	 Additional analyses: Not required.

355	COMPOST

•	 Standard: In accordance with PAS 100.

•	 Supplier: Submit proposals.

-	Product reference: Contractor's choice - refer to landscape proposals, management

plan, and ecology report.

•	 Type: Sanitized and stabilized compost.

•	 Horticultural parameters:

-	pH (1:5 water extract): 7.0-8.7.

-	Electrical conductivity (maximum, 1:5 water extract): 200 mS/m.

-	Moisture content (m/m of fresh weight): 35-55%.

-	Organic matter (minimum): 25%.

-	Grading (air dried samples): 99% passing 25 mm screen, and 90% a 10 mm screen

mesh aperture.

-	Carbon:Nitrogen ratio (maximum): 20:1.

•	 Texture: Friable.

•	 Objectionable odour: None.

•	 Composting Association certification: Required.

•	 Submit: Declaration of analysis.

•	 Additional analyses: Not required.

•	 Samples: Supply 5 kg sample before ordering.

•	 Application rate: 2.5 m³/100 m².

•	 Timing: Apply prior to cultivation.

395	PEAT

•	 Peat or products containing peat: Do not use.

650	NOTICE OF IMPORTING TOPSOIL

•	 Give notice: Before stripping topsoil for transfer to site.

-	Notice period: 14 days.

660	SAMPLE LOAD OF IMPORTED TOPSOIL

•	 General: Deliver to site a sample load of not less than 5 m³.

•	 Give notice: Allow inspection before making further deliveries to site. Retain for comparison

with subsequent loads.

-	Notice period: 14 days.

670	CONTAMINATION

•	 General: Do not use topsoil contaminated with subsoil, rubbish or other materials that are:

-	Corrosive, explosive or flammable.

-	Hazardous to human or animal life.

-	Detrimental to healthy plant growth.

•	 Subsoil: In areas to receive topsoil, do not use subsoil contaminated with the above

materials.

•	 Give notice: If any evidence or symptoms of soil contamination are discovered on the site,

or in topsoil to be imported.

690	HANDLING TOPSOIL

•	 Aggressive weeds: Give notice and obtain instructions before moving topsoil.

•	 Plant: Select and use plant to minimize disturbance, trafficking and compaction.

•	 Contamination: Do not mix topsoil with:

-	Subsoil, stone, hardcore, rubbish or material from demolition work.

-	Other grades of topsoil.

•	 Multiple handling: Keep to a minimum. Use or stockpile topsoil immediately after stripping.

•	 Wet conditions: Handle topsoil in the driest condition possible. Do not handle during or

after heavy rainfall or when it is wetter than the plastic limit less 3%, to BS 1377-2.

700	SPREADING TOPSOIL

•	 Temporary roads/surfacing: Remove before spreading topsoil.

•	 Layers:

-	Depth (maximum): 150 mm.

-	Gently firm each layer before spreading the next.

•	 Depths after firming and settlement (minimum): 150 mm.

•	 Crumb structure: Do not compact topsoil. Preserve a friable texture of separate visible

crumbs wherever possible.

710	LOOSE TIPPING OF TOPSOIL

•	 General: Do not firm, consolidate or compact topsoil when laying. Tip and grade to

approximate levels in one operation with minimum of trafficking by plant.

•	 Depths after settlement (minimum): 150 mm.

910	FINISHED LEVELS OF TOPSOIL AFTER SETTLEMENT

•	 Above adjoining paving or kerbs: 20 mm.

•	 Below dpc of adjoining buildings: Not less than 150 mm.

•	 Shrub areas: Higher than adjoining grass areas by 100 mm.

•	 Within root spread of existing trees: Unchanged.

•	 Adjoining soil areas: Marry in.

•	 Thickness of turf or mulch: Included.

920	DOCUMENTATION

•	 Timing: Submit at handover.

•	 Contents:

-	Full description of all soil components.

-	Record of source for all soil components.

-	Analyst's report for each test carried out.

-	Record drawings showing the location of all soils by type and grade.

•	 Number of copies: 2.

Q30

Seeding/ turfing

Q30 Seeding/ turfing

To be read with Preliminaries/General conditions.

GENERAL INFORMATION/REQUIREMENTS

115A	SEEDED AND TURFED AREAS

Roll out turf should be laid in all front and rear gardens instead of seeding in all cases. In

curtilage lawns must become the responsibility of tenant at handover.

Communal planting areas must be fully maintained by the landscape contractor for 12

months after completion of planting. Any costs for the maintenance service must be

included within the contract. Maintenance Department should take responsibility for the

landscaping of each schemes landlords areas on date of handover and relevant costs

should be deducted from tender sum to cover same. Tenants should be made aware of

their responsibility to care for turf within the curtilage of their homes.

•	 Growth and development: Healthy, vigorous grass sward, free from the visible effects of

pests, weeds and disease.

•	 Appearance: A closely knit, continuous ground cover of even density, height and colour.

120	CLIMATIC CONDITIONS

•	 General: Carry out the work while soil and weather conditions are suitable.

145	WATERING

•	 Quantity: Wet full depth of topsoil.

•	 Application: Even and without displacing seed, seedlings or soil.

•	 Frequency: As necessary to ensure the establishment and continued thriving of all

seeding/turfing.

160	NOTICE

•	 Give notice before:

-	Setting out.

-	Applying herbicide.

-	Applying fertilizer.

-	Preparing seed bed.

-	Seeding or turfing.

-	Visiting site during maintenance period.

•	 Period of notice: 2 weeks.

170	SETTING OUT

•	 Boundaries: Mark clearly.

•	 Delineation: In straight lines or smoothly flowing curves as shown on drawings.

PREPARATION

210	HERBICIDEFOR ALL GRASSED AREAS

•	 Type: Suitable for suppressing perennial weeds.

•	 Timing: Allow fallow period before cultivation.

Duration: As manufacturer's recommendation.

212	SEED BED CLEANING BEFORE SOWINGALL GRASSED AREAS

•	 Operations: As seed supplier's recommendations in accordance with landscaping plan and

maintenance plans and ecology report.

226	COMPOST 	GENERALLY

•	 Type: Sanitized and stabilized compost.

•	 Standard: In accordance with PAS 100.

•	 Supplier: Contractor's choice.

-	Product reference: Contractor's choice.

•	 Standard: To PAS 100.

•	 Horticultural parameters:

-	pH (1:5 water extract): 7.0-8.7.

-	Electrical conductivity (maximum, 1:5 water extract): 200 mS/m.

-	Moisture content (m/m of fresh weight): 35-55%.

-	Organic matter content (minimum): 25%.

-	Grading (air dried samples): 99% passing 25 mm screen, and 90% passing 10 mm

screen mesh aperture.

-	Carbon:Nitrogen ratio (maximum): 20:1.

•	 Texture: Friable.

•	 Objectionable odour: None.

•	 Composting Association certification: Not required.

•	 Declaration of analysis: Submit

•	 Samples: Supply 5 kg sample before ordering.

•	 Application rate: 50 mm thick layer.

•	 Timing: Apply prior to cultivation.

231	PEAT

•	 Peat or products containing peat: Do not use.

250A	CULTIVATION

•	 Compacted topsoil: Break up to full depth. Minimum overall depth of topsoil in unplanted

areas should be 250mm.

•	 Soil ameliorant/ Conditioner/ Fertilizer: Fully incorporate into topsoil to a depth of 150 mm.

•	 Tilt: Reduce topsoil to a tilt suitable for blade grading.

-	Depth: 75 mm.

-	Particle size (maximum): 5 mm.

•	 Material brought to the surface: Remove stones and clay balls larger than 50 mm in any

dimension, roots, tufts of grass, rubbish and debris.

260	GRADING

•	 Topsoil condition: Reasonably dry and workable.

•	 Contours: Smooth and flowing, with falls for adequate drainage.

-	Hollows and ridges: Not permitted.

•	 Finished levels after settlement: 25 mm above adjoining paving, kerbs, manholes etc.

•	 Blade grading: May be used to adjust topsoil levels provided depth of topsoil is nowhere

less than 125 mm .

•	 Give notice: If required levels cannot be achieved by movement of existing soil.

275	FERTILIZERFOR ALL GRASSED AREAS

•	 Type: Organic.

•	 Manufacturer: Contractor's choice.

-	Product reference: Submit proposals.

•	 Application: Before final cultivation and three to five days before seeding/ turfing.

Rate: Spread evenly at 70 g/m².

280	FINAL CULTIVATION

•	 Timing: After grading and fertilizing.

•	 Seed bed: Reduce to fine, firm tilt with good crumb structure.

-	Depth: 25 mm.

-	Surface preparation: Rake to a true, even surface, friable and lightly firmed but not over

compacted.

-	Remove surface stones/earth clods exceeding:

General areas: 30 mm.

Fine lawn areas: 10 mm.

•	 Adjacent levels: Extend cultivation into existing adjacent grassed areas sufficient to ensure

full marrying in of levels.

SEEDING

310	GRASS SEEDTO AREAS OTHER THAN FRONT AND REAR GARDENS

•	 Mixture:  Refer to landscaping plan and maintenance plans and ecology report - 35%

Chewings fescue, 35% Slender red fescue, 20% Smooth stalked meadow grass, 10%

Brown top bent.

•	 Application rate: Typically 20–35 g/m², but consult suppliers for rates for specific mixtures.

319	QUALITY OF SEEDFOR ALL GRASSED AREAS

•	 Freshness: Produced for the current growing season.

•	 Certification: Blue label certified varieties.

-	Standard: EC purity and germination regulations.

-	Official Seed Testing Station certificate of germination, purity and composition: Submit

when requested.

•	 Samples of mixtures: Submit when requested.

330	SOWING

•	 General: Establish good seed contact with the root zone.

•	 Method: Manually broadcast, raked and rolled.

-	Distribution: 2 equal sowings at right angles to each other and diagonally to main axis.

335	GRASS SOWING SEASON

•	 Grass seed generally: April to June or August to October.

336	WILDFLOWER SOWING SEASON

•	 Wildflower seed generally: March to May or August to October.

340	PRE-EMERGENT HERBICIDEFOR ALL GRASSED AREAS

•	  Standard: Pesticide Safety Directorate approved.

•	 Application rate: In accordance with manufacturer's written recommendation.

-	Timing: Immediately after sowing.

352	EDGES TO SEEDED AREASADJACENT TO PLANTING BEDS AND TREE PITS

•	 Timing: After seeded areas are well established.

•	 Edges: Clean straight lines or smooth curves.

-	Mulch and soil: Draw back to permit edging.

•	 Arisings: Remove.

•	 Completion: Respread soil and mulch.

TURFING

400	CULTIVATED TURFTO FRONT AND REAR GARDENS

•	 Supplier: Contractor's choice.

-	Product reference: Submit proposals.

•	 Properties of soil used for turf production: Well drained sandy loam.

410	TURF TO BS 3969TO FRONT AND REAR GARDENS

•	 Standard: To BS 3969, free from undesirable grasses and weeds.

-	Grade: General purpose utility turf.

•	 Source: Submit proposals.

•	 Herbicide treatment: Apply not less than four weeks and not more than three months

before lifting.

420	DELIVERY AND STORAGE

•	 Timing: Lay turf with minimum possible delay after lifting. If delay occurs, lay turf out on

topsoil and keep moist.

•	 Frosty weather or waterlogged ground: Do not lift turf.

•	 Delivery: Arrange to avoid need for excessive stacking.

•	 Stacking height (maximum): 1 m.

•	 Dried out or deteriorated turf: Do not use.

430	TURFING GENERALLY

•	 Time of year: To be agreed.

•	 Timing of laying:

-   	Spring and summer: Within 18 hours of delivery.

-	Autumn and winter: Within 24 hours of delivery.

•	 Weather conditions: Do not lay turf when persistent cold or drying winds are likely to occur

or soil is frost bound, waterlogged or excessively dry.

•	 Working access: Planks laid on previously laid turf. Do not walk on prepared bed or newly

laid turf.

•	 Jointing: Laid with broken joints, well butted up. Do not stretch turf.

•	 Edges: Whole turfs, trimmed to a true line.

•	 Adjusting levels: Remove high spots and fill hollows with fine soil.

•	 Consolidating: Lightly and evenly firm as laying proceeds to ensure full contact with

substrate. Do not use rollers.

•	 Dressing, brushed well in to completely fill all joints: Compost .

•	 Watering: Thoroughly water completed turf immediately after laying. Check that water has

penetrated into the soil below.

PROTECTING/CUTTING

530	FIRST CUT OF GRASSED AREAS

•	 Timing: When grass is reasonably dry.

-	Height of initial growth: 40-75 mm.

•	 Preparation:

-	Debris and litter: Remove.

-	Stones and earth clods larger than 25 mm in any dimension: Remove

•	 Height of first cut: 40 mm.

•	 Mower type: Rotary.

•	 Arisings: Remove from site.

590	CLEANLINESS

•	 Soil and arisings: Remove from hard surfaces.

•	 General: Leave the works in a clean, tidy condition at Completion and after any

maintenance operations.

MAINTENANCE

605	MAINTENANCE

•	 Duration: Carry out the following operations from completion of seeding/ turfing until practical

completion.

610	FAILURES OF SEEDING/TURFING

•	 Defective materials or workmanship: Areas that have failed to thrive.

-	Exclusions: Theft or malicious damage.

•	 Method of making good: Recultivation and reseeding/ returfing.

•	 Timing of making good: The next suitable planting season.

680	MAINTENANCE FERTILIZERFOR ALL GRASSED AREAS

•	 March application: 15:10:10 Spring turf fertilizer at 35 g/m².

•	 September application: 5:10:10 Autumn turf fertilizer at 50 g/m².

Q31

External planting

Q31 External planting

To be read with Preliminaries/General conditions.

GENERAL INFORMATION/ REQUIREMENTS

REFER TO DEVELOPERS PROPOSALS AND ECOLOGIST

RECOMMENDATIONS AND REPORT FOR DETAILS OF PLANTING

112	SITE CLEARANCE GENERALLY

•	 General: Remove rubbish, concrete, metal, glass, decayed vegetation and contaminated

topsoil.

•	 Stones: Remove those with any dimension exceeding 50 mm.

•	 Contamination: Remove material containing toxins, pathogens or other extraneous

substances harmful to plant, animal or human life.

•	 Vegetation: Clear scrub to ground level by flail mowing and remove arisings.

•	 Large roots: Grub up and dispose of without undue disturbance of soil and adjacent areas.

•	 Additional requirements: none.

118	SOIL CONDITIONS

•	 Soil for cultivating and planting: Moist, friable and (excepting aquatic/ marginal planting) not

waterlogged.

•	 Frozen or snow covered soil: Give notice before planting. Provide additional root

protection. Prevent planting pit sides and bases and backfill materials from freezing.

120	CLIMATIC CONDITIONS

•	 General: Carry out the work while soil and weather conditions are suitable.

-	Strong winds: Do not plant.

125	TIMES OF YEAR FOR PLANTING

•	 Deciduous trees and shrubs: Late October to late March.

•	 Conifers and evergreens: September/ October or April/ May.

•	 Herbaceous plants (including marginal): September/ October or March/ April.

•	 Container grown plants: At any time if ground and weather conditions are favourable.

-	Watering and weed control: Provide as necessary.

•	 Dried bulbs, corms and tubers: September/ October.

•	 Colchicum (crocus): July/ August.

•	 Green bulbs: After flowering in spring.

•	 Wildflower plugs: Late August to mid November or March/ April.

•	 Aquatic plants: May/ June or September/ October.

130	MECHANICAL TOOLS

•	 Restrictions: Do not use within 100 mm of tree and plant stems.

145	WATERING

•	 Quantity: Wet full depth of topsoil.

•	 Application: Even and without damaging or displacing plants or soil.

•	 Frequency: As necessary to ensure establishment and continued thriving of planting.

160	NOTICE

•	 Give notice before:

-	Setting out.

-	Applying herbicide.

-	Applying fertilizer.

-	Delivery of plants/ trees.

-	Planting shrubs.

-	Planting trees into previously dug pits.

-	Watering.

-	Visiting site during maintenance period.

•	 Period of notice: 2 weeks.

200	PLANTS/ TREES - GENERAL

•	 Condition: Materially undamaged, sturdy, healthy and vigorous.

•	 Appearance: Of good shape and without elongated shoots.

•	 Hardiness: Grown in a suitable environment and hardened off.

•	 Health: Free from pests, diseases, discoloration, weeds and physiological disorders.

•	 Budded or grafted plants: Bottom worked.

•	 Root system and condition: Balanced with branch system.

-	Standard: The National Plant Specification.

•	 Species: True to name.

•	 Origin/ Provenance: Local provenance.

Definition: Origin and Provenance have the meaning given in the National Plant

Specification.

216	PLANTS/ TREES - SPECIFICATION CRITERIA

•	 Name, forms, dimensions and other criteria: To the relevant part of BS 3936.

225	BULBS/ CORMS/ TUBERS

•	 Condition: Firm, entire, not dried out or shrivelled.

•	 Health: Free from pests, diseases and fungus.

•	 Handling: Remove from packaging immediately.

•	 Storage: Permitted only when necessary.

-	Location: Well ventilated, dark, covered, rodent proof container, away from exhausts and

fruit.

-	Duration: Minimum period.

-	Temperature: 18-21°C.

235	CONTAINER GROWN PLANTS/ TREES

•	 Growing medium: With adequate nutrients for plants to thrive until permanently planted.

•	 Plants: Centred in containers, firmed and well watered.

•	 Root growth: Substantially filling containers, but not root bound, and in a condition

conducive to successful transplanting.

•	 Hardiness: Grown in the open for at least two months before being supplied.

•	 Containers: With holes adequate for drainage when placed on any substrate commonly

used under irrigation systems.

245	LABELLING AND INFORMATION

•	 General: Provide each plant/ tree or group of plants/ trees of a single species or cultivar

with supplier's labelling for delivery to site, showing:

-	Full botanical name.

-	Total number.

-	Number of bundles.

-	Part bundles.

-	Supplier's name.

-	Employer's name and project reference.

-	Plant specification, in accordance with scheduled National Plant Specification

categories.

•	 Additional information: Submit on request: Potting dates and Pruning dates.

246	LABELLING AND INFORMATION

•	 Standard: To BS 3936.

260	PLANT/ TREE SUBSTITUTION

•	 Plants/ trees unobtainable or known to be likely to be unobtainable at time of ordering:

Submit alternatives, stating:

-	Price.

-	Difference from specified plants/ trees.

•	 Approval: Obtain before making any substitution.

265	PLANT HANDLING, STORAGE TRANSPORT AND PLANTING

•	 Standard: To HTA 'Handling and establishing landscape plants'.

•	 Frost: Protect plants from frost.

•	 Handling: Handle plants with care. Protect from mechanical damage and do not subject to

shock, e.g. by dropping from a vehicle.

•	 Plant packaging: Black polyethylene bags.

•	 Packaging of bulk quantities: Pallets or bins sealed with polyethylene and shrink wrapped.

•	 Planting: Upright or well balanced with best side to front.

280	TREATMENT OF TREE WOUNDS

•	 Cutting: Keep wounds as small as possible.

-	Cut cleanly back to sound wood using sharp, clean tools.

-	Leave branch collars. Do not cut flush with stem or trunk.

-	Set cuts so that water will not collect on cut area.

•	 Fungicide/ Sealant: Do not apply unless instructed.

285	PROTECTION OF EXISTING GRASS

•	 General: Protect areas affected by planting operations using boards/ tarpaulins.

-	Excavated or imported material: Do not place directly on grass.

-	Duration: Minimum period.

290	SURPLUS MATERIAL

•	 Subsoil, stones, debris, wrapping material, canes, ties, temporary labelling, rubbish,

pruning’s and other arisings: Remove.

PLANT CONTAINERS

292	PREFABRICATED PLANT CONTAINERS

•	 Manufacturer: Submit proposals.

-	Product reference: Contractor's choice.

•	 Material: Stone.

•	 Dimensions/ Shape: To suite plant.

•	 Lining: Not required.

•	 Accessories: None.

PREPARATION OF PLANTING BEDS/ PLANTING MATERIALS

305	WEED CONTROLFOR INVASIVE NON-NATIVE WEEDS

•	 Locations: All planting areas.

•	 General: Prevent weeds from seeding and perennial weeds from becoming established, by

hand weeding.

315	LIME	FOR GENERAL APPLICATION

•	 Locations: All planting areas.

•	 Composition: Fine ground limestone containing not less than 50% of CaO equivalent.

•	 Application: Spread evenly.

-	Timing: Immediately before cultivation.

-	Rate: As recommended by contractor.

341	PEAT

•	 Peat or products containing peat: Do not use.

PLANTING SHRUBS/ HERBACEOUS PLANTS/ BULBS

400	RANDOM PLANT LAYOUTTO ALL BEDS

•	 Spacing: Random groups of 3-11 plants of the same species..

•	 Density: As advised by plant guidance.

435	CLIMBING PLANTS USED AS GROUND COVER

•	 Planting:

-	Canes or other supports: Remove.

-	Arrangement: Spread stems.

•	 Fixing: Pinned to ground to ensure good contact.

445	PLANTING BULBS/ CORMS/ TUBERS

•	 Depth: Top of bulb/ corm/ tuber at a depth of approximately twice its height, base in contact

with bottom of hole.

•	 Backfilling: Finely broken soil. Lightly firm to existing ground level.

•	 Naturalized planting in existing grassed areas:

-	Scattering: Random. Plant bulbs/ corms/ tubers where they fall.

Planting: Neatly remove a plug of turf and replace after planting.

470	FORMAL HEDGES

•	 Shrubs for hedges: Consistent in species, cultivar and clone to ensure a uniform hedge.

•	 Planting: In trenches large enough to take full spread of roots. Set out plants evenly.

471	NATURALIZED HEDGES

•	 Planting: In trenches large enough to take full spread of roots. Set out plants evenly.

472	FENCING SUPPORT FOR NEW HEDGES

•	 Type: Timber post and general pattern wire mesh.

•	 Standard: To BS 1722-2.

•	 Height: 600 mm.

•	 Timing: Before planting hedge.

•	 Support: Lightly secure hedge plants to fence wires at appropriate intervals.

480	AFTER PLANTING

•	 Watering: Immediately after planting, thoroughly and without damaging or displacing plants

or soil.

•	 Firming: Lightly firm soil around plants and fork and/ or rake soil, without damaging roots,

to a fine tilt with gentle cambers and no hollows.

•	 Top dressing: Sanitized and stabilized compost.

Depth: 25-30 mm.

PLANTING TREES

500	ANTIDESICCANT FOR CONIFERS/ EVERGREENS

•	 Manufacturer: Contractor's choice.

-	Product reference: Submit proposals to client for approval.

•	 Application: Dip in or thoroughly spray before delivering to site. Spray again soon after

planting.

-	Do not apply in wet or frosty weather.

-	Ensure full coverage of underside of foliage.

505	TREE PITS

•	 Sizes: 500 mm wider than, and the same depth as the rootball.

•	 Sloping ground: Maintain horizontal bases and vertical sides with no less than minimum

depth throughout.

•	 Pit bottoms: With slightly raised centre. Break up to a depth of 200 mm.

-	Treatment: Soil ameliorant worked into pit bottoms.

•	 Pit sides: Scarify.

•	 Backfilling material: Tree backfilling material.

•	 Accessories: Tree pit drainage layer.

WOODLAND/ MATRIX/ BUFFER ZONE PLANTING

600	WOODLAND WORK GENERALLY

•	 Services: Check for below and above ground services, including land drainage, in the

vicinity. Give notice if they may be affected and obtain instructions before proceeding.

•	 Safety: Comply with Arboriculture and Forestry Advisory Group Safety leaflets.

617	REMOVING TREES AND HEDGES

•	 Identification: Clearly mark trees and hedges to be removed.

•	 Work near retained trees: Where canopies overlap, take down trees carefully in small

sections to avoid damage to adjacent trees that are to be retained.

•	 Arisings: Remove.

•	 Tree stumps: Remove mechanically to a minimum depth of 300 mm below ground level.

PROTECTING/ MAINTAINING/ MAKING GOOD DEFECTS

710	MAINTENANCE

•	 Duration: Carry out the operations in the following clauses from completion of planting until t

he end of the defects liability period.

•	 Frequency of maintenance visits: Monthly during growing season.

720	FAILURES OF PLANTING

•	 Defects due to materials or workmanship not in accordance with the Contract: Plants/

trees/ shrubs that have failed to thrive.

-	Exclusions: Theft or malicious damage after completion.

-	Rectification: Replace with equivalent plants/ trees/ shrubs.

•	 Replacements: To match size of adjacent or nearby plants of same species or match

original specification, whichever is the greater.

•	 Timing of making good: In accordance with an agreed defects rectification programme.

740	CLEANLINESS

•	 Soil and arisings: Remove from hard surfaces and grassed areas.

•	 General: Leave the works in a clean tidy condition at completion and after any

maintenance operations.

750	PLANTING MAINTENANCE GENERALLY

•	 Weed control: Maintain weed free area around each tree and shrub.

-	Diameter (minimum): The larger of 1 m or the surface of original planting pit.

-	Keep planting beds clear of weeds: By hoeing.

•	 Planted areas: Fork over beds as necessary to keep soil loose, with gentle cambers and

no hollows. Take care not to reduce depth or effect of mulch.

•	 Precautions: Ensure that trees and shrubs are not damaged by use of mowers, nylon

filament rotary cutters and similar powered tools.

•	 Staking: Check condition of stakes, ties, guys and guards.

-	Broken or missing items: Replace.

-	Rubbing: Prevent.

-	Ties: Adjust to accommodate growth.

-	Damage to bark: Cut back neatly with sharp knife. Prevent further damage.

-	Frequency of checks: Every 3 months.

•	 Firming up: Gently firm loosened soil around trees/ shrubs. Straighten leaning trees/

shrubs.

•	 Trees: Spray crown when in leaf during warm weather.

-	Timing: After dusk.

•	 Watering: When instructed.

755	PLANTING MAINTENANCE - FERTILIZER

•	 Time of year: March or April.

•	 Fertilizer: Sanitized and stabilized compost.

-	Manufacturer: Contractor's choice.

-	Product reference: Submit proposals.

•	 Application: Evenly spread, carefully incorporating below mulch materials.

•	 Application rate: To manufacturer's recommendations.

760	PLANTING MAINTENANCE - PRUNING

•	 General: Prune to promote healthy growth and natural shape.

-	Dead, dying, diseased wood and suckers: Remove.

-	Timing: As appropriate to the species.

-	Trees: Favour a single central leading shoot.

•	 Arisings: Remove.

770	WOODLAND PLANTING MAINTENANCE

•	 Watering: Only as necessary to prevent plants wilting.

•	 Loose plants: Refirm surrounding soil, without compacting.

•	 Weed control: Cut down and remove weeds prior to setting seed in a 1 m diameter area

around each tree.

•	 Vegetation except trees and coppice shoots to be retained: Cut within the plantation area.

-	Height (maximum): 50 mm.

-	Arisings: Leave between rows.

•	 Mechanical, chemical or mulching methods of vegetation control: Submit proposals.

•	 Ditches and drains: Keep clear.

•	 Watering: Contractor's choice.

780	MAINTENANCE INSTRUCTIONS

•	 General: Before end of the maintenance period, submit printed instructions recommending

procedures to be established by the Employer for maintenance of the planting work for one

full year: Provide a schedule of any ongoing maintenance problems experienced during the

defects liability period.

Q35

Landscape maintenance

Q35 Landscape maintenance

To be read with Preliminaries/ General conditions.

GENERALLY

110	NOTICE

•	 Give notice before:

-	Application of herbicide.

-	Application of fertilizer.

-	Watering.

-	Each site maintenance visit.

•	 Period of notice: 7 days.

130	REINSTATEMENT

•	 Damage or disturbance to soil structure, planting, grass, fencing, hard landscaping,

structures or buildings: Reinstate to original condition.

140	CONTROL OF MAMMALIAN PESTS

•	 Specialist firms: Submit proposals.

- Method:   Rabbit proof fence.

155	WATERING

•	 Supply: Potable mains water.

•	 Quantity: Wet full depth of topsoil .

•	 Application: Do not damage or loosen plants.

•	 Compacted soil: Loosen or scoop out, to direct water to rootzone.

•	 Frequency: As necessary for the continued thriving of all planting.

160	WATER RESTRICTIONS

•	 General: If water supply is, or is likely to be, restricted by emergency legislation, submit

proposals for an alternative suitable source of water. Obtain instructions before

proceeding.

170	DISPOSAL OF ARISINGS

•	 General: Unless specified otherwise, dispose of arisings as follows:

-	Biodegradable arisings: Remove to recycling facility.

-	Grass cuttings: Remove to recycling facility.

-	Tree roots and stumps: Remove from site.

-	Shrub and tree prunings: Remove to recycling facility.

-	Litter and non-biodegradable arisings: Remove from site.

180	CHIPPING OR SHREDDING

•	 General: Not permitted on site.

181	MECHANICAL EQUIPMENT

•	 General: Minimize.

•	 Prohibited equipment: Leaf blowers & Litter vacuums.

•	 Timing: Use of mechanical equipment allowed between the hours of 10:00 am and 4:00 pm

only.

190	LITTER

•	 Extraneous rubbish not arising from the contract work: Collect and remove from site.

195	PROTECTION OF EXISTING GRASS

•	 General: Protect areas affected by maintenance operations using boards/tarpaulins. Do not

place excavated or imported materials directly on grass.

197	CLEANLINESS

•	 Soil and arisings: Remove from hard surfaces.

•	 General: Leave the works in a clean, tidy condition at completion and after any

maintenance operations.

GRASSED AREAS

210	MAINTENANCE OF GRASSED AREAS

•	 General: Maintain turf in a manner appropriate to the intended use.

•	 Soil and grass:

-	Condition: Maintain a healthy vigorous sward, free from disease, fungal growth,

discolouration, scorch or wilt.

-	Waterlogging and compaction: Prevent.

-	Damage: Repair trampling, abrasion or scalping.

•	 Ornamental lawns: Maintain reasonably free from moss, excessive thatch, weeds, frost

heave, worm casts and mole hills.

-	Edges: Neat and well defined, in clean straight lines or smooth flowing curves.

•	 Litter and fallen leaves: Remove regularly to maintain a neat appearance.

220	GRASS CUTTING GENERALLY

•	 Before mowing: Remove litter, rubbish and debris.

•	 Finish: Neat and even, without surface rutting, compaction or damage to grass.

•	 Edges: Leave neat and well defined. Neatly trim around obstructions.

•	 Adjoining hard areas: Sweep clear and remove arisings.

•	 Drought or wet conditions: Obtain instructions.

225	TREE STEMS

•	 Precautions: Do not use mowing machinery closer than 100 mm to tree stems. Use nylon

filament rotary cutters and other hand held mechanical tools carefully to avoid damage to

bark.

240	MOWING STRIPS

•	 Location: Along the base of walls, fences and hedges.

•	 Width (approximate): 150 mm.

•	 Operations: Maintain by applying a suitable herbicide twice during the growing season.

250	LEAF REMOVAL

•	 Operations: Collect fallen leaves.

•	 Special requirements: Remove by hand raking.

•	 Disposal: Remove from site for recycling.

260	MOWING LAWNS

•	 Grass height: Maintain between 25 and 50 mm.

•	 Arisings: Remove.

295	SPIKING

•	 Location: All lawns.

•	 Timing: As necessary to relieve compaction.

•	 Operations: Aerate the soil and improve surface water penetration.

•	 Depth (minimum): Contractor's choice.

309	EDGES TO SEEDED AREAS

•	 Location: Planting beds and around newly planted trees.

•	 Timing: After seeded areas are well established.

•	 Edges: Cut to clean straight lines or smooth curves. Draw back soil to permit edging.

•	 Arisings: Remove.

310	RE-FORMING GRASS EDGES

•	 Location: Where damage occurs.

•	 Edges: Draw back soil and re-form edges to clean straight lines or smooth flowing curves,

sloping slightly back from vertical.

320	LEVELLING HOLLOWS AND BUMPS IN TURF

•	 Standard: To BS 7370-3, clauses 12.4 and 12.5.

330	SELECTIVE HERBICIDE

•	 Location: All lawns.

•	 Herbicide: Combined weed and feed mix.

•	 Areas not to be sprayed: Desirable herbaceous plantings.

340	SPOT WEEDKILLING IN ROUGH GRASS AREAS

•	 Herbicide: Suitable for suppressing perennial weeds.

•	 Operations: Spot treat injurious weed species listed in the Weeds Act 1959 and Wildlife

and Countryside Act 1981.

350	FERTILIZER - SPRING APPLICATION

•	 Type: Slow release.

•	 Application rate: Manufacturers advice.

360	FERTILIZER - AUTUMN APPLICATION

•	 Type: Slow release.

•	 Application rate: Manufacturers advice.

380	REINSTATEMENT OF DAMAGED LAWNS

•	 Damaged turf: Remove to a depth of 30 mm.

•	 Preparation: Cultivate substrate to a fine tilt.

•	 Reinstatement: Contractor's choice of returfing or topsoiling and reseeding:

-	Returfing: Quality and appearance to match existing.

-	Reseeding: Fill with fine topsoil to BS 3882 general purpose grade, free from stones,

debris and weeds. Reseed with a seed mix to match existing grass in quality and

appearance.

•	 Protection and watering: Provide as necessary to promote successful germination and/ or

establishment.

381	REINSTATEMENT OF WORN OR DAMAGED LAWNS

•	 Worn or damaged areas: Make good by returfing or reseeding:

-	Returfing standard: To BS 7370-3, Clause 12.2.

-	Reseeding standard: To BS 7370-3, Clause 12.6.

•	 Turf or seed: To match existing in appearance and quality.

•	 Protection and watering: Provide as necessary to promote successful germination and/ or

establishment.

FLOWER BEDS/ SEASONAL BEDDINGS

450	PLANTING BEDS OF ANNUALS

•	 Clearance: Remove previous season's bedding, including all bulbs, litter and debris.

•	 Preparation: Dig over beds using a spade or hand held mechanical cultivator:

-	Annual weeds: Bury.

-	Perennial weeds: Carefully dig out.

•	 Fertilizer: Either in autumn or spring spread and incorporate Organic fertilizer .

-	Application rate: As manufacturer's recommended rate.

•	 Annual bedding plants:

-	Standard: To BS 3936-7.

-	Setting out: Plant out to approved layout, including edging plants, main layer, specimen

or pot plants, corms, bulbs or tubers.

•	 Watering: Keep plants watered as necessary before planting out and water in after

planting.

•	 Failed planting: Replant as necessary any plants, or areas of plants, that have failed to

thrive.

460	BEDS OF PERENNIALS OR PERENNIALS AND ANNUALS

•	 Plant supports: Stake and tie plants using bamboo canes.

-	Length: To suit plant height.

-	Maintain throughout the growing season.

•	 Gaps in planting: Refill by replanting.

•	 Watering:

-	New plants: Before and after planting out.

-	Ongoing: As necessary for the continued thriving of all planting.

•	 Operations at end of growing season:

-	Trim: Older flowering stems of herbaceous perennials.

-	Remove: Redundant plant supports, litter, debris and arisings.

-	Cultivate: Fork over the soil, taking care not to cause undue disturbance to plants.

-	Top dress: Apply sanitized and stabilized compost top dressing.

470	FLOWER BEDS GENERALLY

•	 Operations:

-	Remove: Dead flower heads, fallen leaves, litter and debris.

-	Weeds: Thoroughly hand weed.

-	Cultivate: Lightly hoe.

-	Trim: Clip grass edges.

•	 Fungicide: Apply once during summer as instructed.

•	 Insecticide: Apply once during summer as instructed.

SHRUBS/TREES/HEDGES

500	ESTABLISHMENT OF NEW PLANTING

•	 Duration: Two full growing seasons from the date of planting.

•	 Weed control:

-	Method: Keep planting beds clear of weeds by hoeing and screening .

-	Area: Maintain a weed free area around each tree and shrub, minimum diameter the

larger of 1 m or the surface of the original planting pit.

•	 Soil condition: Fork over beds to keep soil loose, with gentle cambers and no hollows. Do

not reduce depth or effect of mulch.

•	 Trees: When in leaf, spray crowns during warm weather.

-	Timing: After dusk.

•	 Watering: When instructed.

502	ESTABLISHMENT OF NEW PLANTING - FERTILIZER

•	 Time of year: March or April.

•	 Type: Slow release.

•	 Spreading: Spread evenly. Carefully lift and replace any mulch materials.

-	Application rate: As manufacturer's recommendations.

510	TREE STAKES AND TIES

•	 Inspection/ Maintenance times: As scheduled and immediately after strong winds.

•	 Stakes:

-	Replace loose, broken or decayed stakes to original specification.

-	If longer than half of clear tree stem height, cut to this height in spring. Retie to tree firmly

but not tightly with a single tie.

•	 Ties: Adjust, refix or replace loose or defective ties, allowing for growth and to prevent

chafing.

-	Where chafing has occurred, reposition or replace ties to prevent further chafing.

•	 Removal of stakes and ties: During spring when no longer required to support the tree.

Fill stake holes with lightly compacted soil.

520	REFIRMING OF TREES AND SHRUBS

•	 Timing: After strong winds, frost heave and other disturbances.

•	 Refirming: Tread around the base until firmly bedded.

•	 Collars in soil at base of tree stems, created by tree movement: Break up by fork, avoiding

damage to roots. Backfill with topsoil and refirm.

525	TREE GUARDS

•	 Loose or defective guards: Adjust, refix or replace to original specification and to prevent

chafing.

530	TREE SHELTERS

•	 Loose or defective shelters: Adjust, refix or replace to original specification and to prevent

chafing.

•	 Removal: During spring when no longer required to protect the tree.

540	PRUNING GENERALLY

•	 Pruning: In accordance with good horticultural and arboricultural practice.

-	Removing branches: Do not damage or tear the stem or bark.

-	Wounds: Keep as small as possible and cut cleanly back to sound wood.

-	Cutting: Make cuts above and sloping away from an outward facing healthy bud, angled

so that water will not collect on cut area.

-	Larger branches: Prune neither flush nor leaving a stub, but using the branch bark ridge

or branch collar as a pruning guide.

•	 Appearance: Thin, trim and shape each specimen appropriately to species, location,

season, and stage of growth, leaving a well-balanced natural appearance.

•	 Tools: Use clean sharp secateurs, hand saws or other approved tools. Trim off ragged

edges of bark or wood with a sharp knife.

•	 Disease or infection: Give notice if detected.

•	 Growth retardants, fungicide or pruning sealant: Do not use unless instructed.

545	PRUNING OF EXCESSIVE OVERHANG

•	 Timing: Annually.

•	 Operations: Remove growth encroaching onto grassed areas, paths, roads, signs,

sightlines and road lighting luminaires.

•	 Special requirements: None.

550	PRUNING OF EXCESSIVE HEIGHT

•	 Timing: As instructed.

Operations: Remove excessive height As instructed.

555	PRUNING TREES AND SHRUBS

•	 Standard: To BS 7370-4.

•	 Special requirements: None.

570	FORMATIVE PRUNING OF YOUNG TREES

•	 Standard: Type and timing of pruning operations to suit the plant species.

•	 Time of year: Do not prune during the late winter/ early spring sap flow period.

•	 Young trees up to 4 m high:

-	Crown prune by removing dead branches and reducing selected side branches by one

third to preserve a well-balanced head and ensure the development of a single strong

leader.

-	Remove duplicated branches and potentially weak or tight forks. In each case cut back

to live wood.

•	 Whips or feathered trees: Do not prune.

•	 Operatives: Approved specialist contractor.

575	PRUNING ORNAMENTAL SHRUBS

•	 General: Prune to encourage healthy and bushy growth and desirable ornamental features,

e.g. flowers, fruit, autumn colour, stem colour.

•	 Suckers: Remove by cutting back level with the source stem or root.

580	PRUNING FLOWERING SPECIES OF SHRUBS AND ROSES

•	 Time of year:

-	Winter flowering shrubs: Spring.

-	Shrubs flowering between March and July: Immediately after the flowering period.

-	Shrubs flowering between July and October: Back to old wood in winter.

-	Rose bushes: Early spring to encourage basal growths and a balanced, compact habit.

600	TRIMMING RAPIDLY ESTABLISHING HEDGES

•	 General: Allow to reach planned height as rapidly as possible.

-	Form: Trim back lateral branches moderately.

605	TRIMMING SLOWLY ESTABLISHING HEDGES

•	 Operations:

-	Timing: Cut back hard in June and September to encourage bushy growth down to

ground level.

-	Form: Allow to reach planned dimensions only by gradual degrees, depending on growth

rate and habit.

610	TRIMMING TAPERING ESTABLISHED HEDGES

•	 Time of year: Regular trimming from June to September.

•	 Operations:

-	Form: Trim carefully and neatly to regular line and shape, with the width at the top less

than that at the base.

-	Trim: Remove current growth rather than old wood.

•	 Tools/ Cutting: Suitable mechanical cutters.

611	TRIMMING NONTAPERING ESTABLISHED HEDGES

•	 Time of year: Regular trimming from June to September.

•	 Operations:

-	Form: Trim carefully and neatly to regular line and shape with vertical sides.

-	Trim: Remove current growth rather than old wood.

•	 Tools/ Cutting: Suitable mechanical cutters.

615	TRIMMING FIELD HEDGES

•	 Operations: Trim to specified height and profile using suitable mechanical cutters.

620	REMOVAL OF DEAD PLANT MATERIAL

•	 Operations: At the end of the growing season, check all shrubs and remove all dead

foliage, dead wood, and broken or damaged branches and stems.

625	CLIMBING PLANTS

•	 Pruning: Remove excess growth, to ensure that signs, light fittings, doors and windows are

kept clear at all times.

•	 Insecure growth: Attach to supporting wires or structures using 1 mm diameter black

plastics coated steel wire.

•	 Supporting structures: Check and repair as necessary.

630	DEAD AND DISEASED PLANTS

•	 Removal: As soon as possible.

•	 Replacement: In the next suitable planting season.

635	REINSTATEMENT OF SHRUB/ HERBACEOUS AREAS

•	 Dead and damaged plants: Remove.

•	 Mulch/ matting materials:

-	Carefully move to one side and dig over the soil, leaving it fit for replanting.

•	 -  Do not disturb roots of adjacent plants.

•	 Replacement plants:

-	Use pits and plants: To original specification or to match the size of adjacent or nearby

plants of the same species, whichever is the greater.

-	Additional requirements: Submit details and cost of plants before ordering.

•	 Dressing: Slow release fertilizer:

-	Type: Contractor's choice.

-	Application rate: As manufacturer's recommendations.

645	WEED CONTROL GENERALLY

•	 Weed tolerance: At all times, weed cover less than 5% and no weed to exceed 100 mm

high.

•	 Adjacent plants, trees and grass: Do not damage.

650	HAND WEEDING

•	 General: Remove weeds entirely, including roots.

•	 Disturbance: Remove the minimum quantity of soil, and disturb plants, bulbs and mulched

surfaces as little as possible.

•	 Completion: Rake area to a neat, clean condition.

•	 Mulch: Reinstate to original depth.

657	HERBICIDE TO KILL REGROWTH

•	 Type: Suitable foliar acting herbicide to kill regrowth.

•

665	WEED CONTROL WITH WINTER HERBICIDE

•	 Type: Suitable residual soil acting herbicide.

•	 Time of year: Unless otherwise agreed, complete before end of March.

•	 Timing: Allow recommended period for herbicide to take effect before clearing dead weeds.

670	WEED CONTROL WITH SUMMER HERBICIDE

•	 Type: Suitable foliar acting herbicide.

•

680	SOIL AERATION

•	 Compacted soil surfaces:

-	Prick up: To aerate the soil of root areas and break surface crust.

-	Size of lumps: Reduce to crumb and level off.

Damage: Do not damage plants and their roots.

685	SOIL LEVEL ADJUSTMENT

•	 Level of soil/mulch at edges of beds: Reduce to 50 mm below adjacent grass or hard

surface.

Arisings (if any): Spread evenly over the bed.

700	SNOW REMOVAL FROM SHRUBS/ TREES

•	 Standard: To BS 7370-4.

•	 Plants subject to snow removal:   All evergreens.

•	 Timing: Within 24 hours of snowfall.

705	WINTER LEAF REMOVAL

•	 Operations: Take down temporary leaf fences. Collect accumulations of drifted leaves from

the vicinity and from planting beds.

•	 Arisings: Remove to recycling facility.

TREE WORK

810	TREE WORK GENERALLY

•	 Identification: Before starting work agree which trees, shrubs and hedges are to be

removed or pruned.

•	 Protection: Avoid damage to neighbouring trees, plants and property.

•	 Standards: To BS 3998 and Health & Safety Executive (HSE) 'Forestry and arboriculture

safety leaflets'.

•	 Removing branches: Cut as Arboricultural Association Leaflet 'Mature tree management'.

Cut vertical branches similarly, with no more slope on the cut surface than is necessary to

shed rainwater.

•	 Appearance: Leave trees with a well-balanced natural appearance.

•	 Chain saw work: Operatives must hold a Certificate of Competence.

•	 Tree work: To be carried out by an approved member of the Arboricultural Association.

815	ADDITIONAL WORK

•	 Defective, diseased, unsafe or weak parts of trees additional to those scheduled for

attention: Give notice if detected.

820	PREVENTION OF WOUND BLEEDING

•	 Standard: To BS 3998, clause 8.

825	PREVENTION OF DISEASE TRANSMISSION

•	 Standard: To BS 3998, clause 9 and Appendix B.

835	CUTTING AND PRUNING GENERALLY

•	 Tools: Appropriate, well maintained and sharp.

•	 Final pruning cuts:

-	Chainsaws: Do not use on branches of less than 50 mm diameter.

-	Hand saws: Form a smooth cut surface.

-	Anvil type secateurs: Do not use.

•	 Removing branches: Do not damage or tear the stem.

•	 Wounds: Keep as small as possible, cut cleanly back to sound wood leaving a smooth

surface, and angled so that water will not collect on the cut area.

•	 Cutting: Cut at a fork or at the main stem to avoid stumps wherever possible.

Large branches: Remove only with prior approval.

-	Remove in small sections and lower to ground with ropes and slings.

•	 Dead branches and stubs: When removing, do not cut into live wood.

•	 Unsafe branches: Remove epicormic shoots and potentially weak forks that could fail in

adverse weather conditions.

•	 Disease or fungus: Give notice if detected. Do not apply fungicide or sealant unless

instructed.

855	CUTTING TREE ROOTS

•	 Excavating: Use hand tools only.

•	 Protected area: Do not cut roots within an area which is the larger of:

-	The branch spread of the tree.

-	An area with a Fold of half the tree's height, measured from the trunk.

•	 Outside protected area: Give notice of roots exceeding 50 mm in diameter. Do not cut

without approval.

•	 Cutting:

-	Cutting: Make clean smooth cuts with a hand saw.

-	Wounds: Minimize. Avoid ragged edges.

-	Finishing: Pare cut surfaces smooth with a sharp knife.

•	 Backfilling:

-	Protection: Cover cut roots with clean sharp sand.

-	Material: Backfill with original topsoil.

860	REMOVING TREES, SHRUBS AND HEDGES

•	 Standards: To BS 3998, Appendix A and Health & Safety Executive (HSE)/ Arboricultural

and Forestry Advisory Group Safety Leaflets.

•	 Existing services: Check for below and above ground services. Give notice if they may be

affected.

•	 Shrubs and smaller trees: Cut down and grub up roots.

•	 Tree stumps:

-	Removal: Remove mechanically to a minimum depth of 300 mm below ground level.

-	Removal by winching: Give notice. Do not use other trees as supports or anchors.

•	 Protection: Avoid damage to neighbouring trees, plants and property.

•	 Work near retained trees: Where tree canopies overlap and in confined spaces generally,

take down trees carefully in small sections to avoid damage to adjacent trees that are to be

retained.

•	 Filling holes:

-	Material: Use as-dug material and/ or imported soil as required.

Finishing: Consolidate and grade to marry in with surrounding ground level.

865	BARK DAMAGE

•	 Wounds:

-	Do not attempt to stop sap bleeding.

-	Bark: Remove ragged edges using a sharp knife.

-	Wood: Remove splintered wood from deep wounds.

-	Size: Keep wounds as small as possible.

•	 Liquid or flux oozing from apparently healthy bark: Give notice.

870	CAVITIES IN TREES

•	 Investigation: Remove rubbish and rotten wood. Probe the cavity to find the extent of any

decay, and give notice.

•	 Water filled cavities: Do not drain.

•	 Sound wood inside cavities: Do not remove.

•	 Cavity openings: Cover, as scheduled, with galvanized wire mesh, lightly secured.

HARD LANDSCAPE AREAS/FENCING

900	SNOW CLEARANCE

•	 Clearance: On reaching a depth of 5 mm.

•	 De-icing: To footpaths and car park.

-	Material: Rock salt to BS 3247.

-	Timing: When freezing precipitation is forecast.

-	Application rate: Spread evenly at a rate of As manufacturer's recommendations.

910	HARD SURFACES AND GRAVEL AREAS

•	 Herbicide: Apply a suitable foliar acting or residual herbicide. Allow recommended period

for herbicide to take effect before clearing arisings.

•	 Hard surfaces: Remove litter, leaves and other debris.

•	 Surface gutters and channels: Remove mud, silt and debris.

•	 Drainage gullies: Empty traps and flush clean.

•	 Gravel areas: Rake over. Remove weeds, litter, leaves and debris, and level off.

•	 Repairs to flexible bituminous pavings: In accordance with the original paving specification

or BS 7370-2, clause 4.12.

•	 Stain removal: In accordance with BS 7370-2, table 4.

915	PAVING SEALANT

•	 Type: Polyurethane.

•	 Manufacturer: Contractor's choice.

-	Product reference: Contractor's choice.

•	 Application method: As manufacturer's recommendations.

-	Coats: As manufacturer's recommendations.

-	Coverage: As manufacturer's recommendations.

920	FENCING

•	 Fences: Inspect and repair to maintain protection against intruders.

930	GRAFFITI REMOVAL

•	 Method: Chemical poultice.

•	 Subsequent treatment: Not required.

-	Finish: -.

Q40

Fencing

Q40 Fencing

To be read with Preliminaries/ General conditions.

FENCING SYSTEMS

125A	OPEN MESH STEEL PANEL GENERAL PURPOSE FENCING PALADIN TYPE FENCING

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Proprietary fencing panel and post system of contractor's choice with

4no reinforcing beams per panel, provide sample for CA approval.

•	 Standard: To BS 1722-14, category 1.

•	 Height: 2100 mm.

•	 Mesh and wire: Galvanised and polyester powder coated galvanised steel expanded metal

mesh, 200mm vertical x 25mm horizontal x 6mm diameter horizontal wire, 5mm diameter

vertical wire.  Vertical wire to protrude 22mm above top horizontal wire. Panel fixed to posts

with proprietary slotted crap bars with tamper-resistant bolt and threaded nutserts.

•	 Posts: Polyester powder coated galvanised steel rectangular hollow section.  Min

60x60mm intermediate posts with resistance to bending of 8.30cm3.

•	 Maximum centres of posts: 2950mm.

•	 Method of setting posts: 300 mm square x 700 mm deep holes completely filled with 20N

concrete.

•	 Bottom of fencing: Anchored to a concrete sill.

•	 Accessories: Matching compatible pedestrian gates as necessary as indicated. Minimum

pedestrian gate leaf width to be 1000mm and gates to be complete with drop bolts and

suitable slide bolt locking complete with waterproof padlock and 3 keys.  Provide suitable

steel / concrete locking receptors in surrounding ground finish.

•	 Conformity: Submit manufacturer's and installer's certificates, to BS 1722-14, clause 9.

•	 Finishing: Galvanised to BS EN ISO 1461 & Powder coating to BS EN 13438.  Colour to be

chosen by CA / Client.

•	 Fixings: Coated tamper-resistant bolts and hexagonal anti-rotational threaded nutserts in

accordance with manufacturer's instructions.  Minimum 5no to each side of panels.

140A	GENERAL PATTERN WIRE MESH FENCING Metal Forest Stock Fencing Generally

(temporary exclusion zones)

•	 Standard: To BS 1722-2.

•	 Height: 1000 mm, to be 300m from ground level to allow badger(s) / protected species to

walk under.

•	 Mesh: Rectangular with 150mm wide wire spacing, 1M C7/10/15 to BS EN 10223-5.

•	 Posts and struts: Contractor's choice  - Square/Round sawn wood.

-	Treatment: Galfan coated to provide a minimum 10 year service life.

•	 Maximum centres of posts:

-	Straining posts: 12 m in straight runs and at all ends, corners, changes of direction and

acute variations in level.

-	Intermediate posts: 3.0 m.

•	 Method of setting posts and struts:

-	Straining posts: 400 mm square or 300 mm diameter holes, driven into ground where

possible otherwise with 600 mm deep filled to two thirds depth with concrete.

-	Struts: 300 x 450 mm holes, 450 mm deep filled to not less than half the depth with

concrete.

-	Intermediate posts: Driven to a minimum depth of 600 mm.

•	 Accessories: Fix notices 1.0 m from ground, every 15m and high visibility rope / tape

marking as necessary.

310A	DOUBLE SIDED CLOSE BOARDED FENCING, CONCRETE POSTS AND GATES

1800MM HIGH refer to architects drawing

•	 Standard: To BS 1722-5, type BW 180A.

•	 Height: 1800 mm between properties and to the rear of properties.

•	 Wood: Treated S/W (European and English).

-	Treatment: Preservative treated To provide a 15 year service life.

•	 Boards/ rails: Double rail and double Softwood feather edged boards at least 25mm thick

by 144mm wide on rectangular rails.

•	 Posts: Concrete.

•	 Centres of posts (maximum): 2m centres unless otherwise advised by structural engineer.

•	 Method of setting posts: 300 mm square or round holes, 600 mm deep filled to not less

than half the depth with concrete .

•	 Accessories: Gates should be the same height as the adjoining fence and must provide a

clear opening width of at least 1000mm. Gates should be constructed of the same height

boards as fence, securely fixed to 100mm x 33mm pre-treated timber framing. 3 no. Bat

and band hinges must be used.

All foundations to structural engineers recommendations.

All bolts which used to fixed the d rail to the conc. posts are to be cut back to the bolt and

sharp edges removed.

310B	SINGLE SIDED CLOSE BOARDED FENCING, CONCRETE POSTS AND GATES

1800MM HIGH refer to architects drawing

Standard: To BS 1722-5, type  [BW 180A].

Height:  [1800 mm between properties and to the rear of properties].

Wood:  [Treated S/W (European and English)].

-	Treatment: Preservative treated  [To provide a 15 year service life].

Boards/ rails:  [Softwood feather edged boards at least 25mm thick by 144mm wide on

rectangular rails].

Posts:  [Concrete].

Centres of posts (maximum): 2m centres unless otherwise advised by structural

engineer.

Method of setting posts:  [300 mm square or round holes, 600 mm deep filled to not less

than half the depth with concrete ].

Accessories: Gates should be the same height as the adjoining fence and must provide

a clear opening width of at least 1000mm. Gates should be constructed of the same

height boards as fence, securely fixed to 100mm x 33mm pre-treated timber framing. 3

no. Bat and band hinges must be used.

All foundations to structural engineers recommendations.

All bolts which used to fixed the d rail to the conc. posts are to be cut back to the bolt

and sharp edges removed.

340B	MILD STEEL VERTICAL RAILINGS, POSTS, STILES AND GATES CONTRACTORS

DESIGNED (STAND ALONE AND/OR WITH BRICK WALL BELOW AND/OR WITH

RETAINING STRUCTURE BELOW)  refer to architects and engineers drawings

•	 Standard: To BS 1722-9.

•	 Height: Varies as indicated - 600mm, 1200mm & 1800mm.

Horizontal rails: Top & Bottom - min.40 x 8mm

•	 Vertical infill bars: Min 25x25mm bar. Bow top to gates as indicated.

•	 Centres of verticals: 100 mm.

•	 Frame Posts & Rails: RHS, min. 100 x 100 x 4 mm.

•	 Treatment: Hot dip galvanized to BS EN ISO 1461.

•	 Centres of posts (maximum): 2.8 m.

•	 Method of setting posts/ stays/ legs: Posts embedded in accordance with designers

requirements - minimum 450 mm with minimum 100 mm concrete cover, intermediate

supports in rammed earth.  Contractor is responsible for coordination to ensure

compatibility between railing proposals and retaining wall support / construction.

•	 Accessories: Double leaf & single leaf pedestrian gates as indicated. Refer to site plan for

locations.  All with slide bolts, drop bolts, adjustable hinges, and supports as necessary.

Minimum pedestrian gate leaf width to be 900mm and gates to be complete with drop bolts

and suitable slide bolt locking complete with waterproof padlock and 3 keys.  Provide

suitable steel / concrete locking receptors in surrounding ground finish.

•	 Other Requirements: Gates to be remote electrically operated as indicated - refer to

Electrically Operated Fence & Gate Assembly Detail.

Steel driveway gates should not be fixed directly onto brick pillar or fence, but rather onto

steel gateposts that must be concreted into the ground. All gates must match height of

adjacent fencing.

Welding to be carried out on the top surface of any exposed elements to ensure no areas

exist for water to pond / lie in.

Contractor to provide samples, detailed fixing specification details, insurances and

warranties for inspection / CA approval in good timing prior to full manufacture and

installation.

ACCESSORIES

EXECUTION

710	INSTALLATION GENERALLY

•	 Set out and erect:

-	Alignment: Straight lines or smoothly flowing curves.

-	Tops of posts: Following profile of the ground.

-	Setting posts: Rigid, plumb and to specified depth, or greater where necessary to ensure

adequate support.

-	Fixings: All components securely fixed.

715	COMPETENCE

•	 Operatives: Contractors must employ competent operatives.

•	 Qualifications: Submit certification of training.

-	Sector Scheme: 2A.

Categories: -.

720	SETTING POSTS IN CONCRETE

•	 Standard: To BS 8500-2.

•	 Mix: Designated concrete not less than GEN1 or Standard prescribed concrete not less

than ST2.

•	 Alternative mix for small quantities: 50 kg Portland cement to 150 kg fine aggregate to 250

kg 20 mm nominal maximum size coarse aggregate, medium workability.

•	 Admixtures: Do not use.

•	 Holes: Excavate neatly and with vertical sides.

•	 Filling: Position post/ strut and fill hole with concrete to not less than the specified depth,

well rammed as filling proceeds and consolidated.

•	 Backfilling of holes not completely filled with concrete: Excavated material, well rammed

and consolidated.

730	EXPOSED CONCRETE FOUNDATIONS

•	 Filling: Compact until air bubbles cease to appear on the upper surface.

•	 Finishing: Weathered to shed water and trowelled smooth.

740	SETTING POSTS IN EARTH

•	 Holes: Excavated neatly, with vertical sides and as small as practicable to allow refilling.

•	 Filling: Position posts/ struts and replace excavated material, well rammed as filling

proceeds.

750	DRIVEN POSTS

•	 Damage to heads: Minimize.

-	Repair: Neatly finish post tops after installation.

760	NAILED WOOD RAILS

•	 Length (minimum): Two bays, with joints in adjacent rails staggered.

•	 Fixing: Nail each length of rail to each post with two 100 mm galvanized nails.

•	 Rails with split ends: Replace.

765	CLEFT WOOD RAILS

•	 Length (maximum): 3.05 m.

•	 Fixing: Rail end section shaped to adequately fill the post mortice. Nail each rail to each

prick post with two galvanized nails.

•	 Rails with split ends: Replace.

766	ARRIS RAILS

•	 Fixing:

-	Rail end section: Shaped to adequately fill the post mortice or recess.

-	Recessed posts: Rails bolted to each post.

-	Top rails: Fixed at both ends using One 8 mm diameter bolt .

•	 Rails with split ends: Replace.

770	SITE CUTTING OF WOOD

•	 General: Kept to a minimum.

•	 Below or near ground level: Cutting prohibited.

•	 Treatment of surfaces exposed by minor cutting and drilling: Two flood coats of solution

recommended for the purpose by main treatment solution manufacturer.

780	DAMAGE TO GALVANIZED SURFACES

•	 Treatment of minor damage (including on fasteners and fittings): Low melting point zinc

alloy repair rods or powders made for this purpose, or at least two coats of zinc-rich paint

to BS 4652.

•	 Thickness: Apply sufficient material to provide a zinc coating at least equal in thickness to

the original layer.

790	SITE PAINTING

•	 Timing: Prepare surfaces and apply finishes as soon as possible after fixing.

COMPLETION

910	CLEANING

•	 General: Leave the works in a clean, tidy condition.

•	 Surfaces: Clean immediately before handover.

920	FIXINGS

•	 All components: Tighten.

-	Timing: Before handover.

930	GATES

•	 Hinges, latches and closers: Adjust to provide smooth operation. Lubricate where

necessary.

Timing: Before handover.

Q50

Site/ street furniture/ equipment

Q50 Site/ street furniture/ equipment

To be read with Preliminaries/ General conditions.

GATES, BARRIERS AND PARKING CONTROLS

190	BOLLARDSFOR TRAFFIC CONTROL TO KERB EDGE

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Material: Steel.

-	Finish: Polyester powder coated as section Z31.

-	Colour: To BS 4800, & to be confirmed.

•	 Height above ground: 450 mm.

•	 Special features: White reflective band.

•	 Method of fixing: Base plate bolted to 400 x 400 x 400 mm concrete base 100 mm below

paving surface.

SITE AND STREET FURNITURE

242	BINS	PROPRIETARY 'WHEELIE' TYPE 240 LITRE BIN - 3no. PER HOUSE &

APARTMENT

•	 Manufacturer: Contractor's choice.

-	Product reference: Submit proposals.

•	 Material: Plastics.

-	Finish: As manufactured.

-	Colour: 1no. GREY/BLACK (general household), 1no. BLUE (recycling), 1no. BROWN

(green waste) - all in accordance with Code for Sustainable Homes.  Alternate colours

may be required by Local Authority - Contractor to confirm with Local Authority

Environmental Health / Building Control Services.

•	 Accessories/ Special requirements: Hinged lid.

•	 Method of fixing: No fixed.

330A	EXTERNAL ROTARY CLOTHES DRIER PROPRIETARY STEEL UMBRELLA TYPE TO

ALL PROPERTIES

•	 Manufacturer: Contractor's Choice, provide sample for CA approval. Provide 5year

manufacturer’s warranty.

-	Material:  [Robust coated steel.  Plastic coated, non-slip profile, line in one continuous

piece].

Size: minimum 50 m drying length.

-	Arms: 4.

•	 Requirements:  [Adjustable Umbrella type system - washing lines can be tensioned in three

positions. Circular pole to be height adjustable.  Arms to be rectangular and hollow in

section (channel type arms are not acceptable)].

•	 Method of fixing: Suitable galvanized steel socket grommet with integral plastic cap for

future drier removal in concrete base to fit rotary dryer in accordance with manufacturers

instructions..

INSTALLATION

510	CONCRETE FOUNDATIONS GENERALLY

•	 Standard: To BS 8500-2.

•	 Mix: Designated concrete not less than GEN 1 or standard prescribed concrete not less

than ST2.

•	 Admixtures: Do not use.

•	 Foundation holes: Neat vertical sides.

•	 Depth of foundations, bedding, haunching: Appropriate to provide adequate support and to

receive overlying soft landscape or paving finishes.

515	SETTING COMPONENTS IN CONCRETE

•	 Holes: 250 x 250 x minimum 300 mm deep.

•	 Components: Accurately positioned and securely supported.

•	 Concrete fill: Fully compacted as filling proceeds.

•	 Concrete foundations exposed to view: Compacted until air bubbles cease to appear on

the upper surface, then weathered to shed water and trowelled smooth.

•	 Temporary component support: Maintain undisturbed for minimum 48 hours.

530	PRESERVATIVE TREATED TIMBER

•	 Surfaces exposed by minor cutting and drilling: Treated by immersion or with two flood

coats of a solution recommended for the purpose by main treatment solution manufacturer.

•	 Heavily worked sections: Re-treat.

540	BUILDING IN TO MASONRY WALLS

•	 Components being built in: Accurately positioned and securely supported. Set in mortar

and pointed neatly to match adjacent walling.

•	 Temporary support: Maintain for 48 hours (minimum) and prevent disturbance.

545	ERECTION OF TIMBER AND PREFABRICATED STRUCTURES

•	 Checking: 5 days (minimum) before proposed erection date, check foundations, holding

down bolts, etc.

•	 Inaccuracies or defects in prepared bases or supplied structures: Report immediately.

Obtain instructions before proceeding.

550	DAMAGE TO GALVANIZED SURFACES

•	 Minor damage in areas up to 40 mm² (including on fixings and fittings): Make good.

-	Material: Low melting point zinc alloy repair rods or powders made for this purpose or at

least two coats of zinc-rich paint to BS 4652.

-	Thickness: Sufficient to provide a zinc coating at least equal to the original layer.

560	SITE PAINTING

•	 Timing: Prepare surfaces and apply finishes as soon as possible after fixing.

R

Disposal systems

R10

Rainwater drainage systems

R10 Rainwater drainage systems

To be read with Preliminaries/ General conditions.

GENERAL

SYSTEM PERFORMANCE

210	DESIGN

•	 Design: Complete the design of the rainwater drainage system.

•	 Standard: To BS EN 12056-3, clauses 3-7 and National Annexes.

•	 Proposals: Submit drawings, technical information, calculations and manufacturers'

literature.

221	COLLECTION AND DISTRIBUTION OF RAINWATER

•	 General: Complete, and without leakage or noise nuisance.

230	DESIGN PARAMETERS - GENERAL

•	 Roof and gutter construction and finish: Seamless.

•	 Design rate of rainfall: As BS EN 12056-3, National Annex NB.2.

-	Category: Check with the drainage authority.

•	 Design life of building: 60 years.

•	 Available capacity of existing below ground drainage (maximum): Check with the drainage

authority.

PRODUCTS

350B	PVC-U GUTTERS SQUARELINE GENRALLY

•	 Standard: To the relevant parts of BS 4576-1, BS EN 607 and BS EN 1462, Kitemark

certified.

•	 Manufacturer: Contractor's choice  to PIFA Standard 6/83A or Agrément certified. Provide

sample for CA approval.

Profile: Box.

•	 Nominal size: 114x62mm.

•	 Colour: Black.

•	 Brackets: PVC-U.

-	Fixings: Stainless steel screws.

Size: To suite.

•	 Accessories: Leaf guards.

426A	PVC-U PIPEWORK - SEALED SQUARE GENRALLY

•	 Standard: To BS EN 1329-1 or BS 4514, Kitemark certified.

•	 Manufacturer: Contractor's choice  to PIFA Standard 6/83A or Agrément certified. Provide

sample for CA approval.

Nominal size: Squareline / box section min. 65x65mm.

•	 Colour: Black.

•	 Brackets: PVC-U clips, black.

-	Fixings: Stainless steel screws.

Size: 40 x 5 mm.

•	 Accessories: Leaf guards.

470A	THRESHOLD DRAINAGE CHANNELS GENERALLY

•	 Manufacturer: Contractor's choice, provide sample for CA approval.

•	 Product reference: Proprietary 3rd Party accredited polypropylene offset brick slot drain

complete with channel, cover, leave/debris guard, corner units, end caps, required outlets

and connectors, sump units and full accessory bag as recommended by the manufacturer.

•	 Requirements: Discreet inlet slot (min. 10mm) tapered to prevent blockage. Integral debris

guard to stop the ingress of sand and cement between units during installation. To be

suitable for wide range of domestic and light traffic applications and CE marked and fully

certified to Load Class A15 BS EN 1433:2002.

Installation: To be connected to storm drainage system as detailed and fitted strictly in

accordance with the manufacturers recommendations.

EXECUTION

600	PREPARATION

•	 Work to be completed before commencing work specified in this section:

-	Below ground drainage. Alternatively, make temporary arrangements for dispersal of

rainwater without damage or disfigurement of the building fabric and surroundings.

Painting of surfaces which will be concealed or inaccessible.

605	INSTALLATION GENERALLY

•	 Electrolytic corrosion: Avoid contact between dissimilar metals where corrosion may occur.

•	 Plastics and galvanized steel pipes: Do not bend.

•	 Allowance for thermal and building movement: Provide and maintain clearance as fixing

and jointing proceeds.

•	 Protection:

-	Fit purpose made temporary caps to prevent ingress of debris.

-	Fit access covers, cleaning eyes and blanking plates as the work proceeds.

610	FIXING AND JOINTING GUTTERS

•	 Joints: Watertight.

•	 Brackets: Securely fixed.

-	Fixings: Screwed into softwood fascia board.

Fixing centres: 900 mm.

-	Additional brackets: Where necessary to maintain support and stability, provide at joints

in gutters and near angles and outlets.

•	 Roofing underlay: Dressed into gutter.

615	SETTING OUT EAVES GUTTERS - TO FALLS

•	 Setting out: To true line and even gradient to prevent ponding or backfall. Position high

points of gutters as close as practical to the roof and low points not more than 50 mm

below the roof.

•	 Outlets: Align with connections to below ground drainage.

616	SETTING OUT EAVES GUTTERS - LEVEL

•	 Setting out: Level and as close as practical to the roof.

•	 Outlets: Aligned with connections to below ground drainage.

635	FIXING PIPEWORK

•	 Pipework: Fix securely, plumb and/ or true to line.

•	 Branches and low gradient sections: Fix with uniform and adequate falls to drain efficiently.

•	 Externally socketed pipes and fittings: Fix with sockets facing upstream.

•	 Additional supports: Provide as necessary to support junctions and changes in direction.

•	 Vertical pipes:

-	Provide a loadbearing support at least at every storey level.

-	Tighten fixings as work proceeds so that every storey is self-supporting.

-	Wedge joints in unsealed metal pipes to prevent rattling.

•	 Wall and floor penetrations: Isolate pipework from structure.

-	Pipe sleeves: As section P31.

-	Masking plates: Fix at penetrations if visible in the finished work.

•	 Expansion joint pipe sockets: Fix rigidly to buildings. Elsewhere, provide brackets and

fixings that allow pipes to slide.

640	FIXING VERTICAL PIPEWORK

•	 Bracket fixings: Plugged and screwed into masonry.

•	 Distance between bracket fixing centres (maximum): 800 for uPVC & 1500 for metals.

645	FIXING LOW GRADIENT PIPEWORK

•	 Bracket fixings: Plugged and screwed into masonry.

•	 Distance between bracket fixing centres (maximum): 800 for uPVC & 1500 for metals.

650	JOINTING PIPEWORK AND GUTTERS

•	 General: Joint with materials and fittings that will make effective and durable connections.

•	 Jointing differing pipework and gutter systems: Use adaptors intended for the purpose.

•	 Cut ends of pipes and gutters: Clean and square. Remove burrs and swarf. Chamfer pipe

ends before inserting into ring seal sockets.

•	 Jointing or mating surfaces: Clean and, where necessary, lubricate immediately before

assembly.

•	 Junctions: Form with fittings intended for the purpose.

•	 Jointing material: Strike off flush. Do not allow it to project into bore of pipes and fittings.

•	 Surplus flux, solvent jointing materials and cement: Remove.

675	CUTTING COATED PIPEWORK AND GUTTERS

•	 Cutting: Recoat bare metal.

690	ELECTRICAL CONTINUITY - PIPEWORK

•	 Joints in metal pipes with flexible couplings: Clips (or suitable standard pipe couplings)

supplied for earth bonding by pipework manufacturer to ensure electrical continuity.

695	ELECTRICAL CONTINUITY - GUTTERS

•	 Joints in metal gutters: Purpose made links supplied by the gutter manufacturer to ensure

electrical continuity.

700	ACCESS FOR TESTING AND MAINTENANCE

•	 General: Install pipework and gutters with adequate clearance to permit testing, cleaning

and maintenance, including painting where necessary.

•	 Access fittings and rodding eyes: Position so that they are not obstructed.

COMPLETION

905	INTERNAL PIPEWORK TEST - ENGLAND, WALES, IRELAND AND NORTHERN

IRELAND

•	 Preparation: Temporarily seal open ends of pipework with plugs.

•	 Test apparatus: Connect a 'U' tube water gauge and air pump to pipework via a plug.

•	 Testing: Pump air into pipework until gauge registers 38 mm.

•	 Required performance:

-	Allow a period for temperature stabilization, after which the pressure of 38 mm is to be

maintained without loss for at least 3 minutes.

910	GUTTER TEST

•	 Preparation: Temporarily block all outlets.

•	 Testing: Fill gutters to overflow level and after 5 minutes closely inspect for leakage.

915	MAINTENANCE INSTRUCTIONS

•	 General: At completion, submit printed instructions recommending procedures for

maintenance of the rainwater installation, including full details of recommended inspection,

cleaning and repair procedures.

920	IMMEDIATELY BEFORE HANDOVER

•	 Construction rubbish, debris, sward, temporary caps and fine dust which may enter the

rainwater system: Remove. Do not sweep or flush into the rainwater system.

•	 Access covers, rodding eyes, outlet gratings and the like: Secure complete with fixings.

R11

Above ground foul drainage systems

R11 Above ground foul drainage systems

To be read with Preliminaries/ General conditions.

GENERAL

115	ABOVE GROUND FOUL DRAINAGE SYSTEM

•	 Sanitary and floor drainage outlets: Sanitary fittings as MECHANICAL ENGINEERS

SPECIFICATION.

•	 Waste pipework: MUPVC or PVC-U.

•	 Discharge stack and branch pipework: M&E to confirm. Refer to Mechanical and Electrical

Engineers drawings and specifications.

•	 Separate ventilating pipework: PVC-U .

•	 Accessories: Air admittance valves & rodding eyes.

•	 Disposal: To below ground drainage as section R12.

SYSTEM PERFORMANCE

210	DESIGN

•	 Design: Complete the design of the above ground foul drainage system.

•	 Standards: To BS EN 12056-1 and BS EN 12056-2, and in accordance with BS EN 12056-

2 National Annexes NA-NG.

-	System type to BS EN 12056-2: System III.

•	 Proposals: Submit drawings, technical information, calculations and manufacturers'

literature.

220	COLLECTION AND DISTRIBUTION OF FOUL WATER

•	 General: Quick, quiet and complete, self-cleansing in normal use, without blockage,

crossflow, backfall, leakage, odours, noise nuisance or risk to health.

•	 Pressure fluctuations in pipework (maximum): ±38 mm water gauge.

•	 Water seal retained in traps (minimum): 25 mm.

PRODUCTS

315A	FLOOR DRAINSTO LEVEL ACCESS ENTRANCE DOORS (FRONT AND REAR) AND

TO HARD STANDINGS AND DEDICATED AREAS. REFER TO CIVIL ENGINEERS

DRAWINGS

•	 Floor construction: Tarmac/concrete landing.

•	 Manufacturer: Contractor's choice, provide sample for CA approval.

-	Product reference: Proprietary trapped linear percolating drainage channel consisting of

shallow form perforated channel sections, slotted gratings complete with end stops and

outlets.

•	 Body type: Channel. FACTA Load Class A.

-	Material: Stainless steel grade 304.

•	 Grating/ cover:

-	Type: Flat, slotted.

-	Material: Stainless steel grade 304, proprietary screw fixed in accordance with

manufacturer's instructions.

•	 Outlet: Type and direction to suit pipework.

•	 Accessories: All components and connections as necessary.

345	HDPE PIPEWORKFOR WASTES

•	 Standard: To BS EN 1519-1.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Sizes: DN 32 and DN 40.

•	 Brackets: HDPE pipe clips, black.

-	Fixings: Stainless steel screws.

Size: 40 x 4 mm.

•	 Accessories: Access fittings.

365	PVC-U PIPEWORK- FOR SOIL PIPES

•	 Standard: To BS EN 1329-1, Kitemark certified.

-	Weather resistance, connectors to WC pans, opening dimensions of access fittings,

design of swept fittings, stand off dimensions of pipe and fitting brackets and

requirements for adaptors and plugs: To BS 4514.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Nominal size: DN 110.

•	 Colour: Black/Gray.

•	 Brackets: Plastics pipe clips, colour to match pipes.

-	Fixings: Stainless steel screws.

Size: 40 x 4 mm.

•	 Accessories: Access fittings.

370	STAINLESS STEEL PIPEWORKFOR WASTES

•	 Standards: BS EN 1124-1 and -3.

•	 Grade: 1.4301 (304) to BS EN 10088-1.

•	 Jointing: Push fit with elastomeric joint rings to BS 7874 and BS EN 681-1.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Nominal sizes: DN 110.

•	 Brackets: Stainless steel with rosette and spacer.

-	Fixings: Stainless steel screws.

Size: 40 x 4 mm.

•	 Accessories: Access fittings.

375	AIR ADMITTANCE VALVES

•	 Standard: To BS EN 12380  or Agrément certified.

•	 Minimum air flow rate: To BS EN 12056-2.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

390	RODDING EYESINTERNALLY

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Body material: To match pipe.

•	 Cover type: Flush.

•	 Cover material: To match pipe.

EXECUTION

601	INSTALLATION GENERALLY

•	 Standard: To BS EN 12056-5.

•	 Components: From the same manufacturer for each type of pipework.

•	 Electrolytic corrosion: Avoid contact between dissimilar metals where corrosion may occur.

•	 Plastics and galvanized steel pipes: Do not bend.

•	 Allowance for thermal and building movement: Provide and maintain clearance as fixing

and jointing proceeds.

•	 Concealed or inaccessible surfaces: Decorate before starting work specified in this section.

•	 Protection:

-	Purpose made temporary caps: Fit to prevent ingress of debris.

Access covers, cleaning eyes and blanking plates: Fit as the work proceeds

605	PIPE ROUTES

•	 General: The shortest practical, with as few bends as possible.

-	Bends in wet portion of soil stacks: Not permitted.

Routes not shown on drawings: Submit proposals before commencing work.

610	FIXING PIPEWORK

•	 Pipework: Fix securely plumb and/ or true to line. Fix discharge stack pipes at or close

below socket collar or coupling.

•	 Branches and low gradient sections: Fix with uniform and adequate falls to drain efficiently.

•	 Externally socketed pipes and fittings: Fix with sockets facing upstream.

•	 Additional supports: Provide as necessary to support junctions and changes in direction.

•	 Vertical pipes: Provide a load bearing support not less than every storey level. Tighten

fixings as work proceeds so that every storey is self-supporting.

•	 Wall and floor penetrations: Isolate pipework from structure, e.g. with pipe sleeves.

-	Masking plates: Fix at penetrations if visible in the finished work.

•	 Expansion joint sockets: Fix rigidly to the building.

•	 Fixings: Allow the pipe to slide.

625	JOINTING FLOOR CHANNELS

•	 Jointing: Silicone sealant.

630	JOINTING PIPEWORK - GENERALLY

•	 General: Joint with materials, fittings and techniques that will make effective and durable

connections.

•	 Jointing differing pipework systems: With adaptors intended for the purpose.

•	 Cut ends of pipes: Clean and square. Remove burrs and swarf. Chamfer pipe ends before

inserting into ring seal sockets.

•	 Jointing or mating surfaces: Clean and, where necessary, lubricate immediately before

assembly.

•	 Junctions: Form with fittings intended for the purpose.

•	 Jointing material: Do not allow it to project into bore of pipes and fittings.

•	 Surplus flux, solvent jointing materials and cement: Remove from joints.

650	JOINTING PIPEWORK - COPPER

•	 Jointing: Integral lead free solder ring capillary fittings:

-	Standard: To BS EN 1254-1, Kitemark certified.

•	 Connections to appliances and equipment:

-	Compression fittings: To BS EN 1254-2, Kitemark certified.

Fittings with threaded ends: To BS EN 1254-4, Kitemark certified.

655	JOINTING PIPEWORK - HDPE AND POLYPROPYLENE

•	 Jointing: Compression fittings.

660	JOINTING PIPEWORK - ABS, MUPVC, PVC-C AND PVC-U

•	 Jointing: Solvent welded with lubricated ring seal joints at maximum 1800 mm spacing.

665	JOINTING TO COPPER PREFABRICATED PIPEWORK ASSEMBLIES

•	 Jointing on site: Bolted mechanical joints with synthetic rubber gaskets.

-	Expansion joints (minimum provision): At every floor level.

Waste pipes: Connect with compression fittings.

675	COATED PIPES

•	 Cutting: Recoat bare metal.

680	ELECTRICAL CONTINUITY

•	 Joints in metal pipes with flexible couplings: Make with clips (or suitable standard pipe

couplings) supplied for earth bonding by pipework manufacturer to ensure electrical

continuity.

685	IDENTIFICATION OF INTERNAL FOUL DRAINAGE PIPEWORK

•	 Markings: To BS 1710.

-	Type: Black, with arrows to indicate direction of flow.

-	Wording: White lettering 'FOUL DRAINAGE' on a black background.

•	 Type: Integral lettering on pipe wall, self-adhesive bands or identification clips.

•	 Locations: At 500 mm centres, junctions and both sides of slabs, valves, appliances,

bulkheads and wall penetrations.

695	DISCHARGE AND VENTILATING STACKS

•	 Terminations: Perforated cover or cage that does not restrict airflow.

-	Material: Plastics, as discharge stack.

700	INSTALLING AIR ADMITTANCE VALVES

•	 Position: Vertical, above flood level of highest appliance served and clear of insulation

materials (other than the manufacturer's insulating cover).

•	 Connection to discharge stack: Allow removal for rodding, e.g. ring seal.

•	 Roof spaces and other unheated locations: Fit manufacturer's insulating cover.

705	ACCESS FOR TESTING AND MAINTENANCE

•	 General: Install pipework with adequate clearance to permit testing, cleaning and

maintenance, including painting where necessary.

•	 Access fittings and rodding eyes: Position to avoid obstruction.

COMPLETION

900	TESTING GENERALLY

•	 Dates for testing: Give notice.

-	Period of notice (minimum): 5 working days.

•	 Preparation:

-	Pipework: Securely fixed and free from obstruction and debris.

-	Traps: Filled with clean water.

•	 Testing:

-	Supply clean water, assistance and apparatus.

-	Do not use smoke to trace leaks.

•	 Records: Submit a record of tests.

905	PIPEWORK AIRTIGHTNESS TEST

•	 Preparation:

-	Open ends of pipework: Temporarily seal using plugs.

-	Test apparatus: Connect a 'U' tube water gauge and air pump to pipework via a plug or

through trap of an appliance.

•	 Testing: Pump air into pipework until gauge registers 38 mm.

•	 Required performance: Pressure of 38 mm is to be maintained without loss for at least

three minutes.

910	SIPHONAGE AND BACK PRESSURE TESTS

•	 Method:

-	WC pans: Test by flushing.

-	Other appliances: Test by filling to overflow level, then removing the plug.

•	 Number of tests: Test each appliance three times. Recharge traps before each test.

•	 Self siphonage testing: Test each appliance individually.

•	 Induced siphonage and back pressure testing: Test by discharging the following numbers

of appliances simultaneously on each stack:

-	WCs: 1.

-	Washbasins: 1.

-	Sinks: 1.

Selection of appliances: Submit proposals.

915	PREHANDOVER CHECKS

•	 Temporary caps: Remove.

•	 Permanent blanking caps, access covers, rodding eyes, floor gratings and the like: Secure

complete with fixings.

920	SUBMITTALS

•	 Manufacturer's instructions for grease traps: Handover at completion.

R12

Below ground drainage systems

R12 Below ground drainage systems

To be read with Preliminaries/ General conditions.

GENERAL

110	BELOW GROUND DRAINAGE SYSTEMS GENERALLY

•	 Surface water and rainwater drainage sources: Rainwater downpipes, as section R10.

•	 Foul drainage sources: Discharge stack and branch pipes, as section R11.

•	 Land drainage sources: Below ground pipelines from land drainage, as section R13.

•	 Pressure relief drainage sources: Below ground pipelines from pressure relief drainage, as

section R16.

•	 Pipes, bends and junctions: PVC-U - plain wall.

-	Accessories:

-  Access points;

-  Fresh air inlets; and

-  Rodding points.

•	 Manholes, inspection chambers, traps, and separators:

-  Inspection chambers - brickwork, as section F10;

-  Inspection chambers - plastics;

-  Manholes and inspection chambers - concrete; and

-  Manholes and inspection chambers - brick, as section F10.

-	Accessories: Submit proposals .

•	 Disposal: To sewers.

•	 Accessories – general: Access covers and frames  and Concrete (general).

SYSTEM PERFORMANCE

211	DESIGN – BELOW GROUND DRAINAGE SYSTEMS

•	 Design: Complete the design of the below ground drainage system in accordance with BS

EN 752-1, -2, -3 and -4, BS EN 1295-1 and BS EN 1610.

•	 Ground conditions: Varies.

•	 Performance criteria: Refer to  BS EN 1295-1, 'the choice of design assumptions is left to

the judgement of the engineer'.

•	 Proposals: Submit drawings, technical information, calculations and manufacturers'

literature.

PRODUCTS

311	CONNECTORS 	- WASTE PIPES TO CLAY DRAINAGE

•	 Material and standard: Plastics to BS 4660 and Kitemark certified.

•	 Type: DN 100 discharge stacks to DN 100 clay and DN 100 rainwater pipes to DN 100 clay.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

Product reference: Contractor's choice.

311A	CONNECTORS 	- WASTE PIPES TO PLASTICS DRAINAGE

•	 Material and standard: Plastics to BS 4660 and Kitemark certified.

•	 Type: DN 100 discharge stacks to DN 110 plastics and DN 100 rainwater pipes to DN 110

plastics.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

Product reference: Contractor's choice.

313	ONE PIECE GULLIES - PAVED AREAS

•	 Standards:

-	Cast iron: To BS 437 and Kitemark certified, or Agrément certified.

-	Clay: To BS EN 295-1 and Kitemark certified, or Agrément certified.

-	Concrete: To BS 5911-6 and Kitemark certified, or Agrément certified.

-	Plastics: To BS 4660 and Kitemark certified, or Agrément certified.

-	Polypropylene: To BS EN 1852-1.

•	 Material: Plastics.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Sizes: Contractor's choice.

•	 Outlet sizes: DN 100 and DN 150.

•	 Silt buckets: Plastics.

Product reference: Contractor's choice.

315A	ONE PIECE GULLIES AND COVERSGENERALLY

•	 Standards:

-	Cast iron: To BS 437 and Kitemark certified, or Agrément certified.

-	Clay: To BS EN 295-1 and Kitemark certified, or Agrément certified.

-	Concrete: To BS 5911-6 and Kitemark certified, or Agrément certified.

-	Plastics: To BS 4660 and Kitemark certified, or Agrément certified.

-	Polypropylene: To BS EN 1852-1.

•	 Material: Plastics.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Sizes: Contractor's choice.

•	 Outlet sizes: Contractor's choice.

•	 Covers: Hinged grating.

-	Product reference: Contractor's choice.

-	Type: Loose solid plate with cut out for rainwater or waste pipes.

-	Material: Aluminium.

-	Sizes: Contractor's choice.

-	Loading grades to BS EN 124: B125.

•	 Silt buckets: None.

-	Product reference: N/A.

329	PIPES, BENDS AND JUNCTIONS - SUPPLY

•	 Pipes and fittings: From same manufacturer for each pipeline.

344	PIPES, BENDS AND JUNCTIONS - PLASTICS - STRUCTURED WALL - DRAINAGE

•	 Standard: To WIS 04-35-01, Kitemark or Agrément certified.

•	 Material: PVC-U.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Sizes: DN 150.

•	 Jointing type: Spigot and socket.

346	PIPES, BENDS AND JUNCTIONS - PVC-U - PLAIN WALL - DRAINAGE

•	 Standard: BS EN 1401-1, class SN4, with flexible joints, Kitemark certified.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Sizes: DN 100.

•	 Application area code: UD.

352	ACCESS POINTS - PLASTICS - DRAINAGE

•	 Standard: To BS 4660 and Kitemark certified, to BS EN 13589-1, or Agrément certified.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

•	 Nominal diameter: 100mm.

•	 Bases:

-	Product reference: Contractor's choice.

•	 Raising pieces:

-	Product reference: Contractor's choice.

-	Heights: 150 mm.

•	 Access covers and frames:

-	Product reference: Contractor's choice.

Loading grades to BS EN 124: A15, for pedestrian use/ B125, for light traffic use.

359	FLEXIBLE COUPLINGS

•	 Standard: To BS EN 295-4 or WIS 04-41-01 and Kitemark certified, or Agrément certified.

•	 Manufacturer: Contractor's choice.

Product reference: Submit proposals.

361	FRESH AIR INLETS

•	 Manufacturer: Contractor's choice.

-	Product reference: Contractor's choice.

367	RAT BARRIERS

•	 Manufacturer: Contractor's choice.

-	Product reference: Contractor's choice.

371	RODDING POINTS 	As Shown on Drainage Layout Drawing

•	 Standards:

-	Cast iron: To BS 437 and Kitemark certified, or Agrément certified.

-	Clay: To BS EN 295-1 and Kitemark certified, or Agrément certified.

-	Concrete: To BS 5911-6 and Kitemark certified, or Agrément certified.

-	Plastics: To BS 4660 and Kitemark certified, or Agrément certified.

•	 Material: Cast iron/ Clay/Plastics.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

- Product reference: Submit proposals.

•	 Sizes: DN 100.

373	ROOT BARRIERS

•	 Manufacturer: Contractor's choice.

-	Product reference: Submit proposals.

379	WARNING MARKER TAPES - FOUL DRAINAGE

•	 Type: Heavy gauge polyethylene.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Colour: Red with black lettering.

•	 Widths: 150 mm.

•	 Message: FOUL SEWER BELOW.

•	 Wire detection aid: Not required.

401	INSPECTION CHAMBERS - PLASTICS IN GRASSED AREAS

•	 Standard: To BS 7158 or BS EN 13598-1, or Agrément certified.

•	 Diameter: 450 mm.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

•	 Bases:

-	Product reference: Contractor's choice.

•	 Shaft units:

-	Product reference: Contractor's choice.

•	 Access covers and frames:

-	Product reference: Contractor's choice.

Loading grades to BS EN 124: A15, for pedestrian use.

407	MANHOLES AND INSPECTION CHAMBERS - CONCRETE IN ACCESS ROADS

•	 Standards:

-	To BS 5911-3 and BS EN 1917 and Kitemark certified; or

-	To BS 5911-4 and BS EN 1917.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified

•	 Shape: Rectangular

•	 Sizes: 900 X 900 mm.

•	 Cement type and content: To BS 5911-1 and BS EN 1916.

•	 Chamber sections:

-	Product reference: Contractor's choice.

-	Jointing type: Mortar.

•	 Cover slabs:

-	Product reference: Contractor's choice.

-	Thickness: Contractor's choice.

-	Loading grades to BS EN 124: B125 and C250.

-	Openings: To suit access covers.

•	 Steps: Required in chambers over 900mm deep.

409	MANHOLES - CONCRETE - ADDITIONAL COMPONENTS FOR DEEP MANHOLES

•	 Standards:

-	To BS 5911-3 and BS EN 1917 and Kitemark certified; or

-	To BS 5911-4 and BS EN 1917.

•	 Manufacturer: Contractor's choice.

•	 Cement type and content: To BS 5911-3 and BS EN 1917 and Kitemark certified; or to BS

5911-4 and BS EN 1917.

•	 Landing slabs:

-	Product reference: Contractor's choice.

-	Sizes: 900 X 900 mm.

•	 Reducing slabs:

-	Product reference: Contractor's choice.

-	Sizes: Contractor's choice.

•	 Straight backed tapers:

-	Product reference: Contractor's choice.

-	Nominal sizes: -.

•	 Shaft sections:

-	Product reference: Contractor's choice.

-	Sizes: -.

435	MANHOLE CHANNELS AND BRANCHES - PREFORMED PLASTICS

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

Product reference: Contractor's choice.

444	SEALING FOR CONCRETE MANHOLES - BITUMINOUS STRIPS

•	 Manufacturer: Contractor's choice.

-	Product reference: Contractor's choice.

446	SEALING FOR CONCRETE MANHOLES - MORTAR

•	 Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

448	SEALING FOR CONCRETE MANHOLES - SEALANT

•	 Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

471	ACCESS COVERS AND FRAMES  	- DRAINAGE

•	 Standard: To BS EN 124.

•	 Types: Double seals and grease.

•	 Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

-	Product reference: Contractor's choice.

•	 Materials: Grey cast iron.

•	 Finishes: Self finish.

•	 Sizes: 600 x 600 mm.

•	 Loading grades to BS EN 124: B125 and C250.

•	 Edging trims: Not required.

•	 Accessories: none.

475	ACCESS LADDERS 	GENERALLY

•	 Standard: To BS 4211.

•	 Manufacturer: Contractor's choice.

-	Product reference: Submit proposals.

•	 Finish: Galvanized to BS EN ISO 1461.

•	 Accessories: Safety chains and hoops.

483	CONCRETE (GENERAL)

•	 Standards: To BS 8500-1, -2 and BS EN 206-1.

•	 Concrete: To be confirmed by engineer.

485	CONCRETE (STRUCTURAL)

•	 Standards: To BS 8500-1, -2 and BS EN 206-1.

•	 Concrete: To be confirmed by engineer.

487	CONCRETE (ADOPTABLE MANHOLE BENCHINGS AND SURROUNDS)

•	 Standard:

-	England and Wales, Northern Ireland: To WRc 'Sewers for Adoption'.

-	Scotland: To WRc 'Sewers for Scotland'.

•	 Concrete: In situ.

489	CONCRETE (ADOPTABLE MANHOLE BENCHING TOPPING)

•	 Standard:

-	England and Wales, Northern Ireland: To WRc 'Sewers for Adoption'.

-	Scotland: To WRc 'Sewers for Scotland'.

•	 Concrete: High strength.

494	GEOTEXTILE MEMBRANES - IMPERVIOUS

•	 Manufacturer: Contractor's choice.

Product reference: Contractor's choice.

496	GRANULAR MATERIAL

•	 Standard: To BS EN 12620.

-	Size: Dependent on location - see Execution clauses in this section, and in sections R16,

R17 and R18, if used.

498	GRANULAR SUB-BASE MATERIAL

•	 Standard: To Highways Agency Volume 1, 'Specification for Highway Works', Type 1

Unbound mixtures for sub-base.

FABRICATION

510	VERMIN GRATINGS FOR OUTFALLS AND OUTLET HEADWALLS

•	 Construction: Mild steel frame extending 75 mm beyond pipe opening all around, with 25

mm maximum opening steel mesh grille. Top hinged on built-in fish-tail straps and with

bottom pin lock.

•	 Finish: Galvanized to BS EN ISO 1461 after fabrication.

•	 Submit: Shop drawings.

Timing: Before manufacture.

EXECUTION

610	STRIPPING OUT

•	 Extent of stripping out: Drainage within new building footprint.

•	 Exposed ends of existing drainage to be abandoned: Seal with concrete (general).

613	EXCAVATED MATERIAL

•	 Turf, topsoil, hardcore, etc: Set aside for use in reinstatement.

616	SELECTED FILL FOR BACKFILLING

•	 Selected fill: As-dug material, free from vegetable matter, rubbish, frozen soil and material

retained on a 40 mm sieve.

-	Compaction: By hand in 100 mm layers.

623	LOWER PART OF TRENCH – GENERAL

•	 Trench up to 300 mm above crown of pipe: Vertical sides, width as small as practicable.

-	Width (minimum): External diameter of pipe plus 300 mm.

625	LOWER PART OF TRENCH - TRANSITION DEPTH

•	 Trench widths up to 300 mm above crown of pipe (maximum):

-	DN 100 pipelines more than 6.0 m deep: 600 mm.

-	DN 150 pipelines more than 5.4 m deep: 700 mm.

-	DN 225 pipelines more than 4.0 m deep: 800 mm.

-	DN 300 pipelines more than 2.9 m deep: 900 mm.

631	TYPE OF SUBSOIL

•	 General: Where type of subsoil at level of crown of pipe differs from that stated for the type

of bedding, surround or support, give notice.

635	FORMATION FOR BEDDINGS

•	 Timing: Excavate to formation immediately before laying beddings or pipes.

•	 Mud, rock projections, boulders and hard spots: Remove. Replace with consolidated

bedding material.

•	 Local soft spots: Harden by tamping in bedding material.

•	 Inspection of excavated formations: Give notice.

641	PIPES AT DIFFERENT LEVELS IN COMMON TRENCH

•	 Sub trench: Permissible provided soil of step is stable and unlikely to break away.

-	Sub trench not permissible: Trench depth as required for lower pipe. Increase thickness

of bedding to upper pipe as necessary.

•	 Lower pipe: Backfill with compacted granular material to at least half way up higher pipe.

•	 Clear horizontal distance between pipes (minimum):

-	Pipes up to DN 700: 350 mm.

-	Pipes exceeding DN 700: 500 mm.

680	CONCRETE SURROUND FOR PIPE RUNS NEAR FOUNDATIONS

•	 Class Z surround: Provide in locations where bottom of trench is lower than bottom of

foundation and as follows (horizontal clear distance between nearest edges of foundations

and pipe trenches):

-	Trenches less than 1 m from foundations: Top of concrete surround not lower than

bottom of foundation.

-	Trenches more than 1 m from foundations: Top of concrete surround not lower than D

mm below bottom of foundation, where D mm is horizontal distance of trench from

foundation, less 150 mm.

683	LAYING PIPELINES

•	 Laying pipes: To true line and regular gradient on even bed for full length of barrel with

sockets (if any) facing up the gradient.

•	 Ingress of debris: Seal exposed ends during construction.

•	 Timing: Minimize time between laying and testing.

685	JOINTING PIPELINES

•	 Connections: Durable, effective and free from leakage.

•	 Junctions, including to differing pipework systems: With adaptors intended for the purpose.

•	 Cut ends of pipes: Clean and square. Remove burrs and swarf. Chamfer pipe ends before

inserting into ring seal sockets.

•	 Jointing or mating surfaces: Clean and, where necessary, lubricate immediately before

assembly.

•	 Allowance for movement: Provide and maintain appropriate clearance at ends of spigots as

fixing and jointing proceeds.

•	 Jointing material: Do not allow to project into bore of pipes and fittings.

687	CONCRETE SURROUND FOR CROSSOVERS

•	 Class Z surround: Provide where two pipelines (other than plastics pipes) cross with less

than 300 mm separation.

-	Extent, on both pipes: 1 m centred on the crossing point, and beyond as necessary to

come within 150 mm of nearest flexible joints.

689	PIPELINES PASSING THROUGH STRUCTURES

•	 Pipelines that must be cast in or fixed to structures (including manholes, catchpits and

inspection chambers): Provide 600 mm long rocker pipes adjacent to the external face of

the structure (or both faces where appropriate, e.g. walls to footings), with flexible joints at

both ends.

-	Distance to rocker pipe from structure (maximum):150 mm.

•	 Provision for movement for pipelines that need not be cast in or fixed to structures (e.g.

walls to footings):

-	Rocker pipes as specified above; or

-	Openings in the structures to give 50 mm minimum clearance around the pipeline.

Closely fit a rigid sheet to each side of opening to prevent ingress of fill or vermin.

691	BENDS AT BASE OF SOIL STACKS

•	 Type: Large Fold.

-	Fold to centreline of pipe (minimum): 800 mm.

•	 Height of invert of horizontal drain at base of stack below centreline of lowest branch pipe

(minimum): 450 mm.

•	 Bedding: Do not impair flexibility of pipe couplings.

-	Material: Concrete (general).

693	DIRECT CONNECTION OF GROUND FLOOR WCS TO DRAINS

•	 Drop from crown of WC trap to invert of drain (maximum): 1.5 m.

•	 Horizontal distance from the drop to a ventilated drain (maximum): 6 m.

695	BACKDROP PIPES OUTSIDE MANHOLE WALLS

•	 Excavation beneath backdrop pipe: Backfill.

-	Material: Concrete (general).

•	 Pipe encasement:.

-	Material: Concrete (general).

Thickness (minimum): 150 mm.

697	INSTALLING FLEXIBLE COUPLINGS

•	 Ends of pipes to be joined: Cut cleanly and square.

•	 Outer surfaces of pipes to be joined: Clean and smooth. Where necessary, e.g. on

concrete or iron pipes, smooth out mould lines and/ or apply a cement grout over the

sealing area.

•	 Clamping bands: Tighten carefully to make gastight and watertight seals.

699	CONNECTIONS TO SEWERS

•	 General: Connect new pipework to existing adopted sewers to the requirements of the

adopting authority or its agent.

705	INITIAL TESTING OF PIPELINES

•	 Before testing:

-	Cement mortar jointing: Leave 24 h.

-	Solvent welded pipelines: Leave 1 h.

•	 Method: Block open ends of pipelines to be tested and pressurise. Air test short lengths to

BS EN 1610.

711	TRENCH SUPPORTS

•	 Removal of trench supports and other obstacles: Sufficient to permit compacted filling of all

spaces.

713	INSTALLING ROOT BARRIERS

•

715	BACKFILLING TO PIPELINES

•	 Backfilling above top of surround or protective cushion: Material excavated from trench,

compacted in layers 300 mm (maximum) thick.

•	 Heavy compactors: Do not use before there is 600 mm (total) of material over pipes.

718	BACKFILLING OVER CONCRETE

•	 Minimum times from placing concrete:

-	Backfilling generally: 24 h.

Heavy compactors and traffic loads: 72 h.

720	BACKFILLING UNDER ROADS AND PAVINGS

•	 Backfilling from top of surround or protective cushion up to formation level: Granular sub-

base material, laid and compacted in 150 mm layers.

724	PUBLIC ROADS AND PAVINGS - NI

•	 Excavating and backfilling of trenches: To Northern Ireland Road Authority and Utilities

Committee 'Specification for the reinstatement of openings in highways'.

728	LAYING WARNING MARKER TAPES

•	 Installation: During backfilling, lay continuously over pipelines.

•	 Depth: 300-400 mm.

Pipelines deeper than 2 m: Lay an additional tape 600 mm above the top of the pipeline.

732	TEMPORARY BRIDGES

•	 Trench bridges: As necessary to prevent construction traffic damaging pipes after

backfilling.

734	INSTALLING ACCESS POINTS AND GULLIES

•	 Bedding:

-	Material: Granular material, size 4/10.

-	Thickness (minimum): 100 mm.

•	 Surround:

-	Material: Concrete (general).

-	Thickness (minimum): 150 mm.

-	Height: Full height.

•	 Backfilling: -.

-	Material: Granular material, size 4/10, to mm above crown of pipes, then selected fill.

-	Compaction: By hand in 100 mm layers.

•	 Setting out relative to adjacent construction features: Square and tightly jointed.

•	 Permissible deviation in level of external covers and gratings: +0 to -6 mm.

•	 Raising pieces (clay and concrete units): Joint with 1:3 cement:sand mortar.

•	 Exposed openings: Fit purpose made temporary caps. Protect from traffic.

736	INSTALLING RODDING POINTS

•	 Bedding and surround:

-	Material: Concrete (general).

-	Thickness (minimum): 100 mm.

•	 Permissible deviation in level of external covers and gratings: +0 to -6 mm.

741	INSTALLING INSPECTION CHAMBERS - PLASTICS

•	 Bedding:

-	Material: Granular material, size 4/10.

-	Thickness (minimum): 150 mm.

•	 Surround:

-	Material: Concrete (general).

-	Thickness (minimum): 150 mm.

•	 Backfilling: Granular material, size 4/10, to mm above crown of pipes, then selected fill.

-	Compaction: By hand in 100 mm layers.

•	 Concrete collar:

-	Material: Concrete (general).

-	Thickness (minimum): 200 mm.

-	Width (minimum): 300 mm.

•	 Seating: Not required.

743	INSTALLING CONCRETE MANHOLES

•	 Bases:

-	Material: Concrete (general).

-	Thickness (minimum): 225 mm.

•	 Surround:

-	Material: Concrete (general).

-	Thickness (minimum): 150 mm.

-	Height: Full height.

•	 Backfilling:

-	Material: Granular material, size 4/10, to mm above crown of pipes, then selected fill.

Compaction: By hand in 100 mm layers.

753	FIXING MANHOLE STEPS

•	 Fixing: Bed in joints.

•	 Positioning: 300 mm vertical centres staggered 300 mm horizontally, with lowest step 300

mm (maximum) above benching and top step 450 mm (maximum) below top of cover.

755	JOINTING CONCRETE MANHOLE CHAMBER SECTIONS

•	 Jointing and sealing: Mortar.

•	 Inner joint surface: Trim surplus jointing material extruded into chamber and point neatly.

757	LAYING CONVENTIONAL CHANNELS, BRANCHES AND BENCHING

•	 Main channel: Bed solid in 1:3 cement:sand mortar.

-	Branches: Connect to channel, preferably at half pipe level, so that discharge flows

smoothly in direction of main flow.

-	Branches greater than nominal size 150 mm: Connect the branch soffit level with the

main drain soffit.

-	Connecting angles more than 45° to direction of flow: Use three-quarter section channel

bends.

•	 Benching:

-	Material: Concrete (general).

-	Profile: Rise vertically from top of main channel to a level not lower than soffit of outlet

pipe, then slope upwards at 10% to walls.

-	Topping:

Material: 1:3 Cement:sand mortar.

-	Application: Before benching concrete has set, and with dense smooth uniform finish.

759	LAYING PREFORMED PLASTICS CHANNELS, BRANCHES AND BENCHING

•	 Main channel: Bed solid in 1:3 cement:sand mortar.

-	Branches: Connect to channel, preferably at half pipe level, so that discharge flows

smoothly in direction of main flow.

-	Connecting angles more than 45° to direction of flow: Use three-quarter section channel

bends.

•	 Bedding: 1:3 cement:sand mortar. Use clips or ensure adequate mechanical key.

•	 Benching:

-	Material: Concrete (general).

-	Profile: Rise vertically from top of main channel to a level not lower than soffit of outlet

pipe, then slope upwards at 10% to walls.

-	Topping:

Material: 1:3 Cement:sand mortar.

Application: Before benching concrete has set, and with dense smooth uniform finish.

761	LAYING SEALED ACCESS FITTINGS, BRANCHES AND BENCHING

•	 Unused branches: Fit caps.

•	 Bedding: 1:3 cement:sand mortar.

•	 Benching:

-	Material: Concrete (general).

Profile: 10% fall from manhole walls to component rim.

-	Topping:

Material: 1:3 Cement:sand mortar.

Application: Before benching concrete has set, and with dense smooth uniform finish.

771	INSTALLING OUTFALLS

•	 Pipe outflow invert (minimum): Seasonal peak level or 150 mm above normal water level,

whichever is the higher.

•	 Pipe surround and backfill to the last 2 m run of drain: Excavated subsoil, rammed home.

773	INSTALLING ACCESS COVERS AND FRAMES

•	 Seating: Precast concrete.

•	 Bedding and haunching of frames: Continuously.

-	Material: 1:3 cement:sand mortar.

-	Top of haunching: 30 mm below surrounding surfaces.

•	 Horizontal positioning of frames:

-	Centred over openings.

-	Square with joints in surrounding paving.

•	 Vertical positioning of frames:

-	Level; or

-	Marry in with levels of surrounding paving.

•	 Permissible deviation in level of external covers and frames: +0 to -6 mm.

776	EXPOSED OPENINGS IN INSPECTION CHAMBERS, ACCESS POINTS, FITTINGS AND

EQUIPMENT

•	 General: Fit purpose made temporary caps. Protect from site traffic.

COMPLETION

901	REMOVAL OF DEBRIS AND CLEANING

•	 Preparation: Lift covers to manholes, inspection chambers and access points. Remove

mortar droppings, debris and loose wrappings.

-	Timing: Before cleaning, final testing, CCTV inspection if specified, and immediately

before handover.

•	 Cleaning: Thoroughly flush pipelines with water to remove silt and check for blockages.

Rod pipelines between access points if there is any indication that they may be obstructed.

•	 Washings and detritus: Do not discharge into sewers or watercourses.

•	 Covers: Securely replace after cleaning and testing.

903	TEMPORARY MEASURES

•	 Water used to stabilize tanks and the like during installation: Drain.

921	FINAL TESTING OF PRIVATE GRAVITY DRAINS AND SEWERS UP TO DN 300

•	 Before testing:

-	Cement mortar jointing: Leave 24 h.

-	Solvent welded pipelines: Leave 1 h.

•	 Standard: To Building Regulations.

•	 Method: Water.

931	FINAL TESTING OF ADOPTABLE AND LARGE PRIVATE SEWERS

•	 Standard (sewers up to and including size DN 750):

-	England, Wales and Northern Ireland: To WRc 'Sewers for adoption'.

-	Scotland: To WRc 'Sewers for Scotland'.

•	 Method: Water.

941	WATER TESTING OF MANHOLES AND INSPECTION CHAMBERS

•	 Timing: Before backfilling.

•	 Standard:

-	Exfiltration: To BS EN 1610.

-	Method: Testing with water (method W).

Infiltration: No identifiable flow of water penetrating the chamber.

971	CCTV INSPECTION OF PRIVATE PIPELINES

•	 General: Carry out and record internal inspection using CCTV equipment.

-	Locations to be inspected: Adoptable foul and surface water sewers.

•	 Illumination: Of adequate intensity.

•	 Recording: Provide continuous position recording, still photographs and stopping of the

camera at any point.

Copy of videotape recording: Submit.

978	LIFTING KEYS

•	 Lifting keys: Supply suitable keys for each type of access cover.

Timing: At completion.

Z

Building fabric reference specification

Z10

Purpose made joinery

Z10 Purpose made joinery

To be read with Preliminaries/ General conditions.

110	FABRICATION

•	 Standard: To BS 1186-2.

•	 Sections: Accurate in profile and length, and free from twist and bowing. Formed out of

solid unless shown otherwise.

-	Machined surfaces: Smooth and free from tearing, wooliness, chip bruising and other

machining defects.

•	 Joints: Tight and close fitting.

•	 Assembled components: Rigid. Free from distortion.

•	 Screws: Provide pilot holes.

-	Screws of 8 gauge (4 mm diameter) or more and screws into hardwood: Provide

clearance holes.

-	Countersink screws: Heads sunk at least 2 mm below surfaces visible in completed

work.

•	 Adhesives: Compatible with wood preservatives applied and end uses of timber.

120	CROSS SECTION DIMENSIONS OF TIMBER

•	 General: Dimensions on drawings are finished sizes.

•	 Maximum permitted deviations from finished sizes:

-	Softwood sections: To BS EN 1313-1:-

Clause 6 for sawn sections.

Clause NA.2 for further processed sections.

-	Hardwood sections: To BS EN 1313-2:-

Clause 6 for sawn sections.

Clause NA.3 for further processed sections.

130	PRESERVATIVE TREATED WOOD

•	 Cutting and machining: Completed as far as possible before treatment.

•	 Extensively processed timber: Retreat timber sawn lengthways, thicknessed, planed,

ploughed, etc.

•	 Surfaces exposed by minor cutting and/ or drilling: Treat with two flood coats of a solution

recommended by main treatment solution manufacturer.

140	MOISTURE CONTENT

•	 Wood and wood based products: Maintained within range specified for the component

during manufacture and storage.

210	LAMINATED PLASTICS VENEERED BOARDS/ PANELS

•	 Fabrication: To British Laminated Plastics Fabricators Association Ltd (BLF) fabricating

standards.

•	 Balancing veneer: From decorative veneer manufacturer and of similar composition.

Applied to reverse side of core.

•	 Finished components: Free from defects, including bow, twist, scratches, chipping, cracks,

pimpling, indentations, glue marks, staining and variations in colour and pattern.

•	 Joints visible in completed work: Tight butted, true and flush.

220	WOOD VENEERED BOARDS/ PANELS

•	 Core material and veneers: Conditioned before bonding.

•	 Setting out: Veneer features and grain pattern aligned regularly and symmetrically unless

instructed otherwise.

•	 Balancing veneer: Applied to reverse side of core material.

-	Moisture and temperature movement characteristics: As facing veneer.

•	 Veneer edges: Tight butted and flush, with no gaps.

•	 Tolerance of veneer thickness (maximum): ± 0.5 mm.

•	 Finished components: Free from defects, including bow, twist, scratches, chipping, splits,

blebs, indentations, glue marks and staining.

•	 Surface finish: Fine, smooth, free from sanding marks.

250	FINISHING

•	 Surfaces: Smooth, even and suitable to receive finishes.

-	Arrises: Eased unless shown otherwise on drawings.

•	 End grain in external components: Sealed with primer or sealer as section M60 and

allowed to dry before assembly.

Z11

Purpose made metalwork

Z11 Purpose made metalwork

To be read with Preliminaries/ General conditions.

310	METAL PRODUCTS

•	 Standards: Generally, as specified in the following clauses.

•	 Fasteners: Generally, same metal as component, with matching coating and finish.

320	STEEL LONG AND FLAT PRODUCTS

•	 Hot rolled structural steels (excluding structural hollow sections and tubes): To BS EN

10025-1.

•	 Fine grain steels, including special steels: To BS EN 10025-3 and -4.

•	 Improved atmospheric corrosion resistance: To BS EN 10025-5.

330	STEEL PLATE, SHEET AND STRIP

•	 Plates and wide flats, high yield strength steel: To BS EN 10025-6.

340	HOT ROLLED STEEL PLATE, SHEET AND STRIP

•	 Flat products, high yield strength for cold forming: To BS EN 10149-1, -2 and -3.

•	 Low carbon steel sheet and strip for cold forming: To BS EN 10111.

•	 Narrow strip, formable and general engineering purposes: To BS 1449-1.8 and BS 1449-

1.14.

350	COLD ROLLED STEEL PLATE, SHEET AND STRIP

•	 Steel sections: To BS EN 10162.

•	 Flat products, high yield strength micro-alloyed steels for cold forming: To BS EN 10268.

•	 Low carbon steel flat products for cold forming: To BS EN 10130 and BS EN 10131.

•	 Uncoated mild steel narrow strip for cold forming: To BS EN 10139 and BS EN 10140.

•	 Narrow strip, general engineering purposes: To BS EN 10132-1, -2, and -3.

•	 Low carbon steel flat products for vitreous enamelling: To BS EN 10209.

360	STEEL COATED FLAT PRODUCTS

•	 Hot dip zinc coated low carbon steel sheet and strip for cold forming: To BS EN 10327 and

BS EN 10143.

•	 Hot dip zinc coated structural steel sheet and strip: To BS EN 10143 and BS EN 10326.

•	 Hot dip zinc-aluminium (za) coated sheet and strip: To BS EN 10326 and 10327.

•	 Hot dip aluminium-zinc (az) coated sheet and strip: To BS EN 10327.

•	 Organic coated flat products: To BS EN 10169-1.

370	STEEL STRUCTURAL HOLLOW SECTIONS (SHS)

•	 Non alloy and fine grain steels, hot finished: To BS EN 10210-1 and -2.

•	 Non-alloy and fine grain steels, cold formed welded: To BS EN 10219-2.

•	 Weather resistant steels, hot finished: To BS 7668.

380	OTHER STEEL SECTIONS

•	 Equal flange tees: To BS EN 10055.

•	 Equal and unequal angles: To BS EN 10056-1 and -2.

•	 Wire, mild steel for general engineering purposes: To BS 1052.

•	 Wire and wire products, general: To BS EN 10218-2.

•	 Tubes:

-	Seamless circular: To BS EN 10297-1.

-	Seamless cold drawn: To BS EN 10305-1.

-	Welded and cold sized square and rectangular: To BS EN 10305-5.

-	Welded circular: To BS EN 10296-1.

-	Welded cold drawn: To BS EN 10305-2.

Welded cold sized: To BS EN 10305-3.

400	STAINLESS STEEL PRODUCTS

•	 Chemical composition and physical properties: To BS EN 10088-1.

•	 Sheet, strip and plate: To BS EN 10088-2.

•	 Semi-finished products bars, rods and sections: To BS EN 10088-3.

•	 Wire: To BS EN 1088-3.

•	 Tubes:

-	Welded circular: To BS EN 10296-2.

-	Seamless circular: To BS EN 10297-2.

410	ALUMINIUM ALLOY PRODUCTS

•	 Designations:

-	Designation system, chemical composition and forms: To BS EN 573-1 to -4.

-	Temper designations: To BS EN 515.

•	 Sheet, strip and plate: To BS EN 485-1 to -4.

•	 Cold drawn rods, bars and tubes: To BS EN 754-1 and -2.

•	 Extruded rods, bars, tubes and profiles: To BS EN 755-1 and -2.

•	 Drawn wire: To BS EN 1301-1, -2 and -3.

•	 Rivet, bolt and screw stock: To BS 1473.

•	 Structural sections: To BS 1161.

420	COPPER ALLOY PRODUCTS

•	 Sheet, strip, plate and circles for general purposes: To BS EN 1652.

•	 Sheet and strip for building purposes: To BS EN 1172.

•	 Rods: To BS EN 12163.

•	 Profiles and rectangular bars: To BS EN 12167.

•	 Wire: To BS EN 12166.

•	 Tubes: To BS EN 12449.

510	PREPARATION FOR APPLICATION OF COATINGS

•	 General: Complete fabrication, and drill fixing holes before applying coatings.

•	 Paint, grease, flux, rust, burrs and sharp arrises: Remove.

515	FABRICATION GENERALLY

•	 Contact between dissimilar metals in components: Avoid.

•	 Finished components: Rigid and free from distortion, cracks, burrs and sharp arrises.

-	Moving parts: Free moving without binding.

•	 Corner junctions of identical sections: Mitre.

•	 Prefinished metals: Do not damage or alter appearance of finish.

520	COLD FORMED WORK

•	 Profiles: Accurate, with straight arrises.

525	ADHESIVE BONDING

•	 Preparation of surfaces of metals to receive adhesives:

-	Degrease.

-	Abrade mechanically or chemically etch.

-	Prime: To suit adhesive.

•	 Adhesive bond: Form under pressure.

530	THERMAL CUTTING OF STAINLESS STEEL

•	 Carbonation in the heat affected zone: Remove, after cutting.

535	WELDING/ BRAZING GENERALLY

•	 Surfaces to be joined: Clean thoroughly.

•	 Tack welds: Use only for temporary attachment.

•	 Joints: Fully bond parent and filler metal throughout with no inclusions, holes, porosity or

cracks.

•	 Surfaces of materials that will be self-finished and visible in completed work: Protect from

weld spatter.

•	 Flux residue, slag and weld spatter: Remove.

540	WELDING OF STEEL

•	 Method: Metal arc welding to BS EN 1011-1 and -2.

545	WELDING OF STAINLESS STEEL

•	 Method: TIG welding to BS EN 1011-3.

•	 Butt welds: Double bevel.

550	WELDING OF ALUMINIUM ALLOYS

•	 Method: TIG or MIG welding to BS EN 1011-4.

555	BRAZING

•	 Standard: To BS EN 14324.

565	FINISHING WELDED AND BRAZED JOINTS VISIBLE IN COMPLETE WORK

•	 Butt joints: Smooth, and flush with adjacent surfaces.

•	 Fillet joints: Neat.

•	 Grinding: Grind smooth where indicated on drawings.

570	LIQUID ORGANIC COATING FOR ALUMINIUM ALLOY COMPONENTS

•	 Standard: To BS 4842.

575	ZINC AND CADMIUM PLATING OF IRON AND STEEL SURFACES

•	 Zinc plating: To BS EN 12329.

•	 Cadmium plating: To BS EN 12330.

580	CHROMIUM PLATING

•	 Standard: To BS EN 12540.

585	GALVANIZING

•	 Standard: To BS EN ISO 1461.

•	 Vent and drain holes:

-	Location: Submit proposals..

Sealing after galvanizing: Required. Submit proposals.

590	VITREOUS ENAMELLING

•	 Standard: To BS EN 14431.

•	 Substrate metal: Carbon steel or cast iron.

Z12

Preservative/ fire retardant treatment

Z12 Preservative/ fire retardant treatment

To be read with Preliminaries/ General conditions.

110	TREATMENT APPLICATION

•	 Timing: After cutting and machining timber, and before assembling components.

•	 Processor: Licensed by manufacturer of specified treatment solution.

•	 Certification: For each batch of timber provide a certificate of assurance that treatment has

been carried out as specified.

120	COMMODITY SPECIFICATIONS

•	 Standard: Current edition of the British Wood Preserving and Damp-proofing Association

(BWPDA) Manual.

130	PRESERVATIVE TREATMENT SOLUTION STRENGTHS/ TREATMENT CYCLES

•	 General: Select to achieve specified service life and to suit treatability of specified wood

species.

160	ORGANIC SOLVENT PRESERVATIVE TREATMENT

•	 Solution:

-	Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified .

Product reference: Contractor's choice .

-	Application: Double vacuum + low pressure impregnation, or immersion.

•	 Moisture content of wood at time of treatment: As specified for the timber/ component at

time of fixing. After treatment, timber to be surface dry before use.

170	CREOSOTE PRESERVATIVE TREATMENT

•	 Solution:

-	Manufacturer: Contractor's choice .

Product reference: Contractor's choice .

-	Application: High pressure impregnation, or immersion.

•	 Moisture content of wood at time of treatment: Not more than 28%. After treatment, allow

timber to dry before using.

210	FIRE RETARDANT TREATMENT

•	 Solution type: Humidity resistant.

-	Manufacturer: Contractor's choice to PIFA Standard 6/83A or Agrément certified.

Product reference: Contractor's choice.

-	Application: Vacuum + pressure impregnation.

•	 Moisture content of wood at time of treatment: As specified for the timber/ component at

time of fixing. After treatment, timber to be redried slowly at temperatures not exceeding

65°C to minimize distortion and degradation.

Z20

Fixings and adhesives

Z20 Fixings and adhesives

To be read with Preliminaries/ General conditions.

PRODUCTS

310	FASTENERS GENERALLY

•	 Materials: To have:

-	Bimetallic corrosion resistance appropriate to items being fixed.

-	Atmospheric corrosion resistance appropriate to fixing location.

•	 Appearance: Submit samples on request.

320	PACKINGS

•	 Materials: Noncompressible, corrosion proof.

•	 Area of packings: Sufficient to transfer loads.

330	NAILED TIMBER FASTENERS

•	 Nails:

-	Steel: To BS 1202-1 or BS EN 10230-1.

-	Copper: To BS EN 1202-2.

-	Aluminium: To BS 1202-3.

340	MASONRY FIXINGS

•	 Light duty: Plugs and screws.

•	 Heavy duty: Expansion anchors or chemical anchors.

350	PLUGS

•	 Type: Proprietary types to suit substrate, loads to be supported and conditions expected in

use.

360	ANCHORS

•	 Types:

-	Expansion: For use in substrate strong enough to resist forces generated by expansion

of anchor.

-	Adhesive or chemical:

For use in substrate where expansion of anchor would fracture substrate.

For use in irregular substrate where expansion anchors cannot transfer load on anchor.

-	Cavity: For use where the anchor is retained by toggles of the plug locking onto the

inside face of the cavity.

370	WOOD SCREWS

•	 Type:

-  Wood screws (traditional pattern).

Standard: To BS 1210.

-  Wood screws.

Pattern: Parallel, fully threaded shank or twin thread types.

•	 Washers and screw cups: Where required are to be of same material as screw.

380	MISCELLANEOUS SCREWS

•	 Type: To suit the fixing requirement of the components and substrate.

-	Pattern: Self-tapping, metallic drive screws, or power driven screws.

•	 Washers and screw cups: Where required to be of same material as screw.

390	ADHESIVES GENERALLY

•	 Standards:

-	Hot-setting phenolic and aminoplastic: To BS 1203.

-	Thermosetting wood adhesives: To BS EN 12765.

-	Polyvinyl acetate thermoplastic adhesive: To BS 4071.

410	POWDER ACTUATED FIXING SYSTEMS

•	 Types of fastener, accessories and consumables: As recommended by tool manufacturer.

EXECUTION

610	FIXING GENERALLY

•	 Integrity of supported components: Select types, sizes, quantities and spacings of fixings,

fasteners and packings to retain supported components without distortion or loss of

support.

•	 Components, substrates, fixings and fasteners of dissimilar metals: Isolate with washers/

sleeves to avoid bimetallic corrosion.

•	 Appearance: Fixings to be in straight lines at regular centres.

620	FIXING THROUGH FINISHES

•	 Penetration of fasteners and plugs into substrate: To achieve a secure fixing.

630	FIXING PACKINGS

•	 Function: To take up tolerances and prevent distortion of materials and components.

•	 Limits: Do not use packings beyond thicknesses recommended by fixings and fasteners

manufacturer.

•	 Locations: Not within zones to be filled with sealant.

640	FIXING CRAMPS

•	 Cramp positions: Maximum 150 mm from each end of frame sections and at 600 mm

maximum centres.

•	 Fasteners: Fix cramps to frames with screws of same material as cramps.

•	 Fixings in masonry work: Fully bed in mortar.

650	NAILED TIMBER FIXING

•	 Penetration: Drive fully in without splitting or crushing timber.

•	 Surfaces visible in completed work: Punch nail heads below wrot surfaces.

•	 Nailed timber joints: Two nails per joint (minimum), opposed skew driven.

660	SCREW FIXING

•	 Finished level of countersunk screw heads:

-	Exposed: Flush with timber surface.

-	Concealed (holes filled or stopped): Sink minimum 2 mm below surface.

670	PELLETED COUNTERSUNK SCREW FIXING

•	 Finished level of countersunk screw heads: Minimum 6 mm below timber surface.

•	 Pellets: Cut from matching timber, match grain and glue in to full depth of hole.

•	 Finished level of pellets: Flush with surface.

680	PLUGGED COUNTERSUNK SCREW FIXING

•	 Finished level of countersunk screw heads: Minimum 6 mm below timber surface.

•	 Plugs: Glue in to full depth of hole.

•	 Finished level of plugs: Projecting above surface.

690	USING POWDER ACTUATED FIXING SYSTEMS

•	 Powder actuated fixing tools: To BS 4078-2 and Kitemark certified.

•	 Operatives: Trained and certified as competent by tool manufacturer.

700	APPLYING ADHESIVES

•	 Surfaces: Clean. Adjust regularity and texture to suit bonding and gap filling characteristics

of adhesive.

•	 Support and clamping during setting: Provide as necessary. Do not mark surfaces of or

distort components being fixed.

•	 Finished adhesive joints: Fully bonded. Free of surplus adhesive.

Z21

Mortars

Z21 Mortars

To be read with Preliminaries/ General conditions.

CEMENT GAUGED MORTARS

110	CEMENT GAUGED MORTAR MIXES

•	 Specification: Proportions and additional requirements for mortar materials are specified

elsewhere.

120	SAND FOR SITE MADE CEMENT GAUGED MASONRY MORTARS

•	 Standard: To BS EN 13139.

•	 Grading: 0/2 (FP or MP).

-	Fines content where the proportion of sand in a mortar mix is specified as a range (e.g.

1:1: 5-6):

Lower proportion of sand: Use category 3 fines.

Higher proportion of sand: Use category 2 fines.

•	 Sand for facework mortar: Maintain consistent colour and texture. Obtain from one source.

131	READY-MIXED LIME:SAND FOR CEMENT GAUGED MASONRY MORTARS

•	 Standard: To BS EN 998-2.

•	 Lime: Nonhydraulic to BS EN 459-1.

-	Type: CL 90S.

•	 Pigments for coloured mortars: To BS EN 12878.

160	CEMENTS FOR MORTARS

•	 Cement: To BS EN 197-1 and CE marked.

-	Types:  		Portland cement, CEM I.

Portland limestone cement, CEM ll/A-L or CEM ll/A-LL.

Portland slag cement, CEM II/B-S.

Portland fly ash cement, CEM II/B-V.

-	Strength class: 32.5, 42.5 or 52.5.

•	 White cement: To BS EN 197-1 and CE marked.

-	Type: Portland cement, CEM I.

-	Strength class: 52.5.

•	 Sulphate resisting Portland cement:

-	Types:  		To BS 4027 and Kitemarked.

To BS EN 197-1 fly ash cement, CEM ll/B-V and CE marked.

-	Strength class: 32.5, 42.5 or 52.5.

•	 Masonry cement: To BS EN 413-1 and CE marked.

-	Class: MC 12.5.

180	ADMIXTURES FOR SITE MADE CEMENT GAUGED MORTARS

•	 Air entraining (plasticizing) admixtures: To BS EN 934-3 and compatible with other mortar

constituents.

•	 Other admixtures: Submit proposals.

•	 Prohibited admixtures: Calcium chloride, ethylene glycol and any admixture containing

calcium chloride.

190	RETARDED READY TO USE CEMENT GAUGED MORTAR

•	 Standard: To BS EN 998-2.

•	 Lime for cement:lime:sand mortars: Nonhydraulic to BS EN 459-1.

-	Type: CL 90S.

•	 Pigments for coloured mortars: To BS EN 12878.

•	 Time and temperature limitations: Use within limits prescribed by mortar manufacturer.

-	Retempering: Restore workability with water only within prescribed time limits.

200	STORAGE OF CEMENT GAUGED MORTAR MATERIALS

•	 Sands and aggregates: Keep different types/ grades in separate stockpiles on hard, clean,

free-draining bases.

•	 Factory made ready-mixed lime:sand/ ready to use retarded mortars: Keep in covered

containers to prevent drying out or wetting.

•	 Bagged cement/ hydrated lime: Store off the ground in dry conditions.

210	MAKING CEMENT GAUGED MORTARS

•	 Batching: By volume. Use clean and accurate gauge boxes or buckets.

-	Mix proportions: Based on dry sand. Allow for bulking of damp sand.

•	 Mixing: Mix materials thoroughly to uniform consistency, free from lumps.

-	Mortars containing air entraining admixtures: Mix mechanically. Do not overmix.

•	 Working time (maximum): Two hours at normal temperatures.

•	 Contamination: Prevent intermixing with other materials.

Z22

Sealants

Z22 Sealants

To be read with Preliminaries/General conditions.

PRODUCTS

310	JOINTSGENERALLY

•	 Primer, backing strip, bond breaker: Types recommended by sealant manufacturer.

EXECUTION

610	SUITABILITY OF JOINTS

•	 Presealing checks:

-	Joint dimensions: Within limits specified for the sealant.

-	Substrate quality: Surfaces regular, undamaged and stable.

•	 Joints not fit to receive sealant: Submit proposals for rectification.

620	PREPARING JOINTS

•	 Surfaces to which sealant must adhere:

-	Remove temporary coatings, tapes, loosely adhering material, dust, oil, grease, surface

water and contaminants that may affect bond.

-	Clean using materials and methods recommended by sealant manufacturer.

•	 Vulnerable surfaces adjacent to joints: Mask to prevent staining or smearing with primer or

sealant.

•	 Backing strip and/ or bond breaker installation: Insert into joint to correct depth, without

stretching or twisting, leaving no gaps.

•	 Protection: Keep joints clean and protect from damage until sealant is applied.

630	APPLYING SEALANTS

•	 Substrate: Dry (unless recommended otherwise) and unaffected by frost, ice or snow.

•	 Environmental conditions: Do not dry or raise temperature of joints by heating.

•	 Sealant application: Fill joints completely and neatly, ensuring firm adhesion to substrates.

•	 Sealant profiles:

-	Butt and lap joints: Slightly concave.

-	Fillet joints: Flat or slightly convex.

•	 Protection: Protect finished joints from contamination or damage until sealant has cured.

Z31

Powder coatings

Z31 Powder coatings

To be read with Preliminaries/ General conditions.

120	POWDER COATING MATERIALS

•	 Manufacturer: Obtain from one only of the following: Contractor's choice to PIFA Standard

6/83A or Agrément certified .

•	 Selected manufacturer: Submit details before commencement of powder coating.

210	WORKING PROCEDURES

•	 Requirement: Comply with:

-	BS 6496 for aluminium alloy backgrounds.

-	BS EN 13438 for galvanized steel and sheradized backgrounds.

-	British Coatings Federation: Code of safe practice - Application of thermosetting powder

coatings by electrostatic spraying.

Powder coating manufacturer's guarantee.

220	POWDER COATING APPLICATORS

•	 Applicator requirements:

-	Approved by powder coating manufacturer.

-	Currently certified to BS EN ISO 9001.

-	Comply with quality procedures, guarantee conditions, standards and tests required by

powder coating manufacturer.

-	Each applicator to use only one plant.

•	 Selected applicator: Submit details before commencement of powder coating.

225	GUARANTEES

•	 Powder coating manufacturer and applicator guarantees:

-	Submit sample copies before commencement of powder coating.

-	Submit signed project specific copies on completion of work.

230	CONTROL SAMPLES

•	 Sequence: Prior to ordering materials for the works, obtain approval of appearance for:

-	Powder coated samples: Of various grades and forms of background metal to be used,

showing any colour, texture and gloss variation.

-	Fabrication samples: Showing joint assembly, how powder coating is affected and how

any cut metal edges are protected.

•	 Samples to include the following information:

-	Product reference.

-	Colour:

Reference number.

Name.

Gloss level.

241	INDEPENDENT INSPECTION ON SITE

•	 Requirement: Where coating specification compliance at plant is unresolved, contractors/

suppliers must commission an approved Independent Inspection Authority to carry out site

acceptance inspections.

•	 Acceptance inspections: Carry out in accordance with BS 6001-2 with a limiting quality of

5% where the probability of acceptance is 10%. Each component of a fabricated unit will

be assessed as an individual part for sampling procedures.

•	 Components failing inspection: Remove and reprocess/ replace.

250	COMPONENT DESIGN

•	 Condition of components to be powder coated:

-	To comply with relevant recommendations of BS 4479-1, -3, and -4.

-	Of suitable size to fit plant capacity.

-	Of suitable thickness to withstand oven curing.

310	PRETREATMENT

•	 Condition of components to be powder coated:

-	Free from corrosion and damage.

-	Free from impurities including soil, grease, oil.

-	Suitable for and compatible with the pre-treatment and powder coating process.

•	 Process: Clean, conversion coat, condition, rinse in demineralised water, drain and dry

components in accordance with the powder coating manufacturer's requirements and the

pre-treatment supplier's recommendations.

430	EXTENT OF POWDER COATINGS

•	 Application: To visible component surfaces, and concealed surfaces requiring protection.

Coated surfaces will be deemed 'significant surfaces' for relevant BS 6496/ BS EN 13438

performance requirements.

435	APPLICATION OF POWDER COATINGS

•	 Surfaces to receive powder coatings: Free from dust or powder deposits.

•	 Completion of powder coatings: Within 48 hours of pre-treatment of components.

•	 Jig points: Not visible on coated components.

•	 Curing: Controlled to attain metal temperatures and hold periods recommended by powder

coating manufacturer.

•	 Stripping and recoating of components: Only acceptable by prior agreement of powder

coating manufacturer. Stripping, pre-treatment and powder coating are to be in accordance

with manufacturer's requirements.

•	 Overcoating of components: Not acceptable.

440	PERFORMANCE AND APPEARANCE OF POWDER COATINGS

•	 Standard: To BS 6496/ BS EN 13438.

450	ALUMINIUM ALLOY FABRICATIONS

•	 Units may be assembled:

-	Before powder coating.

-	From components powder coated after cutting to size.

-	Where approved, from components powder coated before cutting to size.

•	 Exposure of uncoated background metal: Not acceptable.

•	 Assembly sealants: Compatible with powder coatings. Obtain approval of colour if sealants

are visible after fabrication.

460	STEEL FABRICATIONS

•	 Unit assembly: Wherever practical, before powder coating.

•	 Exposure of uncoated background metal: Not acceptable.

•	 Assembly sealants: Compatible with powder coatings. Obtain approval of colour if sealants

are visible after fabrication.

470	FIXINGS

•	 Exposed metal fixings: Powder coat together with components, or coat with matching

repair paint system applied in accordance with the powder coating manufacturer's

recommendations.

480	FABRICATION DAMAGE REPAIR/ REPLACEMENT

•	 Inspection: Check all components before delivery to site for damage to powder coatings.

Submit proposals for repair or replacement.

510	PROTECTION

•	 Powder coated surfaces of components: Protect from damage during handling and

installation, or by subsequent site operations.

•	 Protective coverings: Must be:

-	Resistant to weather conditions.

-	Partially removable to suit building in and access to fixing points.

•	 Protective tapes in contact with powder coatings: Must be:

-	Low tack, self-adhesive and light in colour.

-	Applied and removed in accordance with tape and powder coating manufacturers'

recommendations. Do not use solvents to remove residues as these are detrimental to

the coating.

•	 Inspection of protection: Carry out monthly. Promptly repair any deterioration or deficiency.

530	SITE DAMAGE REPAIR/ REPLACEMENT

•	 Damage to powder coatings: Rectify immediately damage caused during handling and

installation, or by subsequent site operations. Submit proposals for extensive repair or

replacement.

535	DOCUMENTATION

•	 Submit the following information for each batch of powder coated components:

-	Supplier.

-	Trade name.

-	Colour.

-	Type of powder.

-	Method of application.

-	Batch and reference number.

-	Statutory requirements.

540	COMPLETION

•	 Cleaning and maintenance of powder coatings: Carry out in accordance with procedures

detailed in powder coating manufacturer and applicator guarantees.

Z33

Anodizing

Z33 Anodizing

To be read with Preliminaries/ General conditions.

210	WORKING PROCEDURES

•	 Requirement: Comply with BS 3987 for anodic coatings on wrought aluminium.

220	ANODIZER REQUIREMENTS

•	 Processing:

-	Approved by the Aluminium Finishing Association.

-	Currently certified to BS EN ISO 9001.

Each anodizer to use only one plant.

230	GUARANTEES

•	 Anodizer guarantees:

-	Submit sample copies before commencement of anodizing.

-	Submit signed project specific copies on completion of work.

240	CONTROL SAMPLES

•	 Sequence: Prior to ordering materials for the works, obtain approval of appearance for:

-	Anodic coated samples: Showing colour and texture variation.

-	Fabrication samples: Showing joint assembly, how anodic coating is affected and how

cut metal edges are protected.

260	INDEPENDENT INSPECTION ON SITE

•	 Requirement: Where anodic coating specification compliance at plant is unresolved,

contractors/ suppliers must commission an approved Independent Inspection Authority to

carry out site acceptance inspections.

•	 Acceptance inspections: Carry out in accordance with BS 6001-2 with a limiting quality of

5% where the probability of acceptance is 10%. Each component of a fabricated unit will

be assessed as an individual part for sampling procedures.

•	 Components failing inspection: Remove and reprocess/ replace.

270	COMPONENT DESIGN

•	 Condition of components to be anodized:

-	To comply with relevant recommendations of BS 4479-1, and -5.

-	Of suitable size to fit plant capacity.

310	PRETREATMENT

•	 Condition of components to be anodized:

-	Free from corrosion and damage.

-	Suitable for and compatible with the pre-treatment and anodizing process.

•	 Process: In accordance with the specification requirements for the finish.

410	EXTENT OF ANODIC COATINGS

•	 Application: To visible component surfaces, and concealed surfaces requiring protection.

Coated surfaces will be deemed 'significant surfaces' for relevant BS 3987 performance

requirements.

420	APPLICATION OF ANODIC COATINGS

•	 Surfaces to receive anodic coatings: Clean.

•	 Jig points: To be agreed. Not on visible areas of anodic coated components.

•	 Use of touch-up paint: Not acceptable.

430	PERFORMANCE AND APPEARANCE OF ANODIC COATINGS

•	 Standard: To BS 3987.

•	 Visual inspection after anodizing: Significant surfaces to be free from visible coating/

defects when viewed from a distance of not less than 5 m for external and 3 m for internal

applications.

440	FABRICATIONS

•	 Units may be assembled:

-	Before anodizing, subject to satisfactory drainage.

-	From components anodized after cutting to size.

Where approved, from components anodized before cutting to size.

450	FABRICATION DAMAGE REPAIR/ REPLACEMENT

•	 Inspection: Check all components before delivery to site for damage to anodic coatings.

Submit proposals for repair or replacement.

510	PROTECTION

•	 Anodic coated surfaces of components: Protect from damage during handling and

installation, or by subsequent site operations.

•	 Protective coverings: Must be:

-	Resistant to weather conditions.

-	Partially removable to suit building in and access to fixing points.

•	 Protective tapes in contact with anodizing: Must be:

-	Low tack, self adhesive and light in colour.

-	Applied and removed in accordance with tape and anodizers recommendations.

•	 Inspection of protection: Carry out monthly. Promptly repair any deterioration or deficiency.

520	SITE DAMAGE REPAIR/ REPLACEMENT

•	 Damage to anodic coatings: Rectify immediately damage caused during handling and

installation, or by subsequent site operations. Submit proposals for extensive repair or

replacement.

530	DOCUMENTATION

•	 Submit the following information for each batch of anodic coated components:

-	Supplier.

-	Trade name.

-	Colour (if required).

-	Batch and reference number.

-	Statutory requirements.

540	COMPLETION

•	 Cleaning and maintenance of anodic coated surfaces: Carry out in accordance with

procedures detailed in the anodizer's guarantees.

SECTION 2

CIVIL/STRUCTURAL SPECIFICATION

D20	EXCAVATING AND FILLING

To be read with Preliminaries/ General conditions.

GENERALLY/ THE SITE

D20/110	SITE INVESTIGATION

-	Report: See report by Hanmar Ltd

D20/145	VARIATIONS IN GROUND WATER LEVEL

-	Give notice: If levels encountered are significantly different from levels in the site investigation report or previously measured.

D20/150	EXISTING SERVICES

-	Services: See section A12 for locations.

CLEARANCE/ EXCAVATING

168	SITE CLEARANCE:
Timing: Before topsoil stripping.
General: Clear site of rubbish, debris and vegetation to ensure that topsil is not contaminated during stripping. Do not compact topsoil.

D20/170	REMOVING SMALL TREES, SHRUBS, HEDGES AND ROOTS

-	Small trees, shrubs and hedges: Cut down

-	Roots: Grub up and dispose of without undue disturbance of soil and adjacent areas

-	Safety: Comply with HSE/ Arboriculture and Forestry Advisory Group Safety Guides.

D20/220	STRIPPING TOPSOIL

General: Before beginning general excavation or filling, strip topsoil from areas where there will be re-grading, buildings, paving, roads and other areas shown on drawings. 
-  Remove to an average depth of 200mm
-  Give notice where the depth of topsoil is difficult to determine.
Handling: Handle topsoil for reuse or sale in accordance with clause 225.
Around trees: Do not remove topsoil from below the spread of trees or round hedges which are to be retained.
Site storage: In an area to be decided by the Contractor within the confines of the site.

D20/225	HANDLING TOPSOIL

Earthmoving equipment: Select and use to minimize disturbance, trafficking and compaction.
Contamination: Do not mix topsoil with:
-  Subsoil, stone, hardcore, rubbish or material from demolition work.
-  Oil, fuel, cement or other substances harmful to plant growth.
-  Other grades of topsoil.
Multiple handling: Keep to a minimum. Use topsoil immediately after stripping.
Wet conditions: Handle topsoil in the driest condition possible. Do not handle during or after heavy rainfall or when it is wetter than the plastic limit as defined by BS 3882, Annex N2.

D20/240	ADJACENT EXCAVATIONS

-	Proximity: Where an excavation encroaches below a line drawn at an angle from the nearest formation level of another higher excavation, the lower excavation, all work within it and backfilling thereto must be completed before the higher excavation is made.

-	Angle of line from horizontal: 450

D20/250	PERMISSIBLE DEVIATIONS FROM FORMATION LEVELS

-	Beneath mass concrete foundations: ±25 mm.

-	Beneath ground bearing slabs and r.c. foundations: ±15 mm.

-	Embankments and cuttings: ±50 mm.

-	Ground abutting external walls: ±50 mm, but such as to ensure that finished level is not less than 150 mm below dpc.

D20/260	INSPECTING FORMATIONS

-	Give notice: Make advance arrangements for inspection of formations for trench fill foundations and strip foundations.

-	Preparation: Just before inspection remove the last 150 mm of excavation. Trim to required profiles and levels, and remove loose material.

-	Seal: Within 4 hours of inspection, seal formations with either concrete or mudmat.

D20/270	FOUNDATIONS GENERALLY

-	Give notice if:

-	A natural bearing formation of undisturbed subsoil is not obtained at the depth shown on the drawings.

-	The formation contains soft or hard spots or highly variable material.

D20/280	TRENCH FILL FOUNDATIONS

-	Excavation: Form trench down to formation in one operation.

-	Safety: Prepare formation from ground level.

-	Inspection of formations: Give notice before commencing excavation.

-	Period of notice: 24 hours

-	Shoring: Where inspection of formation is required, provide localised shoring to suit ground conditions.

-	Concrete fill: Place concrete immediately after inspection and no more than four hours after exposing the formation.

D20/290	FOUNDATIONS IN MADE UP GROUND

-	Depth: Excavate down to a natural formation of undisturbed subsoil.

-	Discrepancy: Give notice if this is greater or less than depth given.

D20/310	UNSTABLE GROUND

-	Generally: Ensure that the excavation remains stable at all times.

-	Give notice: Without delay if any newly excavated faces are too unstable to allow earthwork support to be inserted.

-	Take action: If instability is likely to affect adjacent structures or roadways, take appropriate emergency action.

D20/320	RECORDED FEATURES

-	Recorded foundations, beds, drains, manholes, etc: Break out and seal drain ends.

-	Contaminated earth: Remove and disinfect as required by local authority.

D20/330	UNRECORDED FEATURES

-	Give notice: If unrecorded foundations, beds, voids, basements, filling, tanks, pipes, cables, drains, manholes, watercourses, ditches, etc. not shown on the drawings are encountered.

D20/350	EXISTING WATERCOURSES

-	Diverted watercourses which are to be filled: Before filling, remove vegetable growths and soft deposits.

D20/360	EXCESS EXCAVATION

-	Excavation taken deeper than required:

-	Backfill with C8/10 lean mix concrete

DISPOSAL OF MATERIALS

410	EXCAVATED TOPSOIL STORAGE:
Storage: Stockpile in temporary storage heaps not exceeding 3 metres high.

D20/450	WATER

-	Generally: Keep all excavations free from water until:

-	Formations are covered.

-	Below ground construction are completed.

-	Basement structures and retaining walls are able to resist leakage, water pressure and flotation.

-	Drainage: Form surfaces of excavations and fill to provide adequate falls.

-	Removal of water: Provide temporary drains, sumps and pumping as necessary. Do not pollute watercourses with silt laden water.

D20/454	GROUND WATER LEVEL/ RUNNING WATER

-	Give notice: If it is considered that the excavations are below the water table.

-	Springs/ Running water: Give notice immediately if encountered.

D20/457	PUMPING

-	General: Do not disturb excavated faces or stability of adjacent ground or structures.

-	Pumped water: Discharge without flooding the site or adjoining property.

-	Sumps: Construct clear of excavations. Fill on completion.

FILLING

D20/500	PROPOSED FILL MATERIALS

-	Details: Submit full details of proposed fill materials to demonstrate compliance with specification, including:

-	Type and source of imported fill.

-	Proposals for processing and reuse of material excavated on site.

-	Test reports as required elsewhere.

Timing:  One week before use

D20/510	HAZARDOUS, AGGRESSIVE OR UNSTABLE MATERIALS

-	General: Do not use fill materials which would, either in themselves or in combination with other materials or ground water, give rise to a health hazard, damage to building structures or instability in the filling, including material that is:

-	Frozen or containing ice.

-	Organic.

-	Contaminated or noxious.

-	Susceptible to spontaneous combustion.

-	Likely to erode or decay and cause voids.

-	With excessive moisture content, slurry, mud or from marshes or bogs.

-	Clay of liquid limit exceeding 80 and/or plasticity index exceeding 55.

-	Unacceptable, class U2 as defined in the Highways Agency ‘Specification for highway works’, clause 601.

D20/520	FROST SUSCEPTIBILITY

-	General: Except as allowed below, fill must be non frost-susceptible as defined in Highways Agency ‘Specification for highway works’, clause 801.17.

-	Test reports: If the following fill materials are proposed, submit a laboratory report confirming they are non frost-susceptible:

-	Fine grained soil with a plasticity index less than 20%.

-	Coarse grained soil or crushed granite with more than 10% retained on a 0.063 mm sieve.

-	Frost-susceptible fill: May only be used within the external walls of buildings below spaces that will be heated. Protect from frost during construction.

D20/525	TESTING OF SUITABILITY OF FILL MATERIALS BEFORE START OF FILLING

-	Laboratory: NAMAS accredited.

-	Submit report to: Engineer

D20/530	PLACING FILL

-	Excavations and areas to be filled: Free from loose soil, rubbish and standing water.

-	Freezing conditions: Do not place fill on frozen surfaces. Remove material affected by frost. Replace and re-compact if not damaged after thawing.

-	Adjacent structures, membranes and buried services:

-	Do not overload, destabilise or damage.

-	Submit proposals for temporary support necessary to ensure stability during filling.

-	Allow 14 days (minimum) before backfilling against in situ concrete structures.

-	Layers: Place so that only one type of material occurs in each layer.

-	Earthmoving equipment: Vary route to avoid rutting.

D20/535	COMPACTION

-	General: Compact fill as soon as possible after placing.

-	After compaction: Surface of each layer must be well closed, showing no movement under compaction plant, and without cracks, holes, ridges, loose material and the like.

-	Defective areas: Remove and re-compact to full thickness of layer using new material.

D20/540	BENCHING IN FILL

-	Adjacent areas: If, during filling the difference in level between adjacent areas of filling exceeds 600 mm, cut into edge of higher filling to form benches 600 mm minimum width and height equivalent to depth of a layer of compacted filling.

-	New filling: Spread and compact to ensure maximum continuity with previous filling.

D20/550	GEOTEXTILE SHEET

Manufacturer:  Terram Ltd

-  Product reference:  Terram 1000
  Jointing: to manufacturer’s recommendations
Preparation of subgrade:  Leave smooth with no sharp or angular protrusions

Protect from:
-  Exposure to light.
-  Contaminants.
-  Materials listed as potentially deleterious by geotextile manufacturer.
-  Wind uplift.

D20/610	COMPACTED FILLING FOR LANDSCAPE AND GARDEN AREAS

Fill: Material capable of compaction by light earthmoving plant.
Filling:  Layers not more than 200 mm thick. Lightly compact each layer to produce a stable soil structure.

D20/617	HIGHWAYS AGENCY TYPE 1 GRANULAR FILLING

-	Fill: To Highways Agency ‘Specification for highway works’, clause 803:

-	Crushed rock (other than argillaceous rock).

-	Crushed concrete.

-	Recycled aggregates.

-	Filling: To Highways Agency ‘Specification for highway works’, clauses 801.3 and 802.

D20/618	HIGHWAYS AGENCY TYPE 2 GRANULAR FILLING

-	Fill: To Highways Agency ‘Specification for highway works’, clause 804:

-	Crushed rock (other than argillaceous rock).

-	Crushed concrete.

-	Natural gravel.

-	Natural sand.

-	Filling: To Highways Agency ‘Specification for highway works’, clauses 801.3 and 802.

D20/620	SUBGRADE IMPROVEMENT LAYER (CAPPING)

-	Fill: To Highways Agency ‘Specification for highway works’, Table 6/1, Class 6F1 or 6F2.

-	Filling: Place and compact to Highways Agency ‘Specification for highway works’, Table 6/1, clause 612 and clause 613.3, 613.9 and 613.10.

D20/625	COMPACTED GENERAL FILLING/ EARTHWORKS

-	Specification: Highways Agency ‘Specification for highway works’, Earthworks section, clause 612 Table 6/1 and Appendices 900 – 960 in this section.

-	Definition: References to the ‘Overseeing Organisation’ are deemed to be to the issuer of this specification.

626	COMPACTED GENERAL FILLING:
Fill:  Selected excavated material.
Excavated material: Select suitable material and keep separate.
Filling: Spread and level material in layers. As soon as possible thoroughly compact each layer.
Proposals: Well in advance of starting work submit details of proposed:
-  Materials to be used, including quantities of each type.
-  Type of plant.
-  Maximum depth of each compacted layer.
-  Minimum number of passes per layer.

D20/700	BACKFILLING AROUND FOUNDATIONS

-	Under oversite concrete and pavings: Hardcore.

-	Under grassed or soil areas: Material excavated from the trench, laid and compacted in 300 mm maximum layers.

D20/710	HARDCORE FILLING

-	Fill: Granular material, free from excessive dust, well graded, all pieces less than 75 mm in any direction, minimum 10% fines value of 50 kN when tested in a soaked condition to BS 812-111, and in any one layer only one of the following:

-	Crushed rock (other than argillaceous rock) or quarry waste with not more binding material than is required to help hold the stone together.

-	Crushed concrete, crushed brick or tile, free from plaster, timber and metal.

-	Gravel or hoggin with not more clay content than is required to bind the material together, and with no large lumps of clay.

-	Natural gravel.

-	Natural sand.

-	Filling: Spread and level in 150 mm maximum layers. Thoroughly compact each layer.

D20/715	VENTING HARDCORE LAYER

-	Fill: Clean granular material, well graded, passing a 75 mm BS sieve but retained on a 20 mm BS sieve. In each layer only one of the following:

-	Crushed hard rock.

-	Crushed concrete, crushed brick or tile, free from plaster, timber and metal.

-	Gravel.

-	Filling: Spread and level in 150 mm maximum layers. Thoroughly compact each layer whilst maintaining enough voids to allow efficient venting.

D20/730	BLINDING

-	Surfaces to receive sheet overlays or concrete:

-	Blind with:

-	Concrete where shown on drawings; or

-	Sand, fine gravel, or other approved fine material applied to fill interstices. Moisten as necessary before final rolling to provide a flat, closed, smooth surface.

-	Sand for blinding: To BS EN 12620, grade 0/4 or 0/2 (MP).

-	Permissible deviations on surface level: +0 -25 mm.

HIGHWAYS AGENCY EARTHWORKS SPECIFICATION APPENDICES

D20/900	APPENDIX 6/1 – REQUIREMENTS FOR ACCEPTABILITY AND TESTING ETC. OF EARTHWORKS MATERIALS

D20/905	APPENDIX 6/2 – REQUIREMENTS FOR DEALING WITH CLASS U2 UNACCEPTABLE MATERIAL

D20/910	APPENDIX 6/3 – REQUIREMENTS FOR EXCAVATION, DEPOSITION, COMPACTION (OTHER THAN DYNAMIC COMPACTION)

D20/915	APPENDIX 6/4 – REQUIREMENTS FOR CLASS 3 MATERIAL

D20/920	APPENDIX 6/5 – GEOTEXTILES USED TO SEPARATE EARTHWORKS MATERIALS

D20/925	APPENDIX 6/6 – FILL TO STRUCTURES AND FILL ABOVE STRUCTURAL FOUNDATIONS

D20/930	APPENDIX 6/7 – SUB-FORMATION AND CAPPING AND PREPARATION AND SURFACE TREATMENT OF FORMATION

D20/935	APPENDIX 6/8 – TOPSOILING, GRASS SEEDING AND TURFING

D20/940	APPENDIX 6/9 – EARTHWORK ENVIRONMENTAL BUNDS, LANDSCAPE AREAS, STRENGTHENED EMBANKMENTS

D20/945	APPENDIX 6/10 – GROUND ANCHORAGES, CRIB WALLING AND GABIONS

D20/950	APPENDIX 6/11 – SWALLOW HOLES AND OTHER NATURALLY OCCURRING CAVITIES AND DISUSED MINE WORKINGS

D20/955	APPENDIX 6/12 – INSTRUMENTATION AND MONITORING

D20/960	APPENDIX 6/13 – GROUND IMPROVEMENT

E05	IN SITU CONCRETE CONSTRUCTION GENERALLY

To be read with Preliminaries/ General conditions.

E05/300	LEVELS OF STRUCTURAL CONCRETE FLOORS

-	Tolerances: See Preliminaries section A33.

E05/310	SURFACE REGULARITY OF CONCRETE FLOORS - GENERAL

-	Surface deviation: Sudden irregularities not permitted.

-	Measurement: From underside of a straightedge (between points of contact) placed anywhere on surface and using a slip gauge to BS 8204-1 or -2 (or equivalent).

E05/312	SURFACE REGULARITY OF FLOORS - WEARING SURFACES

-	Maximum permissible deviation when measured as clause 310:

-	5 mm under a 3 m straightedge.

-	2 mm under a 1 m straightedge.

E05/314	SURFACE REGULARITY OF FLOORS - SURFACES TO RECEIVE SCREEDS/ BEDS

-	Maximum permissible deviation when measured as clause 310:

-	Screeds/ beds up to 50 mm thick: 10 mm under a 3 m straightedge.

E10	MIXING/ CASTING/ CURING IN SITU CONCRETE

To be read with Preliminaries/ General conditions.

CONCRETE

E10/101	SPECIFICATION

-	Concrete generally: To BS 8500-2.

-	Exchange of information: Provide concrete producer with information required by BS 8500-1, clauses 4 and 5.

E10/130	NORMAL DESIGNED CONCRETE FOR FOUNDATIONS, SLABS, GROUND BEAMS etc

-	Embedded metal: refer to section E30 of specification

-	Compressive strength class (cylinder/ cube minimum): C28/35 N/mm2.

-	Aggregates:

-	Size (maximum): 20mm.

-	Coarse aggregates: to B.S. 882.

-	Sand: to B.S. 882.

-	Limiting values for composition:

-	Water/cement ratio (maximum): 0.6.

-	Cement/ combination content (minimum): 300kg/m3 .

-	Cement: Ordinary Portland.

-	Maximum total percentage of chloride ions by mass of cement: 0.4% .

-	Admixtures: none

-	Information to be provided by the producer: As BS 5328: Part3, Clause 3.

Sampling and testing in accordance with clause 510.

E10/131	NORMAL DESIGNED CONCRETE FOR LINTELS, MANHOLE COVER SLABS, etc

-	Embedded metal: refer to section E30 of specification

-	Compressive strength class (cylinder/ cube minimum): C28/35 N/mm2.

-	Aggregates:

-	Size (maximum): 10mm.

-	Coarse aggregates: to B.S. 882.

-	Sand: to B.S. 882.

-	Limiting values for composition:

-	Water/cement ratio (maximum): 0.65.

-	Cement/ combination content (minimum): 315kg/m3.

-	Cement: Ordinary Portland.

-	Maximum total percentage of chloride ions by mass of cement: 0.4% .

-	Admixtures: none.

-	Information to be provided by the producer: As BS 5328: Part3, Clause 3.

Sampling and testing in accordance with clause 510.

E10/132	NORMAL DESIGNED CONCRETE FOR MUD MAT, CAVITY FILL, FILLING ETC.

-	Compressive strength class (cylinder/ cube minimum): C8/10 N/mm2.

-	Aggregates:

-	Size (maximum): 20mm.

-	Coarse aggregates: to B.S. 882.

-	Sand: to B.S. 882.

-	Limiting values for composition:

-	Water/cement ratio (maximum): 0.85.

-	Cement/ combination content (minimum): 180kg/m3.

-	Cement: Ordinary Portland.

-	Maximum total percentage of chloride ions by mass of cement: 0.4% .

-	Admixtures: none.

-	Information to be provided by the producer: As BS 5328: Part3, Clause 3.

Sampling and testing in accordance with clause 510.

E10/150	PRESCRIBED CONCRETE MIX FOR FLOOR SCREEDS

-	Source of prescribed concrete: mixed using forced action mixer.

-	Fibres: Defribrillated Polypropylene Fibres

-	Aggregates:

-	Size (maximum): 6mm (single size crushed rock)

-	Type/ Density: normal

-	Coarse aggregates: to B.S.882 .

-	Fine aggregate grading: sharp sand to B.S. 882.

-	Cement/ combinations: ordinary Portland.

-	Standard strength class: PC42.5.

-	Mix proportions:

-	Cement/ combination content: 1 part

-	Coarse aggregate: 1.5 parts

-	Fine aggregate: 3 parts

-	Water: 100litres/m3

MATERIALS, BATCHING AND MIXING

E10/215	READY-MIXED CONCRETE must be used for all structural concrete.

-	Production plant: Currently certified by a body accredited by UKAS to BS EN 45011 for product conformity certification of ready-mixed concrete, or meeting the requirements of the NACCB, Category 2 for product conformity.

-	Source of ready-mixed concrete: Obtain from one source unless otherwise approved.

-	Name and address of depot: Submit before any concrete is delivered.

-	Delivery notes: Retain for inspection.

-	Declarations of nonconformity from concrete producer: Notify immediately.

- CEMENTS

The following abbreviations apply;

PC42.5 Portland cement, Class 42.5 (in lieu of OPC)

E10/221	INFORMATION ABOUT PROPOSED CONCRETES

-	Submit when requested:

-	Details listed in BS 8500-1, clause 5.2.

E10/230	INTERRUPTION OF SUPPLY DURING CONCRETING

-	Elements without joints: Where elements are detailed to be cast in a single pour without joints, make prior arrangements for a back-up supply of concrete.

-	Elsewhere:

-	Preparation: Manage pour to have a full face, and have materials available to form an emergency construction joint while concrete can still be worked.

-	Before pour is completed: Submit location and details of joint, make proposals for joint preparation.

E10/305	NATURAL AGGREGATES FOR DESIGNED / PRESCRIBED MIXES:

-	To give a drying shrinkage of concrete not exceeding 0.075% when tested to B.S.:812 Part 120.

E10/355	RISK OF ALKALI SILICA REACTION IN DESIGNED / PRESCRIBED MIXES:

-	Take one of the precautions specified for Designed mixes in clause 5.5.7 of BS 5328: Part 2. Inform CA if this necessitates a change in specification. Submit evidence of compliance to CA before making concrete for use in the Works.

E10/415	ADMIXTURES

- Calcium chloride and admixtures containing calcium chloride: Do not use.

- To BS 5075

- Use only if approved, and then in accordance with manufacturers recommendations.

- Ensure that admixtures are compatible with all other materials, including other admixtures.

E10/429	NON FERROUS FIBRES

-	Requirement: crack control in screeds.

-	Material: Defibrillated polypropylene fibres.

-	Addition rate 0.9kg/m3.

-	Dispersion in fresh concrete: Uniform without balling.

E10/490	PROPERTIES OF FRESH CONCRETE

- Adjustments to suit construction process: Determine with concrete producer. Maintain conformity to the specification.

PROJECT TESTING/ CERTIFICATION

E10/505	PROJECT TESTING OF CONCRETE

-	Testing: To BS EN 206-1, Annex B and BS 8500-1, Annex B.

-	Nonconformity: Obtain instructions immediately.

-	Recording: Maintain complete correlated records including:

-	Concrete designation.

-	Sampling, site tests, and identification numbers of specimens tested in the laboratory.

-	Location of the parts of the structure represented by each sample.

-	Location in the structure of the batch from which each sample is taken.

E10/508	REGULAR PROJECT TESTING

-	Tests: Cube tests (compressive strength testing required).

-	Sampling:

-	Point: Take samples from ready mix lorry chute at dispatch point on site, part way through load discharge.

-	Rate: For compressive strength testing: take one sample per every 6 cu m but not more than 3 samples per day.

-	Other requirements: Information to be provided by the producer: As BS5328: Part 3, clause 3.

E10/520	TESTING LABORATORY

-	Laboratory: Accredited by UKAS / NAMAS or other national equivalent.

-	Name and UKAS reference number: Submit well in advance of making trial mixes or concrete for use in the works.

E10/530	TESTS RESULTS

-	Submission of reports: Within one day of completion of each test.

-	Number of copies: 1 copy of reports to be dispatched to the engineer.

-	Reports on site: A complete set, available for inspection.

E10/550	BROKEN CUBES FROM FAILED STRENGTH TESTS

-	Nonconformity: Keep separately the pieces of each cube which fail to meet the conformity requirements for individual results.

-	Period for keeping cubes: Obtain instructions.

E10/580	FAILURES

If a concrete sample fails to achieve specified criteria or to pass specified tests, inform the CA without delay and submit:

Confirmation of the validity of the test results, and/or

Proposals  for further tests to assess the strength of the concrete in the structure, as set out in BS 6089, and/or

Proposals for rectification.

Obtain approval of all such evidence and proposals before proceeding. The CA may issue instructions for the work to be stopped or delayed until reasons for the failure have been established, possible consequences assessed, and appropriate preventative and remedial measures taken.

E10/581	FAILURES

Where ever the specified sampling, testing and compliance procedures show that a concrete mix is not in accordance with the specification(even if the work is eventually accepted), and measures are taken to help establish whether or not the work is acceptable, such measures:

Will be at the expense of the contractor, and will not be considered as grounds for an extension in time.

PLACING AND COMPACTING

E10/620	TEMPERATURE OF CONCRETE

-	Application: pouring during summer months.

-	Objective: Limit maximum temperature of concrete to minimize cracking during placing, compaction and curing. Take account of:

-	High temperatures and steep temperature gradients: Prevent build-up during first 24 hours after casting. Prevent coincidence of maximum heat gain from cement hydration with high air temperature and/ or solar gain.

-	Rapid changes in temperature: Prevent during the first seven days after casting.

E10/630	PREMATURE WATER LOSS

-	Requirement: Prevent water loss from concrete laid on absorbent substrates.

-	Underlay: Select from:

Polyethylene sheet: 250 micrometres thick.

Building paper: To BS 1521, grade B1F.

-	Installation: Lap edges 150 mm.

E10/640	CONSTRUCTION JOINTS

-	Location of joints: submit details of proposed locations and obtain approval before proceeding.

-	Preparation of joint surfaces: carefully brush and spray surface while concrete is still green to remove surface laitance and expose aggregate finish. Obtain approval for any alternative method. Surface to be clean and damp when fresh concrete is placed against it.

E10/648	ADVERSE TEMPERATURE CONDITIONS

-	Requirement: Submit proposals for protecting concrete when predicted ambient temperatures indicate risk of concrete freezing or overheating.

E10/650	SURFACES TO RECEIVE CONCRETE

-	Cleanliness of surfaces immediately before placing concrete: Clean with no debris, tying wire clippings, fastenings or free water.

E10/660	INSPECTION OF SURFACES

-	Notice: Give notice to allow inspections of reinforcement and surfaces before each pour of concrete.

-	Period of notice: Obtain instructions.

E10/670	TRANSPORTING

-	General: Avoid contamination, segregation, loss of ingredients, excessive evaporation and loss of workability. Protect from heavy rain.

-	Entrained air: Anticipate effects of transport and placing methods in order to achieve specified air content.

E10/680	PLACING

-	Records: Maintain for time, date and location of all pours.

-	Timing: Place as soon as practicable after mixing and while sufficiently plastic for full compaction.

-	Temperature limitations for concrete: 30°C (maximum) and 5°C (minimum), unless otherwise specified. Do not place against frozen or frost covered surfaces.

-	Continuity of pours: Place in final position in one continuous operation up to construction joints. Avoid formation of cold joints.

-	Discharging concrete: Prevent uneven dispersal, segregation or loss of ingredients or any adverse effect on the formwork or formed finishes.

-	Thickness of layers: To suit methods of compaction and achieve efficient amalgamation during compaction.

-	Poker vibrators: Do not use to make concrete flow horizontally into position, except where necessary to achieve full compaction under void formers and cast-in accessories and at vertical joints.

E10/690	COMPACTING

-	General: Fully compact concrete to full depth to remove entrapped air. Continue until air bubbles cease to appear on the top surface.

-	Areas for particular attention: Around reinforcement, under void formers, cast-in accessories, into corners of formwork and at joints.

-	Consecutive batches of concrete: Amalgamate without damaging adjacent partly hardened concrete.

-	Methods of compaction: To suit consistence class and use of concrete.

E10/720	VIBRATORS

-	General: Maintain sufficient numbers and types of vibrator to suit pouring rate, consistency and location of concrete.

-	External vibrators: Obtain approval for use.

E10/730	PLASTIC SETTLEMENT

-	Settlement cracking: Inspect fresh concrete closely and continuously wherever cracking is likely to occur, including the top of deep sections and at significant changes in the depth of concrete sections.

-	Timing: During the first few hours after placing and whilst concrete is still capable of being fluidized by the vibrator.

-	Removal of cracks: Revibrate concrete.

E10/810	CURING GENERALLY

-	Requirement: Keep surface layers of concrete moist throughout curing period, including perimeters and abutments, by either restricting evaporation or continuously wetting surfaces of concrete.

-	Surfaces covered by formwork: Retain formwork in position and, where necessary

to satisfy curing period, cover surfaces immediately after striking.

-	Top surfaces: Cover immediately after placing and compacting. If covering is removed for finishing operations, replace it immediately afterwards.

-	Surface temperature: Maintain above 5°C throughout the specified curing period or four days, whichever is longer.

-	Records: Maintain details of location and timing of casting of individual batches, removal of formwork and removal of coverings. Keep records on site, available for inspection.

E10/811	COVERINGS FOR CURING

-	Sheet coverings: Suitable impervious material.

-	Curing compounds: Selection criteria:

-	Curing efficiency: Not less than 75% or for surfaces exposed to abrasion 90%.

-	Colouring: Fugitive dye.

-	Application to concrete exposed in the finished work: Readily removable without disfiguring the surface.

-	Application to concrete to receive bonded construction/ finish: No impediment to subsequent bonding.

-	Interim covering to top surfaces of concrete: Until surfaces are in a suitable state to receive coverings in direct contact, cover with impervious sheeting held clear of the surface and sealed against draughts at perimeters and junctions.

E10/812	PREVENTING EARLY AGE THERMAL CRACKING

-	Deep lifts or large volume pours: Submit proposals for curing to prevent early age thermal cracking, taking account of:

-	Temperature differentials across sections.

-	Coefficient of thermal expansion of the concrete.

-	Strain capacity of the concrete mix (aggregate dependent).

-	Restraint.

E10/820	CURING PERIODS

-	General: Curing periods are in days (minimum).

-	Definition of 't': The average number of degrees Celsius air temperature during the curing period.

-	Curing periods for concrete surfaces which, in the finished building, will be exposed to the elements; concrete wearing surface floors and pavements; water resistant concrete:

Concrete made	Concrete made

using CEM1	using cements

strength class  	indicated in

42.5;	BS 8500, table

A.17 except those

listed in adjacent

column and

supersulfated cement

_______________________________________________________

Drying winds or dry,	140	180

sunny weather	t+10	t+10

(relative humidity

< 50%)

___________________________________________________________

Intermediate	100	140

conditions	t+10	t+10

_______________________________________________________

Damp weather, 	100	100

protected from sun 	t+10	t+10

and wind (relative

humidity > 80%)

_______________________________________________________

-	Curing periods for other structural concrete surfaces (cements/

combinations as above):

_______________________________________________________

Drying winds or dry,	80	140

sunny weather	t+10	t+10

(relative humidity

< 50%)

Intermediate	60	80

conditions	t+10	t+10

Damp weather	No special	No special

protected from sun	requirements	requirements

and wind (relative

humidity > 80%)

_______________________________________________________

-	Curing periods for concretes using admixtures or other types of

cements/ combinations: Submit proposals.

E10/821	CURING PERIODS, in days:

-	Concrete surfaces which in the finished building will be exposed to the elements; concrete wearing surface floors and pavements; watertight concrete:

|  |  | Concrete made using PC42.5, | Concrete made using PPFAC, PBFC, HSBC, Pfa,ggbs |
| --- | --- | --- | --- |
|  | November to April May to October | 10 7 | 12 10 |

-	Other structural concrete surfaces: No special requirements if in damp weather and protected from sun and wind, otherwise as follows (cements as above):

|  | November to April May to October | 6 4 | 10 7 |
| --- | --- | --- | --- |

-	Obtain prior approval for curing periods for mixes using admixtures or other types of cement.

E10/822	CURING PERIODS, not less than:

-	Surfaces which in the finished building will be

exposed to the elements, and wearing

surfaces of floors and pavements,

regardless of weather conditions		10 days

-	Other structural concrete surfaces	5 days

E10/840	PROTECTION

-	Prevent damage to concrete, including:

-	Surfaces generally: From rain, indentation and other physical damage.

-	Surfaces to exposed visual concrete: From dirt, staining, rust marks and other disfiguration.

-	Immature concrete: From thermal shock, physical shock, overloading, movement and vibration.

-	In cold weather: From entrapment and freezing expansion of water in pockets, etc.

E20	FORMWORK FOR IN SITU CONCRETE

To be read with Preliminaries/ General conditions.

GENERALLY/ PREPARATION

E20/110	LOADINGS

-	Requirement: Design and construct formwork to withstand the worst combination of the following:

-	Total weight of formwork, reinforcement and concrete.

-	Construction loads including dynamic effects of placing, compacting and construction traffic.

-	Wind and snow loads.

E20/170	WORK BELOW GROUND

-	Casting vertical faces of footings, bases and slabs against faces of excavation: Submit proposals and obtain consent, it is unlikely that ground conditions will be suitable in this scheme.

-	Casting walls against faces of excavation: Use formwork on both sides.

E20/190	SUBSTRUCTURE FORMWORK FOR SLABS / FOUNDATIONS IF REQUIRED

-	Contractor to submit details for approval; suitable formwork would be block work walling, constructed on mud-matt covered formation, or timber form work construction using plywood of adequate quality and rigidity to provide true finish to beams, or proprietary formwork such as permaform. Form work must be straight plumb, and rigid, with all joints sealed to prevent grout loss. Specified cover must be provided in all locations.

E20/200	PROPRIETARY GROUND FLOOR INSULATION

Insulation placed on top of suspended ground floor slab, between slab and screed. Insulation to Architects requirements (refer to separate section of specification)

CONSTRUCTION

E20/310	ACCURACY

-	General requirement for formwork: Accurately and robustly constructed to produce finished concrete in the required positions and to the required dimensions.

-	Formed surfaces: Free from twist and bow (other than any required cambers).

-	Intersections, lines and angles: Square, plumb and true.

E20/320	JOINTS IN FORMS

-	Requirements including joints in form linings and between forms and completed work:

-	Prevent loss of grout, using seals where necessary.

-	Prevent formation of steps. Secure formwork tight against adjacent concrete.

E20/330	INSERTS, HOLES AND CHASES

-	Positions and details: Submit proposals.

-	Positioning relative to reinforcement: Give notice of any conflicts well in advance of placing concrete.

-	Method of forming: Fix inserts or box out as required. Do not cut hardened concrete without approval.

E20/340	KICKERS

-	Method statement: Submit proposals including means of achieving quality of concrete consistent with that specified for the column or wall.

-	Kicker height (minimum): 75 mm.

E20/350	FORM TIES

-	Metal associated with form ties/ devices: Prohibited within cover to reinforcement. Compatible with reinforcement metal.

E20/351	PROHIBITION OF FORM TIES

-	Do not use ties in the following work:

Lintels.

E20/470	RELEASE AGENTS

-	General: Achieve a clean release of forms without disfiguring the concrete surface.

-	Product types: Compatible with formwork materials, specified formed finishes and subsequent applied finishes. Use the same product throughout the entire area of any one finish.

-	Protection: Prevent contact with reinforcement, hardened concrete, other materials not part of the form face, and permanent forms.

E20/480	SURFACE RETARDERS

-	Use: Obtain approval.

-	Reinforcement: Prevent contact with retarder.

STRIKING

E20/510	STRIKING FORMWORK

-	Timing: Prevent any disturbance, damage or overloading of the permanent structure.

E20/520	MINIMUM PERIODS:

-	The following periods (in days) for retaining formwork in position before striking apply to class 42.5 or sulphate- resisting Portland cement concrete with no cement replacement materials or admixtures:

|  | Type of formwork | Average mean of daily minimum and maximum air temperatures during the period |  |  |
| --- | --- | --- | --- | --- |
|  |  | 16xºC | 7xºC | 3xºC |  |
|  | Vertical formwork to columns, walls and beams | 0.5 | 75 | 1 |  |
|  | Soffit forms to slabs | 4 | 6 | 8 |  |
|  | Props to slabs and soffit forms to beams | 10 | 15 | 20 |  |
|  | Props to beams | 14 | 21 | 28 |  |

-	Submit details of proposed periods for mixes using admixtures or other types of cement.

E20/521	MINIMUM PERIODS: Alternative methods of determining minimum periods for retaining formwork in position may be submitted for approval. Accept responsibility for cost of checking of proposals by CA and for any testing.

FORMED FINISHES

E20/600	SAMPLES OF FINISHES AVAILABLE FOR INSPECTION

-	Samples available for inspection: initial sample pour must be carried out for all elements of insitu concrete work for inspection by engineer to confirm acceptability of standard of workmanship, which must then be maintained throughout scheme.

E20/610	BASIC FINISH

-	no particular requirements, except those for tolerances and full compaction.

E20/615	FINISH TO RECEIVE TANKING

-	Finish: Even and suitable to receive a tanking membrane.

-	Permissible deviation of surfaces:

-	Sudden irregularities (maximum): 3 mm.

-	Gradual irregularities when measured from underside of a 1 m straight edge, placed anywhere on surface (maximum): 3 mm.

-	Surface blemishes:

-	Permitted: Blowholes less than 10 mm in diameter.

-	Not permitted: Voids, honeycombing, segregation and other large defects.

-	Projecting fins: Remove.

-	Formwork tie holes: Filled with mortar.

E20/620	PLAIN SMOOTH FINISH

-	Finish: Even with panels arranged in a regular pattern as a feature of the surface.

-	Permissible deviation of surfaces:

-	Sudden irregularities (maximum): 5 mm.

-	Gradual irregularities when measured from the underside of a 1 m straightedge, placed anywhere on surface (maximum): 5 mm.

-	Variations in colour:

-	Permitted: Those caused by impermeable form linings.

-	Not permitted: Discoloration caused by contamination or grout leakage.

-	Surface blemishes:

-	Permitted: Blowholes less than 10 mm in diameter and at an agreed frequency.

-	Not permitted: Voids, honeycombing, segregation and other large defects.

-	Formwork tie holes: In a regular pattern and filled with matching mortar.

E20/630	FINE SMOOTH FINISH

-	Finish: Smooth and even. Panels to be as large as is practicable and arranged in a regular pattern as a feature of the surface.

-	Permissible deviation of surfaces:

-	Sudden irregularities (maximum): 3 mm.

-	Gradual irregularities when measured from the underside of a 1 m straightedge, placed anywhere on surface (maximum): 3 mm.

-	Variations in colour:

-	Permitted: Those caused by impermeable form linings.

-	Not permitted: Discoloration caused by:

Contamination or grout leakage.

Replacement of formwork panels.

-	Cover spacers: must obtain engineers approval prior to using.

-	Surface blemishes:

-	Permitted: Blowholes less than 5 mm in diameter and at an agreed frequency.

-	Not permitted: Voids, honeycombing, segregation and other defects.

-	Formwork tie holes: not permitted.

E30	REINFORCEMENT FOR IN SITU CONCRETE

To be read with Preliminaries/ General conditions.

REINFORCEMENT

E30/110	QUALITY ASSURANCE OF REINFORCEMENT

-	Standards:

-	Reinforcement: To BS 4449, BS 4482, BS 4483 or BS 6744.

-	Cutting and bending: To BS 8666.

-	Source of reinforcement: Companies holding valid certificates of approval for product conformity issued by the UK Certification Authority for Reinforcing Steels (CARES).

E30/140	PLAIN BAR REINFORCEMENT

-	Standard: To BS 4482.

-	Strength grade: 250.

E30/150	RIBBED BAR REINFORCEMENT

-	Standard: To BS 4449.

-	Strength grade: B500b.

E30/210	STANDARD FABRIC REINFORCEMENT

-	Standard: To BS 4483.

WORKMANSHIP

E30/310	CUTTING AND BENDING REINFORCEMENT

-	General: To schedules and to BS 8666.

-	Bending on site, including minor adjustments: do not bend when below 5 degree C without prior approval. Steel may be warmed to not more than 100 deg C. Do not re-bend bars without approval. Tag bundles of reinforcement with labels to BS 4466

E30/320	PROTECTION OF REINFORCEMENT

-	Dropping from height, mechanical damage and shock loading: Prevent.

-	Cleanliness of reinforcement at time of pouring concrete: Free from corrosive pitting, loose mill scale, loose rust and contaminants which may adversely affect the reinforcement, concrete, or bond between the two.

E30/410	LAPS OR SPLICES

-	Details not shown on drawings: Obtain instructions.

E30/425	LAPS NOT DETAILED ON DRAWINGS

-	Laps in bar reinforcement (minimum): 300mm

-	Laps in fabric reinforcement (minimum): 250mm.

-	Laps at corners: Avoid four layer build-up.

E30/430	WELDED JOINTS

-	Site welding: not permitted.

E30/451	FIXING REINFORCEMENT

-	Standard: To BS 7973-1 and -2.

-	Installation: In addition to any spacers and chairs shown on drawings or schedules, provide adequate support, tie securely and maintain the specified cover.

-	Tying:

-	Wire type: 16 gauge black annealed. Use stainless steel wire for stainless steel reinforcement.

-	Ends of tying wire: Prevent intrusion into the concrete cover. Remove loose ends.

-	Compatibility of metals: Prevent contact between ordinary carbon steel and stainless or galvanized reinforcement.

E30/470	TOLERANCES ON COVER

-	Definition of nominal cover to BS 8500-1: Minimum cover plus tolerance for fixing.

-	Tolerance (maximum): 5mm

-	Checking specified cover dimensions: Before concreting check that cover dimensions will be achieved.

E30/480	NOMINAL COVER TO REINFORCEMENT

-	Top face: 30mm minimum superstructure / 50mm minimum substructure.

-	Formed faces: 30mm minimum superstructure / 50mm minimum substructure.

E30/510	RUST STAINING

-	Staining of surfaces of concrete which will be exposed to view in the finished work: Prevent.

E30/520	COVER METER SURVEY

-	Purpose of survey: To check positions of reinforcement and that the specified cover has been achieved. If any site inspections give rise to concerns with respect to adequacy of cover, engineer / architect may request a cover meter survey.

-	Type of cover meter: A magnetic induction digital display type selected to suit arrangement and type of reinforcement.

-	Use: In accordance with recommendations of BS 1881-204 and manufacturer as appropriate to yield accurate results.

-	Surveyor: Experienced with cover meter surveys.

-	Calibration: At the outset and thereafter regularly at 45 minute (maximum) intervals.

-	Locations for checking: Include beams, lintels and all faces exposed to the weather in the finished structure.

-	Timing: As soon as practicable after casting.

-	Notification: Give adequate notice.

-	Results: Submit. Notify immediately where specified cover has not been achieved.

E40	DESIGNED JOINTS IN IN-SITU CONCRETE

To be read with Preliminaries/ General conditions.

E40/120	CONSTRUCTION/ MOVEMENT JOINTS GENERALLY

-	Accuracy: Position and form joints accurately, straight, well- aligned and truly vertical or horizontal or parallel with setting out lines of the building.

-	Modifications to joint design or location: Submit proposals.

-	Placing concrete to form movement joints:

-	Maintain effectiveness of joints. Prevent concrete entering joints or penetrating or impregnating compressible joint fillers.

-	Do not place concrete simultaneously on both sides of movement joints.

E40/132	JOINTS IN FLOOR SCREED

-	Proposed positions of butt joints in screed must be agreed with CA prior to commencement.

E40/210	FORMED JOINTS

-	Forms/ stop ends generally: Rigid and grout-tight.

-	Forms/ stop ends for projecting continuity reinforcement: To accommodate bars or fabric without temporary bending or displacement.

E40/211	FORMED JOINTS IN CONCRETE WEARING SURFACES

-	Temporary forms: Square edged with a steel top surface.

-	Placing concrete: Compact thoroughly at edges to give level, closely abutted joints with no lipping.

E40/230	PREPARATION OF CONSTRUCTION JOINTS

-	Roughening of joint surfaces: Select from:

-	Brushing and spraying: Remove surface laitance and expose aggregate finish while concrete is still green.

-	Other methods: Submit proposals.

-	Condition of joint surfaces immediately before placing fresh concrete: Clean and damp.

E40/260	SAWN CRACK INDUCING GROOVES

-	Groove dimensions:

-	Depth: 5 – 10mm .

-	Width: As narrow as practicable.

-	Sawing: Sufficiently early to prevent random cracking (within 24 hours of casting slab) and to produce strong, well defined arrises.

-	Groove filling: hot pour ashphalt.

E40/410	TIE BARS

-	Standard: To BS 4449,

-	Strength grade: 250 N/mm2.

-	Cleanliness: Free from corrosive pitting, loose millscale, loose rust and contaminants which may adversely affect the tie bars, reinforcement, concrete, or bond between the two.

-	Position: Centred on joint.

E40/430	DOWEL BARS

-	Standard: To B.S. 4449.

-	Product form: Plain.

-	Strength grade: 250.

-	Properties: Perfectly straight, with sawn (not sheared) ends.

-	De-bonding: Achieve effective de-bonding of each bar

-	Material: de-bonding compound or plastic sleeve, incorporating 20mm compressible material at ends of all bars.

-	Position: At right angles to and centred on joint.

E40/590	INSPECTION OF TIED AND PARTIALLY TIED JOINTS

-	Purpose: To determine whether shrinkage is concentrated at occasional joints.

-	Timing: At intervals from one month after casting of slab for duration of works.

E41	WORKED FINISHES TO IN SITU CONCRETE

To be read with Preliminaries/ General conditions.

E41/150	FINISHING

-	Timing: Carry out at optimum times in relation to setting and hardening of concrete.

-	Prohibited treatments to concrete surfaces:

-	Wetting to assist surface working.

-	Sprinkling cement.

E41/210	TAMPED FINISH

-	Surface on completion: tamp surface with edge of board or beam to give an even texture of parallel ribs.

E41/230	BRUSHED FINISH

-	Surface on completion: Light even texture.

E41/240	WOOD FLOATED FINISH

-	Surface on completion: Slightly coarse, even texture with no ridges or steps.

E41/310	SMOOTH FLOATED FINISH

-	Surface on completion: Even with no ridges or steps.

E41/320	TROWELLED FINISH

-	Surface on completion: Uniform, smooth but not polished, free from trowel marks and blemishes, and suitable to receive specified flooring material.

E41/330	TROWELLED FINISH FOR WEARING SURFACES

-	Surface on completion: Uniform and smooth, free from trowel marks and blemishes.

E41/520	SURFACE SEALER

-	Apply an approved resin sealer to concrete wearing surface floors in accordance with manufacturer’s recommendations.

-	Substrate:

-	Moisture content: As recommended by sealer manufacturer. Test relative humidity to BS 8203; Annex A where required to verify suitability.

-	Condition prior to application: Cured, clean and free from contaminants.

-	Application: Evenly to dry surfaces to form an effective seal but without a glossy finish.

E60	PRECAST/ COMPOSITE CONCRETE FLOORS/ ROOF DECKS

To be read with Preliminaries/ General conditions.

PROPRIETARY FLOORS/ ROOF DECKS

130	PRECAST HOLLOWCORE SLAB

•	Slab type: Pre-cast, pre-stressed hollow core units

•	Slab depth: 150mm and 200mm as noted on drawings

•	Finish:

-	Soffit: Smooth formed finish

-	Top surface: Smooth finish

•	In situ continuity reinforcement: required when two slabs meet on a load-bearing	wall

180	PRECAST STAIRS

•	Manufacturer: Approved pre-cast concrete manufacturer

•	Parameters: imposed load as specified on drawing

•	Finish:

-	Exposed faces: Smooth formed finish

-	Treads and risers: Smooth floated finish

•	Other requirements: Lifting sockets to be cast in.

GENERAL/ PERFORMANCE

240	DETAILING OF PROPRIETARY SYSTEM

•	Installation details: Submit location and assembly drawings showing every aspect of the construction, incorporated components and features, trimming for voids, holes for services, and related work by others.

-	Purpose: To allow checking of compatibility with surrounding structure and coordination of services.

•	Method statement and risk assessment for installation: Submit.

•	Programme: Submit well in advance of construction.

INSTALLATION

320	CONCRETE INFILL

•	Designated concrete: BS 8500-2.

-	Designation: C28/35

-	Aggregate size (maximum): 20mm

•	Preparation: Thoroughly clean and wet surfaces of precast units.

•	Placing: Avoid segregation and compact thoroughly to eliminate voids.

-	Extent: Fill troughs and other holes.

-	Finish: Flush with top of precast units.

•	Protection: Prevent movement of units until concrete has gained sufficient strength.

325	GROUTING

•	Mix: 1:3 cement/sand mixture

•	Preparation: Ensure key between units is free from dust and debris

•	Extent: Fill all joints and surface irregularities.

340	LATERAL RESTRAINT STRAPS

•	Preparation: Floors/ roof decks must tightly abut walls.

•	Manufacturer: Expamet

-	Product reference: HDSS

•	Material: Stainless Steel

•	Size:

-	Section: Minimum 30 x 5 mm cross section.

-	Length: To extend minimum 800 mm from inside face of wall.

•	Form: Both ends cranked 100 mm.

•	Position: as required on drawings

•	Build in:

-	External cavity walls: One cranked end in tight contact with cavity face of wall inner leaf, the other cranked end grouted into floor/ roof deck joint.

350	LEVELS OF STRUCTURAL CONCRETE FLOORS

•	Tolerances: See Preliminaries section A33.

Q10	KERBS/ EDGINGS/ CHANNELS/ PAVING ACCESSORIES

To be read with Preliminaries/ General conditions.

TYPES OF KERBS, EDGINGS AND CHANNELS

Q10/110	PROPRIETARY PRECAST CONCRETE KERBS

-	Standard: To BS EN 1340.

-	Designations: Half battered HB2

-	Size (width x height x length): 125 x 255 x 1000

-	Finish: Fair faced

-	Colour: Natural Concrete

-	Bedding: Semi-dry C8/10

-	Joints generally: Mortar 1:3 cement/sand

Q10/111	PRECAST CONCRETE KERBS

-	Standard: To BS EN 1340.

-	Designations: Half battered HB3

-	Size (width x height x length): 125 x 150 x 1000

-	Finish: Fair faced

-	Colour: Natural Concrete

-	Bedding: Semi-dry C8/10

-	Joints generally: Mortar 1:3 cement/sand

Q10/112	PRECAST CONCRETE EDGINGS

-	Standard: To BS EN 1340.

-	Designations: Flat top edging EF

-	Size (width x height x length): 50 x 150 x 915

-	Finish: Plain finish

-	Colour: Natural Concrete

-	Bedding: Semi-dry C8/10

-	Joints generally: Mortar 1:3 cement/sand

Q10/113	PRECAST DWARF WALL

-	Standard: Wet cast to BS 8500-1

-	Designations: Turkington Precast DWFWALLS

-	Size (width x height x length): 90 x 380 x 915

-	Finish: Plain finish

-	Colour: Natural Concrete

-	Bedding: Semi-dry C8/10

-	Joints generally: Mortar 1:3 cement/sand

Q10/114	PRECAST DWARF WALL

-	Standard: Wet cast to BS 8500-1

-	Designations: Turkington Precast DWFWALL2

-	Size (width x height x length): 90 x 600 x 915

-	Finish: Plain finish

-	Colour: Natural Concrete

-	Bedding: Semi-dry C8/10

-	Joints generally: Mortar 1:3 cement/sand

ROADS/ PAVING ACCESSORIES/ MARKING

Q10/395	ROAD MARKING (THERMOPLASTIC)

-	Standard: Road Safety Markings Association standard specification document for road marking and road studs (StanSpec).

LAYING

Q10/510	LAYING KERBS, EDGINGS AND CHANNELS

-	Cutting: Neat, accurate and without spalling. Form neat junctions.

-	Long units (450 mm and over) minimum length after cutting: 300 mm.

-	Short units minimum length after cutting: The lower of one third of their original length or 50 mm.

-	Bedding of units: Positioned true to line and levelled along top and front faces, in a mortar bed on accurately cast foundations or on a race of fresh concrete.

-	Securing of units: After bedding has set, secured with a continuous haunching of concrete or on a race of fresh concrete with backing concrete cast monolithically.

Q10/520	ADVERSE WEATHER

-	Conditions: Do not construct if the temperature is below 3°C on a falling thermometer or 1°C on a rising thermometer. Adequately protect foundations, bedding and haunching against frost and rapid drying by sun and wind.

Q10/530	CONCRETE FOR FOUNDATIONS, RACES AND HAUNCHING

-	Standard: To BS 8500-2.

-	Designated mix: Not less than GEN0 or Standard mix ST1.

-	Workability: Very low.

Q10/540	CEMENT MORTAR BEDDING

-	General: To section Z21.

-	Mix (Portland cement:sand): 1:3.

-	Portland cement: Class CEM I 42.5 to BS EN 197-1.

-	Sand: to BS EN 12620, grade 0/4 or 0/2 (MP).

-	Bed thickness: 12-40 mm.

Q10/547	BEDDING/ BACKING OF UNITS ON FRESH CONCRETE RACES

-	Standard: To BS 7533-6.

Q10/570	CHANNELS

-	Installation: To an even gradient, without ponding or backfall.

-	Lowest points of channels: 6 mm above drainage outlets.

Q10/580	DRAINAGE CHANNEL SYSTEMS

-	Installation: To an even gradient, without ponding or backfall. Commence laying from outlets.

-	Silt and debris: Removed from entire system immediately before handover.

-	Washing and detritus: Safely disposed without discharging into sewers or watercourses.

Q10/590	DRAINAGE CHANNEL SYSTEMS WITH BUILT IN FALL

-	Installation: Top of channels level, installed in correct sequence to form an even gradient without ponding or backfall. Commence laying from outlets.

-	Silt and debris: Removed from entire system immediately before handover.

-	Washings and detritus: Safely disposed without discharging into sewers or watercourses.

Q10/600	FOLD KERBS/ CHANNELS

-	Usage: Radii of 15 m or less.

Q10/610	ANGLE KERBS

-	Usage: Internal and external 90° changes of direction.

-	Cutting of mitres: Not permitted.

Q10/620	ACCURACY

-	Deviations (maximum):

-	Level: ± 6 mm.

-	Horizontal and vertical alignment: 3 mm in 3 m.

Q10/640	TOOLED MORTAR JOINTS

-	Jointing: Ends of units buttered with bedding mortar as laying proceeds. Joints completely filled and tooled to a neat flush profile.

-	Joint width: 6 mm.

Q20	GRANULAR SUB-BASES TO ROADS/ PAVINGS

To be read with Preliminaries/ General conditions.

Q20/120	CHECKING CALIFORNIA BEARING RATIO (CBR) OF SUBGRADES

-	Subgrade variation: If material appears to vary from that stated in the site investigation report, or if there are extensive soft spots, test subgrade CBR to BS 1377-4 or BS 1377-9. Submit results and obtain instructions before proceeding.

Q20/130	HERBICIDES

-	Type: A non selective, non residual herbicide as approved by DEFRA

-	Application: To subgrade of roads and pavements

Q20/140	EXCAVATION OF SUBGRADES

-	Final excavation to formation or subformation level: Carry out immediately before compaction of subgrade.

-	Soft spots and voids: Give notice.

-	Old drainage and service trenches: Give notice

-	Wet conditions: Do not excavate or compact when the subgrade may be damaged or destabilized.

Q20/145	PREPARATION AND COMPACTION OF SUBGRADES

-	Timing: Immediately before placing sub-base.

-	Soft or damaged areas: Remove soft areas and fill with hardcore

-	Compaction: Thoroughly, by roller or other suitable means, adequate to resist subsidence or deformation of the subgrade during construction and of the completed roads/ pavings when in use. Take particular care to compact fully at intrusions, perimeters and where local excavation and backfilling has taken place.

Q20/150	SUBGRADES FOR VEHICULAR AREAS

-	Preparation and treatment: To Highways Agency ‘Specification for highway works’, clauses 616 and 617.

Q20/170	GEOTEXTILE FILTER/ SEPARATOR MEMBRANES

-	Manufacturer: Terram Ltd

-	Product reference: Terram 1000

-	Jointing: 150mm minimum overlap

-	Protect from:

-	Exposure to light, except during laying (maximum five hours).

-	Contaminants.

-	Materials listed as potentially deleterious by geotextile manufacturer.

-	Damage, until fully covered by fill.

-	Wind uplift, by laying not more than 15 m before covering with fill.

-	Preparation: Remove humps and sharp projections and fill hollows before laying.

Q20/200	SUBGRADE IMPROVEMENT LAYER (CAPPING)

-	Material: To Highways Agency ‘Specification for highway works’, table 6/1, Class 6F1, 6F2 or 6F3.

-	Standard: Placed and compacted to Highways Agency ‘Specification for highway works’, table 6/1, clauses 612 and 613.3, 613.8, 613.9, 613.10 and 613.13.

Q20/205	HIGHWAYS AGENCY TYPE 2 GRANULAR MATERIAL

-	Material: Type 2 unbound mixture to Highways Agency ‘Specification for highway works’, clause 801.

-	Recycled aggregate: Crushed Concrete, Brick and glass

-	CBR (minimum): 5%

Q20/210	HIGHWAYS AGENCY TYPE 1 GRANULAR MATERIAL

-	Material: Type 1 unbound mixture to Highways Agency ‘Specification for highway works’, clause 801.

-	Recycled aggregate: as agreed with Engineer

Q20/211	GRANULAR MATERIAL

-	Quality: Free from excessive dust, well graded, all pieces less than 75 mm in any direction, minimum 10% fines value of 50 kN when tested in a soaked condition to BS 812-111 and BS EN 1097-2, and in any one layer only one of the following:

-	Crushed rock (other than argillaceous rock) or quarry waste with not more binding material than is required to help hold the stone together.

-	Crushed concrete, crushed brick or tile, free from plaster, timber and metal.

-	Gravel or hoggin with not more clay content than is required to bind the material together, and with no large lumps of clay.

-	Natural gravel.

-	Natural sand.

-	Filling: Spread and levelled in 150 mm maximum layers, each layer thoroughly compacted.

Q20/220	FROST SUSCEPTIBLE GRANULAR MATERIAL

-	Definition (non frost susceptible material): To Highways Agency 'Specification for highway works' clause 801.8.

-	Depth of frost susceptible material below final surface of paving (minimum): 600mm.

-	Testing: Test materials used if required and supply certificates.

Q20/230	PLACING GRANULAR MATERIAL GENERALLY

-	Preparation: Loose soil, rubbish and standing water removed.

-	Structures, membranes and buried services: Ensure stability and avoid damage.

Q20/240	LAYING GRANULAR SUB-BASES FOR VEHICULAR AREAS

-	General: Spread and levelled in layers. As soon as possible thereafter compact each layer.

-	Standard: To Highways Agency ‘Specification for highway works’ clause 802.

-	At drainage fittings, inspection covers, perimeters and where local excavation and backfilling has taken place: Take particular care to compact fully.

Q20/250	LAYING GRANULAR SUB-BASES

-	General: Spread and levelled.

-	Compaction:

-	Timing: As soon as possible after laying.

-	Method: By roller or other suitable means, adequate to resist subsidence or deformation of the sub-base during construction and of the completed paving when in use. Take particular care to compact fully at intrusions, perimeters and where local excavation and backfilling has taken place.

Q20/310	ACCURACY

-	Permissible deviation  from required levels, falls and cambers (maximum):

-	Subgrades:

Roads and parking areas: +20 -30 mm.

Footways and recreation areas: ± 20 mm.

-	Sub-bases:

Roads and parking areas: ± 12 mm.

Footways and recreation areas: ± 12 mm.

Q20/320	BLINDING

-	Locations: Surfaces to receive sand bedded interlocking brick or block paving to sections Q24 and Q25.

-	Material: Sand, fine gravel or PFA.

-	Finish: Close, smooth, compacted surface.

Q20/330	COLD WEATHER WORKING

-	Frozen materials: Do not use.

-	Freezing conditions: Do not place fill on frozen surfaces. Remove material affected by frost. Replace and recompact if not damaged after thawing.

Q20/340	PROTECTION

-	Sub-bases: As soon as practicable, cover with subsequent layers, specified elsewhere.

-	Subgrades and sub-bases: Prevent degradation by construction traffic, construction operations and inclement

Q22	COATED MACADAM ROADS/ PAVINGS

To be read with Preliminaries/ General conditions.

TYPES OF PAVING

Q22/110	COATED MACADAM PAVING FOR ROADS

-	Standard: Northern Ireland (Private Streets) Order

-	Subgrade improvement layer: Quarry dust

-	Compacted thickness: 75mm

-	Granular sub-base: Type 3 granular material to MCDHW series 800

-	Compacted thickness: 225mm

-	Granular Base: Type 1 granular material to MCDHW series 800

-    Compacted thickness: 150mm

-	Binder course: AC20 dense bin 40/60 to BS EN 13108-01  :2006

-	Compacted thickness: 50mm

-	Surface course: AC14 close surf 40/60 to BS EN 13108-01  :2006

-	Compacted thickness: 40mm

-	Surface treatment: Rolled

Q22/115	ROLLED ASPHALT PAVING FOR RAISED TABLES

-	Standard: Northern Ireland (Private Streets) Order

-	Subgrade improvement layer: Quarry dust

-	Compacted thickness: 75mm

-	Granular sub-base: Type 3 granular material to MCDHW series 800

-	Compacted thickness: 225mm

-	Granular Base: Type 1 granular material to MCDHW series 800

-	Compacted thickness: 150mm

-	Binder course: AC20 dense bin 40/60 to BS EN 13108-01  :2006

-	Compacted thickness: 50mm

-	Surface course: HRA 35/14 F surf 40/60 to BS EN 13108-04  :2006

-	Compacted thickness: 40mm

-	Surface treatment: Red chips rolled into surface

Q22/140	ROLLED ASPHALT PAVING FOR PAVEMENTS

-	Standard: Northern Ireland (Private Streets) Order

-	Subgrade improvement layer: Quarry dust

-	Compacted thickness: 75mm

-	Granular Base: Type 1 granular material to MCDHW series 800

-	Compacted thickness: 150mm generally, 225mm opposite driveways

-	Binder course: AC20 dense bin 40/60 to BS EN 13108-01  :2006

-	Compacted thickness: 50mm

-	Surface course: HRA 15/10F SURF 40/60 to BS EN 13108-04  :2006

-	Compacted thickness: 30mm

-	Surface treatment: White Chips rolled into surface

PREPARATORY WORK/ REQUIREMENTS

Q22/220	BITUMINOUS MATERIALS GENERALLY

-	Suppliers names: Submit.

-	Timing (minimum): 2 weeks before starting work.

-	Test certificates: At the time of delivery for each manufacturing batch submit certificate:

-	Confirming compliance with this specification and the relevant British Standard.

-	Stating full details of composition of mix.

Q22/230	SAMPLES

-	Submit: Samples as required by Private Streets Officer

Q22/240	ACCEPTANCE OF SUB-BASE

-	Surface: Sound, clean and suitably close textured.

-	Levels and falls: To be within the specified tolerances:

-	Vehicular areas: +10 to -30 mm.

-	Pedestrian areas: ±12 mm.

-	Drainage outlets: 0 to -10 mm of the required finished level.

-	Kerbs and edgings: Complete, adequately bedded and haunched and to the required levels.

Q22/250	ABUTMENTS

-	Vertical edges of manholes, gullies, kerbs and other abutments: Clean and paint.

LAYING

Q22/310	LAYING GENERALLY

-	Preparation: Remove all loose material, rubbish and standing water.

-	Adjacent work: Form neat junctions. Do not damage.

-	Channels, kerbs, inspection covers etc: Keep clean.

-	New paving:

-	Keep traffic free until it has cooled to prevailing atmospheric temperature.

-	Do not allow rollers to stand at any time.

-	Prevent damage.

-	Lines and levels: With regular falls to prevent ponding.

-	Overall texture: Smooth, even and free from dragging, tearing or segregation.

-	State on completion: Clean.

Q22/320	ADVERSE WEATHER

-	Frozen materials: Do not use.

-	Suspend laying:

-	During freezing conditions.

-	If the air temperature reaches 0°C, or in calm dry conditions -3°C, on a falling thermometer.

-	Hot rolled asphalt: During periods of continuous or heavy rain or if there is standing water on the base.

Q22/330	LEVELS

-	Permissible deviation from the required levels, falls and cambers (maximum):

-	Finished surface: ±6 mm.

-	Adjacent to gullies and manholes: 0 to +3 mm.

Q22/340	FLATNESS/ SURFACE REGULARITY

-	Deviation of surface: Where appropriate in relation to the geometry of the surface, the variation in gap under a 3 m straightedge placed anywhere on the surface to be not more than:

-	Base: ± 20 mm.

-	Binder course: ± 5 mm.

-	Surface course: ± 3 mm.

-	Where a straightedge cannot be used the surface must be of a comparable standard of accuracy when judged by eye.

Q22/350	CONTRACTOR'S USE OF PAVEMENTS

-	Before use:

-	Open-grained surface: Fill with 0/4 mm size coated grit to BS 4987-1. Remove surplus.

-	Finish: Uncoated chipping and binder surface treatment.

-	Preparation for final surfacing:

-	Timing: Defer laying until as late as practicable.

-	Immediately before laying final surfacing: Clean and make good the base/ binder course. Allow to dry.

Accuracy: Uniform, without puddles.

-	Finishing: Allow emulsion to break completely before applying surface.

Q22/360	UNCOATED CHIPPINGS FOR SURFACE TREATMENT

-	Chippings: Clean aggregate to BS EN 13043 and PD 6682-2, size 2.8/6.3, grading category Gc85/15.

-	Type: Crushed basalt

-	Colour: Natural

-	Binder:

-	Cutback bitumen to BS EN 12591 or bitumen emulsion to BS 434-1.

-	Do not use cut-back bitumen at temperatures below 15°C.

-	Do not use modified binders without prior approval.

-	Application:

-	Binder application rate: In accordance with TRL Road Note 39. Adjust rate for modified binders in accordance with manufacturer's instructions.

-	Coverage: 100–105% shoulder to shoulder to BS 598-108.

-	Compaction: Roll. Do not crush chippings.

-	Completion:

-	Before trafficking, remove excess chippings.

-	Carry out further removal of loose chippings disturbed by traffic as necessary.

Q22/370	COATED CHIPPINGS

-	Chippings and application: To BS 594-1 and -2.

-	Type: Crushed basalt or other approved.

-	Size: 20mm single size

-	Colour

R12	DRAINAGE BELOW GROUND

To be read with Preliminaries/ General conditions.

GENERAL

R12/110	BELOW GROUND DRAINAGE SYSTEMS

-	Storm water drainage:  u-PVC pipes to BS EN 1401-1 up to 300mm dia.

-	Storm water drainage:  Concrete pipes to BS 5911 – 1 for 350mm dia. and over.

-	Foul drainage: u-PVC pipes to BS EN 1401-1

-	Land drainage: 100mm  perforated u-pvc pipes to BS 4962

-	Pipes, bends and junctions: u-PVC to BS EN 1452-4

-	Manholes, inspection chambers, traps, separators, and accessories: BS EN 7903:1997,BS EN 14396:20004, BS EN 8000-14:1989, BS EN 1253-5:20003, BS EN 4660:2000, BS EN 1433:2002.

Construction to be generally to BS 8400:Part 14

-	Disposal: Re-use spoil on site

PRODUCTS

R12/311	CONNECTORS

- Material and standard: Plastics to BS 4660 and Kitemark certified.

R12/313	ONE PIECE GULLIES

-	Standards:

-	Concrete: To BS 5911-6 and Kitemark certified, or Agrément certified.

-	Plastics: To BS 4660 and Kitemark certified, or Agrément certified.

-	Polypropylene: To BS EN 1852-1.

R12/315	ONE PIECE GULLIES AND COVERS

-	Standards:

-	Cast iron: To BS 437 and Kitemark certified, or Agrément certified.

-	Concrete: To BS 5911-6 and Kitemark certified, or Agrément certified.

-	Plastics: To BS 4660 and Kitemark certified, or Agrément certified.

-	Polypropylene: To BS EN 1852-1.

R12/346	PIPES, BENDS AND JUNCTIONS - PVC-U - PLAIN WALL

-	Standard: BS EN 1401-1, class SN4, with flexible joints, Kitemark certified.

R12/348	PIPES, BENDS AND JUNCTIONS - POLYPROPYLENE

-	Standard: To BS EN 1852-1.

R12/357	CONNECTORS - SADDLE

-	Standards:

-	Plastics: To BS 4660 and Kitemark certified, or Agrément certified.

R12/401	INSPECTION CHAMBERS - PLASTICS

-	Standard: To BS 7158 or BS EN 13598-1, or Agrément certified.

-	Diameter: 450-850mm.

R12/407	MANHOLES AND INSPECTION CHAMBERS - CONCRETE

-	Standards:

-	To BS 5911-3 and BS EN 1917 and Kitemark certified; or

-	To BS 5911-4 and BS EN 1917.

-	Sizes: 900-1200mm

-	Steps: BS EN 13101:2002

R12/421	OIL AND PETROL SEPARATOR UNITS - PLASTICS

-	Standards: To Environment Agency PPG 3 and BS EN 858-1, with oil level alarm.

-	Manufacturer: Klargester or equal Approved.

R12/444	SEALING FOR CONCRETE MANHOLES - BITUMINOUS STRIPS

-	Manufacturer: FP Mc Cann Rings with sealant provided.

R12/471	ACCESS COVERS AND FRAMES

-	Standard: To BS EN 124.

R12/475	ACCESS LADDERS

-	Standard: To BS 4211.

R12/483	CONCRETE (GENERAL)

-	Standard: To BS 8500-2.

-	Concrete: C10/20.

R12/487	CONCRETE (ADOPTABLE MANHOLE BENCHINGS AND SURROUNDS)

-	Standard:

-	England and Wales, Northern Ireland: To WRc ‘Sewers for Adoption’.

-	Scotland: To WRc ‘Sewers for Scotland’.

-	Concrete: In situ.

R12/489	CONCRETE (ADOPTABLE MANHOLE BENCHING TOPPING)

-	Standard:

-	England and Wales, Northern Ireland: To WRc ‘Sewers for Adoption’.

-	Scotland: To WRc ‘Sewers for Scotland’.

-	Concrete: High strength.

.

R12/496	GRANULAR MATERIAL

-	Standard: To BS EN 12620.

-	Size: Dependent on location - see Execution clauses in this section, and in sections R16, R17 and R18, if used.

R12/498	GRANULAR SUB-BASE MATERIAL

-	Standard: To Highways Agency Volume 1, ‘Specification for Highway Works’, Type 1 Unbound mixtures for sub-base.

FABRICATION

R12/510	VERMIN GRATINGS FOR OUTFALLS AND OUTLET HEADWALLS

-	Construction: Mild steel frame extending 75 mm beyond pipe opening all around, with 25 mm maximum opening steel mesh grille. Top hinged on built-in fish-tail straps and with bottom pin lock.

-	Finish: Galvanized to BS EN ISO 1461 after fabrication.

-	Submit: Shop drawings.

-	Timing: Before manufacture.

EXECUTION

R12/611	EXISTING DRAINS

-	Setting out: Before starting work, check invert levels and positions of existing drains, sewers, inspection chambers and manholes against drawings. Report discrepancies.

-	Protection: Protect existing drains to be retained and maintain normal operation if in use.

R12/613	EXCAVATED MATERIAL

-	Sub soil, hardcore, etc: Set aside for use in reinstatement.

-	Turf and topsoil: Remove from site

R12/616	SELECTED FILL FOR BACKFILLING

-	Selected fill: As-dug material, free from vegetable matter, rubbish, frozen soil and material retained on a 40 mm sieve.

-	Compaction: By hand in 100 mm layers.

R12/623	LOWER PART OF TRENCH - GENERAL

-	Trench up to 300 mm above crown of pipe: Vertical sides, width as small as practicable.

-	Width (minimum): External diameter of pipe plus 300 mm.

R12/625	LOWER PART OF TRENCH - TRANSITION DEPTH

-	Trench widths up to 300 mm above crown of pipe (maximum):

-	DN 100 pipelines more than 6.0 m deep: 600 mm.

-	DN 150 pipelines more than 5.4 m deep: 700 mm.

-	DN 225 pipelines more than 4.0 m deep: 800 mm.

-	DN 300 pipelines more than 2.9 m deep: 900 mm.

R12/631	TYPE OF SUBSOIL

-	General: Where type of subsoil at level of crown of pipe differs from that stated for the type of bedding, surround or support, give notice.

R12/635	FORMATION FOR BEDDINGS

-	Timing: Excavate to formation immediately before laying beddings or pipes.

-	Mud, rock projections, boulders and hard spots: Remove. Replace with consolidated bedding material.

-	Local soft spots: Harden by tamping in bedding material.

-	Inspection of excavated formations: Give notice.

R12/641	PIPES AT DIFFERENT LEVELS IN COMMON TRENCH

-	Subtrench: Permissible provided soil of step is stable and unlikely to break away.

-	Subtrench not permissible: Trench depth as required for lower pipe. Increase thickness of bedding to upper pipe as necessary.

-	Lower pipe: Backfill with compacted granular material to at least half way up higher pipe.

-	Clear horizontal distance between pipes (minimum):

-	Pipes up to DN 700: 350 mm.

-	Pipes exceeding DN 700: 500 mm.

R12/655	CLASS A BED

-	Type of subsoil: Clay

-	Trench: Excavate slightly shallower than final levels.

-	Trimming: By hand to accurate gradients. Replace overdig with compacted spoil.

-	Pipes: Rest uniformly on barrels, adjust to line and gradient. Do not use hard packings under pipes.

-	Initial testing before backfilling: Air Test.

-	Backfilling:

-	Material: Protective cushion of selected fill.

-	Depth: 150 mm (250 mm for adoptable sewers) above crown of pipe.

-	Compaction: By hand in 100 mm layers.

R12/657	CLASS A BEDDING _Concrete C8/10 bed and surround.

-	Type of subsoil: Clay.

-	Initial testing before backfilling: Air Test.

-	Depth: 150 mm (250 mm for adoptable sewers) above crown of pipe.

-	Compaction: By hand in 100 mm layers.

R12/659	CLASS B BED

-	Type of subsoil: Clay

-	Granular material: Table 3 BS 882:1992.

-	Bedding:

-	Material: As-dug material with a compaction fraction of not more than 0.3.

-	Compaction: Over full width of trench.

-	Thickness (minimum): 50 mm for sleeve jointed pipes, 100 mm for socket jointed pipes. Where trench bottom is uneven, increase thickness by 100 mm.

-	Pipes: Dig slightly into bedding, rest uniformly on barrels and adjust to line and gradient.

-	Initial testing before backfilling: Air Test.

-	Backfilling:

-	Material: Protective cushion of selected fill.

-	Depth: 150 mm (250 mm for adoptable sewers) above crown of pipe.

-	Compaction: By hand in 100 mm layers.

R12/661	CLASS E BED

-	Type of subsoil: Clay.

-	Granular material: Table 3 BS 882:1992.

-	Bedding:

-	Material: Granular, compacted over full width of trench.

-	Thickness (minimum): 100 mm.

-	Pipes: Dig slightly into bedding, rest uniformly on barrels and adjust to line and gradient.

-	Initial testing before placing support: Air Test.

-	Backfilling:

-	Material and depth:

Protective cushion of selected fill to 300 mm above crown of pipe; or

Additional granular material, to 100 mm above crown of pipe.

-	Compaction: By hand in 100 mm layers.

R12/680	CONCRETE SURROUND FOR PIPE RUNS NEAR FOUNDATIONS

-	Class A surround: Provide in locations where bottom of trench is lower than bottom of foundation and as follows (horizontal clear distance between nearest edges of foundations and pipe trenches):

-	Trenches less than 1 m from foundations: Top of concrete surround not lower than bottom of foundation.

-	Trenches more than 1 m from foundations: Top of concrete surround not lower than D mm below bottom of foundation, where D mm is horizontal distance of trench from foundation, less 150 mm.

R12/683	LAYING PIPELINES

-	Laying pipes: To true line and regular gradient on even bed for full length of barrel with sockets (if any) facing up the gradient.

-	Ingress of debris: Seal exposed ends during construction.

-	Timing: Minimize time between laying and testing.

R12/685	JOINTING PIPELINES

-	Connections: Durable, effective and free from leakage.

-	Junctions, including to differing pipework systems: With adaptors intended for the purpose.

-	Cut ends of pipes: Clean and square. Remove burrs and swarf. Chamfer pipe ends before inserting into ring seal sockets.

-	Jointing or mating surfaces: Clean and, where necessary, lubricate immediately before assembly.

-	Allowance for movement: Provide and maintain appropriate clearance at ends of spigots as fixing and jointing proceeds.

-	Jointing material: Do not allow to project into bore of pipes and fittings.

R12/687	CONCRETE SURROUND FOR CROSSOVERS

-	Class Z surround: Provide where two pipelines (other than plastics pipes) cross with less than 300 mm separation.

-	Extent, on both pipes: 1 m centred on the crossing point, and beyond as necessary to come within 150 mm of nearest flexible joints.

R12/689	PIPELINES PASSING THROUGH STRUCTURES

-	Pipelines that must be cast in or fixed to structures (including manholes, catchpits and inspection chambers): Provide 600 mm long rocker pipes adjacent to the external face of the structure (or both faces where appropriate, e.g. walls to footings), with flexible joints at both ends.

-	Distance to rocker pipe from structure (maximum):150 mm.

-	Provision for movement for pipelines that need not be cast in or fixed to structures (e.g. walls to footings):

-	Rocker pipes as specified above; or

-	Openings in the structures to give 50 mm minimum clearance around the pipeline. Closely fit a rigid sheet to each side of opening to prevent ingress of fill or vermin.

R12/691	BENDS AT BASE OF SOIL STACKS

-	Type: U-PVC

- 	Bedding: Do not impair flexibility of pipe couplings.

-	Material: Concrete (general).

R12/693	DIRECT CONNECTION OF GROUND FLOOR WCS TO DRAINS

-	Horizontal distance from the drop to a ventilated drain (maximum): 6 m.

R12/695	BACKDROP PIPES OUTSIDE MANHOLE WALLS

-	Excavation beneath backdrop pipe: Backfill.

-	Material: C10/20 Concrete.

R12/697	INSTALLING FLEXIBLE COUPLINGS

-	Ends of pipes to be joined: Cut cleanly and square.

-	Outer surfaces of pipes to be joined: Clean and smooth. Where necessary, e.g. on concrete or iron pipes, smooth out mould lines and/ or apply a cement grout over the sealing area.

-	Clamping bands: Tighten carefully to make gastight and watertight seals.

R12/699	CONNECTIONS TO SEWERS

-	General: Connect new pipework to existing adopted sewers to the requirements of the adopting authority or its agent.

R12/705	INITIAL TESTING OF PIPELINES

-	Before testing:

-	Cement mortar jointing: Leave 24 h.

-	Solvent welded pipelines: Leave 1 h.

-	Method: Block open ends of pipelines to be tested and pressurise. Air test short lengths to BS EN 1610.

R12/711	TRENCH SUPPORTS

-	Removal of trench supports: Sufficient to permit compacted filling of all spaces.

R12/713	INSTALLING ROOT BARRIERS

-	Root barrier installation: Full depth of excavation. Fit closely to trench wall nearest the tree.

R12/715	BACKFILLING TO PIPELINES

-	Backfilling above top of surround or protective cushion: Material excavated from trench, compacted in layers 300 mm (maximum) thick.

-	Heavy compactors: Do not use before there is 600 mm (total) of material over pipes.

R12/718	BACKFILLING OVER CONCRETE

-	Minimum times from placing concrete:

-	Backfilling generally: 24 h.

-	Heavy compactors and traffic loads: 72 h.

R12/720	BACKFILLING UNDER ROADS AND PAVINGS

-	Backfilling from top of surround or protective cushion up to formation level: Granular sub-base material, laid and compacted in 150 mm layers.

R12/722	PUBLIC ROADS AND PAVINGS - E&W, SCOT

-	Excavating and backfilling of trenches: To Department for Transport ‘Specification for the reinstatement of openings in highways’.

R12/724	PUBLIC ROADS AND PAVINGS - NI

-	Excavating and backfilling of trenches: To Northern Ireland Road Authority and Utilities Committee ‘Specification for the reinstatement of openings in highways’.

R12/726	FOAMED CONCRETE BACKFILL

-	Preparation: Seal off openings in, and ends of, abandoned pipelines and ducts. Seal off cavities in or next to the excavation which are not to be filled.

-	Backfilling: To British Cement Association ‘Foamed concrete - specification for use in the reinstatement of openings in highways’.

R12/728	LAYING WARNING MARKER TAPES

-	Installation: During backfilling, lay continuously over pipelines.

-	Depth: 300-400 mm.

-	Pipelines deeper than 2 m: Lay an additional tape 600 mm above the top of the pipeline.

R12/741	INSTALLING INSPECTION CHAMBERS - PLASTICS

-	Bedding:

-	Material:  Granular BS EN 882 :1992

-	Thickness (minimum): Ref class Type detail

-	Surround:

-	Material:  Concrete C10/20

-	Thickness (minimum): 100mm

R12/743	INSTALLING CONCRETE MANHOLES

-	Bases:

-	Material:  Concrete C10/20

-	Thickness (minimum): 200mm

-	Surround:

-	Material:  Concrete C10/20.

-	Thickness (minimum): 100mm

R12/747	INSTALLING OIL AND PETROL SEPARATOR UNITS

-	As per manufactures details.

R12/753	FIXING MANHOLE STEPS

-	Fixing: Bed in joints.

-	Positioning: 300 mm vertical centres staggered 300 mm horizontally, with lowest step 300 mm (maximum) above benching and top step 450 mm (maximum) below top of cover.

R12/757	LAYING CONVENTIONAL CHANNELS, BRANCHES AND BENCHING

-	Main channel: Bed solid in 1:3 cement:sand mortar.

-	Branches: Connect to channel, preferably at half pipe level, so that discharge flows smoothly in direction of main flow.

-	Branches greater than nominal size 150 mm: Connect the branch soffit level with the main drain soffit.

-	Connecting angles more than 45° to direction of flow: Use three-quarter section channel bends.

-	Benching:

-	Material: _Concrete C10/20.

-	Profile: Rise vertically from top of main channel to a level not lower than soffit of outlet pipe, then slope upwards at 10% to walls.

R12/759	LAYING PREFORMED PLASTICS CHANNELS, BRANCHES AND BENCHING

-	Main channel: Bed solid in 1:3 cement:sand mortar.

-	Branches: Connect to channel, preferably at half pipe level, so that discharge flows smoothly in direction of main flow.

-	Connecting angles more than 45° to direction of flow: Use three-quarter section channel bends.

-	Bedding: 1:3 cement:sand mortar. Use clips or ensure adequate mechanical key.

-	Benching:

-	Material: Concrete (general).

-	Profile: Rise vertically from top of main channel to a level not lower than soffit of outlet pipe, then slope upwards at 10% to walls.

R12/771	INSTALLING OUTFALLS

-	Pipe outflow invert (minimum): Seasonal peak level or 150 mm above normal water level, whichever is the higher.

-	Pipe surround and backfill to the last 2 m run of drain: Excavated subsoil, rammed home.

COMPLETION

R12/901	REMOVAL OF DEBRIS AND CLEANING

-	Preparation: Lift covers to manholes, inspection chambers and access points. Remove mortar droppings, debris and loose wrappings.

-	Timing: Before cleaning, final testing, CCTV inspection if specified, and immediately before handover.

-	Cleaning: Thoroughly flush pipelines with water to remove silt and check for blockages. Rod pipelines between access points if there is any indication that they may be obstructed.

-	Washings and detritus: Do not discharge into sewers or watercourses.

-	Covers: Securely replace after cleaning and testing.

R12/903	TEMPORARY MEASURES

-	Water used to stabilize tanks and the like during installation: Drain.

R12/911	TESTING AND INSPECTION

-	Dates for testing and inspection: Give notice.

R12/921	FINAL TESTING OF PRIVATE GRAVITY DRAINS AND SEWERS UP TO DN 300

-	Before testing:

-	Cement mortar jointing: Leave 24 h.

-	Solvent welded pipelines: Leave 1 h.

-	Standard: To Building Regulations.

-	Method: Air Test.

R12/931	FINAL TESTING OF ADOPTABLE AND LARGE PRIVATE SEWERS

-	Standard (sewers up to and including size DN 750):

-	England, Wales and Northern Ireland: To WRc ‘Sewers for adoption’.

-	Scotland: To WRc ‘Sewers for Scotland’.

-	Method: Air Test.

R12/941	WATER TESTING OF MANHOLES AND INSPECTION CHAMBERS

-	Timing: Before backfilling.

-	Standard:

-	Exfiltration: To BS EN 1610.

-	Method: Testing with water (method W).

-	Infiltration: No identifiable flow of water penetrating the chamber.

R12/971	CCTV INSPECTION OF PRIVATE PIPELINES

-	General: Carry out and record internal inspection using CCTV equipment.

-	Illumination: Of adequate intensity.

-	Recording: Provide continuous position recording, still photographs and stopping of the camera at any point.

-	Copy of videotape recording: Submit.

R12/976	CCTV INSPECTION OF ADOPTABLE PIPELINES

-	General: Permit the Adopting Authority or its agent to carry out and record internal CCTV inspection of pipelines and associated manholes after completion.

-	Pipelines under highways: Complete construction, except for laying of wearing course, before inspection.

R12/978	LIFTING KEYS

-	Lifting keys: Supply suitable keys for each type of access cover.

-	Timing: At completion.

R13	LAND DRAINAGE

To be read with Preliminaries/ General conditions.

DRAINS

R13/211	FILTER DRAIN WITH PIPE

-	Trench size (depth x width):  750mm (minimum) x 450mm

-   Pipes: 150mm twinwall perforated polyethylene pipe

-	Manufacturer: Brett Martin (or other approved).

-   Product reference: 1Tpp6

-	Size: DN: 150mm.

-	Pipe surround/ backfill:

-	Material: Granular material to SHW Clause 515 (surround material to pipes shall be the granular material used as infill to the drain).

-   Depth of cover to pipe (minimum): 590mm

R13/350	LAYING PIPES

-	Weather conditions: Lay pipes in good weather using methods suitable for the site conditions.

-	Prevent compaction, smearing, top ponding, rutting and damage to soil structure.

-	General: Lay to line and gradient on a firm bed free from loose soil to give a free-draining installation without backfalls. Do not lay on soil backfill or in slurry.

-	Junctions between branches and mains: Use purpose made components.

-	Backfilling: Carefully backfill with filter material. Do not damage, distort or displace pipes.

R13/370	COLD WEATHER

-	Plastics pipes: Do not lay or backfill at temperatures lower than 5°C.

R13/380	TREES/ HEDGES

-	Drains closer than 6 m to trees/ hedges: Nonporous, unperforated pipes with positively sealed joints and as-dug backfill.

EXCAVATING/ BEDDINGS/ SURROUNDS/ BACKFILL

R13/505	EXCAVATION

-	Pipe gradients: Between 1 in 200 and 1 in 80.

-	Subsoil: Remove from site or to approved locations at end of each day and before pipe laying. Do not disperse on topsoiled areas.

R13/520	FORMATION FOR PIPES/ BEDS

-	Timing: Excavate to formation immediately before laying beds or pipes.

-	Hard spots: Remove mud, rock projections, boulders, etc. Replace with consolidated bedding material.

-	Soft spots: Tamp in bedding material.

-	Inspection: Give notice of completed excavated formation for each section of the work.

-	Period of notice (minimum): 2 days

R13/530	GRANULAR SURROUND/ BACKFILL

-	Material: Clean gravel, broken stone, hard clinker or slag, with no fines, single size 10 mm.

R13/555	GRANULAR BACKFILLING TO DRAINS WITH PIPES

-	Placing: Surround and backfill in maximum 300 mm thick layers, with mechanical compaction from 300 mm above crown of pipe, up to finished ground level or other specified level.

-	Do not heap material in the trench before spreading.

-	Carefully pack material by hand around the sides of the pipe.

R13/800	CLEANING

-	General: Thoroughly flush out the whole of the installation with clean water to remove silt and debris immediately before handover.

-	Washings and detritus: Dispose of safely. Do not discharge into sewers or watercourses.

SECTION 3

MECHANICAL & ELECTRICAL SPECIFICATION

SPECIFICATION

INDEX

- Product, Materials and Work Standards

- Particular Specification

- Schedules

| 1 | Drawings- Not Used |  |
| --- | --- | --- |
| 2 | Gas Fired Combination Boilers |  |
| 3 | Gas Fired System Boilers |  |
| 4 | Not Used |  |
| 5 | Gas Pipework |  |
| 6 | Gas Safety Valves and Carbon Monoxide Sensors |  |
| 7 | Oil Fired Boiler |  |
| 8 | Electronic Time Clocks and Controls |  |
| 9 | Pipe in Pipe Pipework |  |
| 10 | Radiators |  |
| 11 | Radiator Valves |  |
| 12 | Not Used |  |
| 13 | Gas Boiler Flues |  |
| 14 | Not Used |  |
| 15 | Hot Water Cylinders |  |
| 16 | Flow Regulation Valves |  |
| 17 | Sinks |  |
| 18 | Wash Basins |  |
| 19 | WC’s |  |
| 20 | Baths |  |
| 21 | Showers |  |
| 22 | Shower Former |  |
| 23 | Thermostatic Mixing Valves |  |
| 24 | Soils and Wastes |  |
| 25 | Whole House Ventilation |  |
| 26 | Cooker Hoods |  |

## SECTION 1

PRODUCTS, MATERIALS & WORKS STANDARDS

SECTION 1

PRODUCTS, MATERIALS AND WORKS STANDARDS

# 1.1	Requirement

The Mechanical Services Installation to be carried out by Developer in accordance with Performance Standards set in this specification.

SECTION 2

PARTICULAR SPECIFICATION

FOR MECHANICAL SERVICES DESIGN

SECTION 2

PARTICULAR SPECIFICATION

2.1	SCOPE OF WORK

The Developer shall deliver to site, install, test and commission all items necessary for the complete mechanical installation of the following:

- Negotiation and liaison with Northern Ireland Water regarding new incoming supplies

- Negotiation and liaison where applicable with Natural Gas Supplier regarding new incoming supplies to each house

- Heating Installation

- Plumbing Installation

- Soils and Wastes Installation

- Renewable Energies Installations comprising Whole House Ventilation

- Kitchen Extract Ventilation Installation

- Testing and Commissioning installation

The Developer shall supply, deliver to site, off load, install, test, commission, and set to work, all items of materials and equipment necessary for the continuous operation of the works described throughout the specification and as indicated on the contract drawings to provide the following services.

The Developer shall be solely responsible for the connection of all necessary utilities.

The Developer shall complete and issue to Utility Companies such application forms and connection cards as and when required to suit the Contract Programme.

The Developer shall ensure that all utility connections are completed on time to suit the contract programme and no extension of time shall be provided due to late connection of utility services.

2.2	INSTALLATION REGULATIONS

The whole of the installation shall be carried out in accordance with the current editions of:-

(i)	The Gas Safety (Installation and Use) Regulations 1998

(ii)	BS 6700:2006+Amendment 1:2009 Design, installation, testing and maintenance of services supplying water for domestic use within buildings and their curtilages Specification

(iii)	British Standards Specification.

(iv)	BS Codes of Practice.

(v)	Any regulations issued by the Local Government Authorities in respect of installation in certain specified buildings.

2.3	SAMPLES / APPROVALS

Prior to the placing of any orders the Developer shall engage in a two stage approval process for all items to be provided under this Sub-Contract.  This shall involve the following:

    - Completion of all forms contained within the appendices of this specification confirming both the product details and their compliance with all items relating to their selection and the clients general requirements.

    - Upon initial approval of any or all the items set out within the schedules the client may request that the Developer provide physical samples of any item prior to full approval to provide and install each item.  The Developer shall provide samples free of charge whether or not they are approved and / or installed as part of the works.

Failure to comply with this instruction will result in the Developer replacing any and all items installed without approval and found not to be acceptable at his own expense.

The Developer shall also be liable for the cost of any incidental work involved in replacing the items.

2.4	CO-ORDINATION AND INTEGRATION

The Developer shall take all measures considered to be necessary to enable him to provide installation drawings that:-

(i)	Show services properly related to others within his own and other’s contract, all such drawings being fully co-ordinated with other services and building elements.

(ii)	Allow adequate provision for maintenance.

(iii)	Allow builders work details to be prepared.

During the progress of the work the Developer shall continue to discuss runs of services and locations of plant and devices with other trades.

Possible clashes or inappropriate positioning related to door swings, fixtures etc shall immediately be reported to the Engineer.

No additional cost will be entertained for additional works due to lack of co-ordination.

The Developer drawings provided as part of these contract documents are diagrammatic only and not to scale.  As such some mechanical and electrical items may appear to clash and require careful co-ordination to ensure they are properly located as part of the works.  This process shall be undertaken at no additional cost to the client and shall include the following process.

The Developer shall mark all services locations on walls prior to the commencement of installations to show the locations of all items and to demonstrate that they have been properly co-ordinated.  Failure to show the location of any item which causes a clash at a later date shall result in the Developer relocating one or both items at no cost to the contract.

2.5	COMMISSIONING, INSPECTION, TESTING AND SETTING TO WORK

The Developer shall be required to carry out all commissioning, testing and setting to work of the complete mechanical services and associated equipment, plant etc, as provided under this sub-contract.

This shall be undertaken as recommended within the CIBSE Commissioning Codes of Practice.

2.6	OPERATING AND MAINTENANCE MANUALS

At the completion of the installation the Developer shall instruct and advise the Client as to the proper operation and maintenance of plant.

The instructions shall be carried out during the commissioning period and the ‘Practical Completion Certificate’ will not be issued until all operating instructions are submitted to the Client.

Operating instructions shall be provided in the form of bound documents to include all details of starting up and operation of items of equipment included in the Contract together with specialist information for the operators reference.

This documentation shall be provided by the Developer in duplicate and be available for use during the commissioning of the plant at the commencement of the Defects Liability Period.

The following details shall be provided where applicable.

(a)	Operating instructions

(b)	‘As Fitted’ drawings (in the form of AutoCAD disks)

(c) 	Manufacturers Drawings of Equipment

(d)	Sectional drawings where applicable

(e)	Schedule of accessories & equipment installed, manufacture and type numbers

(f)	Spare parts list

(g)	Maintenance schedules of recommended frequency of inspection and overhaul in terms of time and running hours.

(h)	Test Certificates

(i)	Schedules of Commissioning Tests

Mechanical Services Manual – minimum outline requirements

Contact schedule of names, addresses, normal and out of hours telephone and fax numbers of all sub contractors, suppliers and manufacturers relating to the product or service provided.

Description and details of equipment, appliances and installations used including, where appropriate, wiring diagrams, technical literature, user, operational and maintenance instructions that include for:

- Extractor fans / cooker hood

- Heating & Hot Water Systems (timer/programmer, flue, roomstat, radiators, HW cylinder, immersion, isolation valves etc)

- Solar panels, whole house ventilation & rainwater harvesting system including all automatic controls and equipment

- Sanitary ware (WC’s, taps etc)

Testing and Commissioning Certificates that include for:

- Pressure, heat and sterilisation as appropriate

- Renewable energy systems

Two paper copies of all operating and maintenance manuals and electronic copy of all documents shall be provided including as installed drawings.

2.7	AS INSTALLED DRAWINGS

During the whole of the contract the Developer shall keep on site an up-to-date set of prints marked up with details necessary for the production of As Installed Drawings as described below.

These prints shall be made available for inspection by the Contract Administrator at any time.

Before completion two paper prints of each As Installed Drawing shall be submitted for comment.

Time shall be allowed for comment in accordance with the contract conditions.

In addition time required for correcting any errors shall be allowed.

The final issue shall consist of two paper prints, of each drawing and also one set of computer software discs containing the drawing's information on Autocad 2004 format.

2.8	PERSONNEL INSTRUCTION

The Developer shall include in his Tender Price for the attendances of all necessary persons to fully instruct Client personnel in the operations of the installations.

2.9	TENANT PACKS

Tenant Packs shall be prepared and presented in an A4 wallet / holder with the correct postal address / house numbers and ready for the handover date.

Minimum outline requirements are as follows

Heating programmers / controllers

Room thermostats

Incoming water main stopcock

Extract fans

Whole house ventilation unit

2.10	PROVISIONAL SUMS

The Developer shall refer to the Provisional Sums as set out in the main pricing document.

2.11	RENEWABLE SYSTEMS & INCLUDE DEVELOPER

The Developer shall include for the supply, delivery to site, erection, connection, testing and commissioning of the following renewable energy systems detailed within the attached appendices.

The system shall be supplied and installed by a single specialist supplier.

The renewable systems are to be installed to achieve Code for Sustainable Homes and reduction from the specified system efficiencies and performance levels shall be accepted.

It should be noted that the calculation process for Code for Sustainable Homes is the summation of a number of systems performance criteria and no reduction in any system shall be allowed as this shall affect the overall calculation process.

It should be noted that the Developer shall liaise with their specialist to ensure that all items which are excluded form their price and included within the general mechanical services tender price.

2.12	LTHW PIPEWORK

Above floor pipework and fittings shall be fabricated using half hard light gauge copper tubing to BS2871 Part 1 Table X.

Pipework shall be fitted in standard lengths with no piecing.

Fittings shall be manufactured from non-dezincable copper alloy or gunmetal with integral silver brazing alloy internal rings.

Underfloor pipework and pipework rising in walls shall be manufactured in accordance with Appendix 8.

Each pipe run running under floor shall comprise a single length of pipe with no joints but will include serpentine bends and shall be laid on top of the floor insulation.

The complete installation shall be carried out strictly in accordance with the manufacturer’s instructions and recommendations.

2.13	SANITARY WARE

The Developer shall supply & install the items of sanitary ware as detailed on the drawings.

The installation shall comply generally with the following:

a)	The Developer shall be responsible for all services and to and from all items of sanitary ware throughout the system.

b)	WC pans shall be thoroughly washed with normal flush without splashing over and without having any unwashed areas.

If found defective in this respect the pan shall be replaced free of charge.

c)	All sanitary ware showing visible cracks or crazing before or during the effects

Liability Period not caused by physical damage shall be replaced free of charge by the Developer.

d)	The ball valve in the flushing cistern shall be suitable for the working pressure and shall be stamped by the Local Water Authority.

e)	On the washbasins and sinks, hot taps shall be fitted to the left and cold taps to the right.

f)	All sanitary fittings must be left in a clean and acceptable condition with all protective paper and debris, etc, removed.

g)	A chrome plated flow restrictor shall be fitted on each supply to each sink and washbasin.

All sanitary ware including pedestals to be white.

While every effort has been made to ensure that the items of sanitary ware are positioned correctly, the Developer is required to ensure that the locations correspond to those indicated on the Architects drawing prior to installation.

The Engineer reserves the right to reject any sanitary fittings which are in any way damaged or sub-standard and the Developer will be responsible for removing and replacing items at no expense to the Client.

Any additional cost incurred due to the replacement of fittings shall also be charge to the Developer.

Flow regulation valves as detailed within the schedules shall be installed on the connections to all appliances.

2.14	SOILS & WASTES

The Developer shall supply, erect, and connect a complete soils and wastes installation including traps, as indicated on the drawings, generally carried out in uPVC pipework in accordance with the requirements of BS4514 and the following:

(a)	Sanitary fittings, details of which are indicated on the drawings, shall be supplied & installed under this Mechanical Sub-Contract and shall have the following outlet sizes:-

WC Pans			110mm (4")

Wash Hand Basins		32 mm (1¼)

Sinks				40 mm (1½)

Baths				40 mm (1½)

b)	All fittings to be individually trapped.

c) 	In all instances connections for current and / or future showers must be run separately and independently to main soil stacks and under no circumstances must be combined with any other items.

The Developer shall ensure that the pipework and fittings are installed strictly in accordance with the manufacturers’ recommendations and instructions.

2.15	EXTERNAL PLUMBING & PIPEWORK

Supply and installation as detailed on the drawings of external underground mains water pipework in medium density blue polyethylene to BS 6572.

2.16	INTERNAL PLUMBING, PIPEWORK & FITTINGS

Plumbing pipework in floors and walls shall be as detailed within Schedule 9.

All pipework above floors on final connections to sinks, appliances, sanitary ware, within hot presses and in ceiling voids to be made in half hard light gauge copper tubing. Hot pipes must be above cold where routed together and away from mains drinking water lines.

Each connection between maniFold and an item of sanitary ware shall comprise a single length of pipe with no joints but shall include serpentine bends.

The complete installation shall be carried out strictly in accordance with the manufacturer’s instructions and recommendations.

As well as hot and cold water supplies to kitchen sinks the Developer shall provide connections to an adjacent washing machine and also hot and cold water supplies to an agreed location in the kitchen for a future dish washer (including waste pipework).  The Developer shall also provide an external bib tap generally in the rear of each dwelling (house) behind the kitchen.

2.17	CORROSION INHIBITOR

After testing the Developer shall include for each system to be thoroughly flushed out and Furnox corrosion inhibitor added in accordance with the manufacturer’s instructions and recommendations.

At the end of the Defects Liability Period a water sample shall be taken from each system and analysed to ensure that corrosion is not taking place and that the strength of the inhibitor is adequate.

Inhibitors signage shall be displayed on each system.

2.18	VOLUME CONTROLS

The Developer shall supply and install volume control valves to all plumbing appliance connections as detailed with Schedule 16 and incorporating isolator large bore strainer and inline serviceable flow regulator.

2.19	PIPEWORK INSULATION

Pipework within roofspaces, cupboards, hot presses and in voids shall be insulated  comprising closed cell, pre-formed thermal insulating material designated ‘P’ when tested in accordance with BS 476: Part 5 and in accordance with BS 476 Part 7 when installed, to achieve class 1 spread of flame.

Minimum thickness 25mm for all pipes.

All pipes shall include all associated valves, stop cocks, joints and fittings which shall all be fitted with appropriate insulation jackets.

All valves on pipes must be left visible.

Insulation shall comply with the following:

Thermal conductivity not exceeding 0.35 W/m² deg.C at a -6 °C ambient temperature and +7°C water temperature to provide 8 hours protection in normally occupied dwellings.

Manufacturers own adhesive or tape shall be used for jointing.  Tape shall be heavy quality 50mm wide applied on a longitudinal and butt joints plus circumferential lap bands at 300mm minimum centres between butt joints.

Electrical insulation tape is not permitted.

The Developer shall ensure that all insulating material shall have a GWP less than 5.

2.20	NORTHERN IRELAND WATER CONNECTION

The Developer shall be solely responsible for negotiation and application for a new water main connection to each new dwelling within the development. All fees shall be paid under this contract and the Developer shall allow for adequate time for water main installation within his programme.

2.21	BOILERS

Supply and installation as detailed on the drawings and schedules.

The Developer shall include in his tender price for the servicing of each boiler in the tenth month of the Defects Liability Period.

The full heating system shall have a course of water treatment in line with BS7593 ‘Code of Practice for treatment of water in hot water central heating systems’ commissioning stage.  The Developer shall take a further water sample and retreat the system as necessary during the 10 month boiler service to ensure the system is in full compliance at the end of the Defects Period.

All rust inhibitors used within the system shall have been tested to a BuildCert standard and carry the BuildCert performance tested label.

All boiler condensates shall be run in 40mm pvc to connect to the drainage system internally and no external pipe runs shall be permitted.  Safety Blow off’s from boilers shall pass through a tundish which shall have a dry trap fitted to allow direct connection to the drainage system.

All works to gas installations shall be undertaken by Gas Safe Registered Engineers.

All heating installations to be sealed c/w fill loops and expansion vessels as required.

2.22	PROGRAMMERS

The Developer shall include for the provision of the 1no wall mounted programmer in each dwelling as detailed within Schedule 8.

The programmers shall be handed over to the Developer for erection and connection.

2.23	RADIATORS

Supply and installation of wall mounted radiators as detailed on the drawings each complete with the following:-

Manufacturers purpose made brackets for wall mounting radiators

Screwed connections for valves and air cock

Pair of radiator valves.

Suitable backboard to give proper and effective grounds for radiator being hung.

The Developer shall allow for removing and refixing each radiator twice as required to facilitate the finishing of walls etc by other trades.

The radiators shall have a white stove primer with a white enamel finish.

All radiators shall be supplied and installed with chrome plated thermostatic & lockshield radiator valves excluding the radiator within the room where the room thermostat is installed (generally the Hall).

This radiator shall be fitted with a chrome plated wheelhead valve in place of the TRV.

Where there is more than one radiator within the room where the room stat is to be installed the radiator closest to the room stat shall be provided with a chrome plated wheelhead valve in place of the TRV.

2.24	SLEEVES

Where pipes pass through elements of the building structure, i.e. ceiling, partitions etc., they shall be in all cases enclosed concentrically within purpose made sleeves cut from pipes of the same material one or two sizes larger as may be required to provide reasonable clearance.

Such sleeves shall be cut square at the ends, clean and flush with the finished wall and ceiling surfaces.  The sleeve shall not impede thermal movement of the pipe.

2.25	WALLPLATES

Wall plates shall be fitted where pipes pass through floors, ceilings, walls, partitions, etc within occupied areas.

They shall be split pattern, white plastic and secured by grub screws.

2.26	THERMOSTATIC RADIATOR VALVES

Supply and installation as detailed on the drawings of chrome plated thermostatic radiator valves as detailed within Schedule 11.

2.27	THERMOSTATS

The Developer shall include for the provision of 1no wall mounted room thermostat complete with red/green indicator lights and as detailed with Schedule 8.

The thermostats shall be handed over to the Electrical Sub-Contractor for erection & connection.

2.28	GAS PIPEWORK

Supply and installation of gas pipework & fittings as indicated on the drawings and as detailed within Schedule 5.

Pipework in floor screed between gas meter, boiler & cooker locations to be corrugated stainless steel semi-rigid pipe to BS 7838 and shall be laid in single lengths with no joints within the floor screed.

Care shall be taken to ensure that PVC does not come in contact with stainless steel to prevent corrosion.

Final connection to each boiler shall be half hard light gauge copper tubing to BS2871 Part 1 Table X.

The Developer shall ensure that after all  work associated with the gas pipework installation shall only be carried out by an approved Gas Safe registered contractor/tradesman who is registered with Gas Safe for each particular relevant section of work.

The entire gas installation shall be in accordance with the relevant British Standards & Institute of Gas Engineers Utilisation Procedure 1GE/UP/1, 2 & 4.

On completion of the purging and testing procedure, copies of the test results shall be made available and included in the O&M Manuals.

All exposed pipework & fittings shall be painted yellow to BS 4800 08 C35 and identified at regular intervals by means of standard identification labels.

2.29	EXTRACTOR HOODS

Supply and installation as detailed on the drawings of extractor hoods as detailed with Schedule 25.

2.30	SERVICING OF BOILERS

The Developer shall include in his tender price for the servicing of each boiler during the tenth month after the date of Practical Completion as well as at hand over stage. Dating labels shall be affixed to boilers.

Service certificates shall be provided within ten days of the date of the service & a Final Completion Certificate shall not be issued until these have been received.

All gas boiler service certificates shall be in the form of the Gas Safe CP12 Certificate.

The Developer shall be aware that some dwellings may require more than one visit to gain access and some servicing may require to be carried out outside normal working hours including weekends, and the Developer shall all for the same in his tender price.

2.31	PLANNED PREVENTATIVE MAINTENANCE

The Developer shall carry out full planned preventative maintenance on all mechanical services installed as part of this project during the first year after Practical Completion or until the end of the Defects Liability Period whichever is the greater length of time.

2.32	INSULATION

All insulating material shall have a GWP less than 5. This shall include pipe and duct insulation, boiler insulation and cylinder insulation.

2.33	FIRE COLLARS

Intumescent fire collars rated at 120 minutes shall be provided on all ducts and pipes passing through all walls within each dwelling

SECTION 3

SCHEDULES

MECHANICAL SERVICES INSTALLATION

SCHEDULE OF DRAWINGS

DEVELOPER TO CONFIRM

SCHEDULE 2

GAS FIRED COMBINATION BOILERS

Prior to the supply and installation of any items detailed within this schedule within the scheme the Developer shall complete the schedule below detailing the systems provided to allow the Engineer to review their compliance with the performance specification.

|  | Performance Specified | Developers Proposal |
| --- | --- | --- |
| Boiler Manufacturer | Worchester Bosch |  |
| Boiler Model | - |  |
| Boiler Type | Condensing Combination |  |
| Central Heating/Output Range kW | 7.7-30 |  |
| SED BUK Value % | 90.1% |  |
| DHW Output Range kW | 8-32 |  |
| DHW Flow Rate at 35oC DT (litres/minute) | 13.1 |  |
| NOx Classification | Class 5 |  |
| Dry NOx Output | 38 mgpm |  |
| Height (mm) | 760 |  |
| Width (mm) | 440 |  |
| Depth (mm) | 360 |  |
| Lift Weight (kg) | 48.5 |  |
| Noise at maximum operating output at 1 meter distance (dB(A)) | 42 |  |

Gas fired combination boilers are to be used in Apartments.

The boiler shall be wall mounted condensing combination type manufactured and specified according to the boiler efficiency Directive 92/42/EEC.  The boiler shall be complete with the following:

- A heat cell manufactured from 90% aluminium and 10% silicon, delivering higher efficiency and reliability

- A 10-year guarantee on the primary heat exchanger

- Built-in frost protection

- An in-built keep hot facility of at least 2.5 litres volume within an aluminium-silicon heat cell to deliver instantaneous hot water

- An Eco Mode that can override the keep hot facility, ensuring increased efficiency in hot water delivery

- Boiler condenses in DHW mode

- Energy saving modulating pump

- Standard wall mounted frame to allow space for pipes behind the boiler

- Available as natural gas and LPG

- Full range of flexible fluing options in both 60/100mm and 80/125mm including plume deflector as standard

- Plume management kit

- Separate central heating and DHW controls

- Holiday mode

- Integral High Head Pump

The product must be available through mainline and independent merchants with a maximum 5 day lead time.

Technical assistance should be available from the manufacturer via the project manager, service manager, lead service engineer, local sales manager or divisional service manager.

The manufacturer or their local representative shall commission all boilers installed as part of these works.

The boiler installer shall be Gas Safe registered for all points of the installation and shall demonstrate that they have completed at least a 1 day boiler course run by the boiler manufacturer applicable to each type of boiler being installed as part of the works.  This course should cover installation and commissioning of that particular boiler.

A 2 year parts and labour warranty shall be provided from the manufacturer, as well as a 10-year and 5-year anti-scale guarantee on the primary heat exchanger and Domestic Hot water exchanger respectively.

The manufacturer shall enter into on-site client support clinics with tenants to ensure that their new systems are fully understood and advise on how to achieve optimum performance.  Additional support in this area for the client staff should be provided upon request to include the organising of events and associated training.  Easy to read manuals must be provided.

Each boiler shall be supplied complete with a 125mm diameter standard flue kit capable of permitting a 16m horizontal run inclined at 50mm per meter run from the appliance to allow condensate to drain back into the boiler, where applicable flues shall include a flue turret elbow, weather sealing plate and internal plate.

SCHEDULE 3

GAS FIRED SYSTEM BOILERS

Prior to the supply and installation of any items detailed within this schedule within the scheme the Developer shall complete the schedule below detailing the systems provided to allow the Engineer to review their compliance with the performance specification.

|  | Performance Specified | Developers Proposal |
| --- | --- | --- |
| Boiler Manufacturer | Worchester Bosch |  |
| Boiler Model | - |  |
| Boiler Type | Condensing Regular |  |
| Central Heating/Output Range kW | 8 -24 |  |
| SED BUK Value % | 90.2% |  |
| Noise at max. operating at 1m distance db(A) | 41 |  |
| NOx Classification | Class 5 |  |
| Dry NOx Output | 38 mg/kWHr |  |
| Height (mm) | 600 |  |
| Width (mm) | 390 |  |
| Depth (mm) | 270 |  |
| Lift Weight (kg) | 22.6 |  |
| Noise at maximum operating output at 1 meter distance (dB(A)) | 41 |  |

Gas fired system boilers are to be used in houses.

The boiler shall be wall mounted condensing regular type manufactured and specified according to the Boiler Efficiency Directive 92/42/EEC.  The boiler shall be complete with the following:

- A heat cell manufactured from 90% aluminium and 10% silicon, delivering higher efficiency and reliability

- A 10-year guarantee on the primary heat exchanger

- Built-in frost protection

- Have a maximum flow temperature of 820C

- 22mm compression fittings on the flow and return

- Available as natural gas and LPG

- Full range of flexible fluing options in both 60/100mm and 80/125mm including plume deflector as standard

- Plume management kit

- Integral High Head Pump

The product must be available through mainline and independent merchants with a maximum 5 day lead time.

Technical assistance should be available from the manufacturer via the project manager, service manager, lead service engineer, local sales manager or divisional service manager.

The manufacturer or their local representative shall commission all boilers installed as part of these works.

The boiler installer shall be Gas Safe registered for all points of the installation and shall demonstrate that they have completed at least a 1 day boiler course run by the boiler manufacturer applicable to each type of boiler being installed as part of the works.  This course should include installation and commissioning of that particular boiler.

A 2 year parts and labour warranty shall be provided from the manufacturer, as well as a 10-year guarantee on the primary heat exchanger.

The manufacturer shall enter into on-site client support clinics with tenants to ensure that their new systems are fully understood and advise on how to achieve optimum performance.  Additional support in this area for the client staff should be provided upon request to include the organising of events and associated training.  Easy to read manuals must be provided.

Each boiler shall be supplied complete with a 125mm diameter standard flue kit capable of permitting a 16m horizontal run inclined at 50mm per meter run from the appliance to allow condensate to drain back into the boiler, where applicable flues shall include a flue turret elbow, weather sealing plate and internal plate.

SCHEDULE 5

GAS PIPEWORK

All gas pipework from the incoming gas meter to the boiler and cooker shall be corrugated stainless steel semi-rigid pipe with associated fittings.  A gas line of 28mm DN shall run from the incoming meter to the gas boiler with a 15mm DN gas line continuing from the boiler location to a valved connection in the cooker location.

The corrugated stainless steel pipework shall be certified to BS7838 and kite marked to this standard by BS1

Pipework shall be capable of Auto flare fitting.

Pipework shall have a factory fitted yellow PVC jacket

All pipework shall be in compliance with BS6891 and 1GE/UP/2

Quarter turn isolating valves to be fitted at gas meter location / house entry point and at connections to each appliance. Quarter turn isolating valve also at start of line from boiler to future cooker location and quarter turn isolating and blanked end at future cooker location.

SCHEDULE 6

GAS VALVES AND CARBON MONOXIDE SENSORS

A carbon monoxide sensor shall be installed within the room containing the boiler which shall be linked to a gas solenoid valve on the line to the gas boiler.

Co Detector

The alarm to be BS Kite marked to BS EN 50291: 2001 and Gas Safe certified.

The alarm to be capable of wall or ceiling mounting, using a surface mount pattress or in new build, a dry lining box.

The alarm shall utilise a piezo horn that is rated at 85 decibels at 3m and shall have reset & test buttons.

The alarm shall incorporate 3 LED’s: a green LED will be steady on when AC power is present and will flash every 7 seconds when in the battery only mode; a red LED will flash in unison with the sounder pattern for either a smoke or CO incident, flash once every 30 seconds if the alarm needs service or be steady on if the alarm is in error mode; an amber LED will illuminate if that unit is the originating alarm in a CO incident. The alarm shall indicate a low battery warning by issuing a brief alarm chirp and the red LED will then flash approximately every 15 seconds.

When the alarm detects carbon monoxide, the alarm pattern will be four (4) short beeps – followed by five (5) seconds of silence – followed by four (4) short beeps.

The unit shall include a peak level memory feature that will store the peak CO level sensed since the alarm was last reset. The peak CO level stored in the unit’s memory shall be displayed (in ppm) on the digital display by pressing the appropriate button on the unit.

The alarm shall incorporate an Interconnect feature that allows it to respond to a smoke/heat incident when interconnected with Smoke or Heat alarms. During a smoke/heat incident, the alarm will sound in the required, repetitive manner of a smoke alarm – three (3) beeps, a pause, three (3) beeps, a pause. The digital display will also scroll the word “Fire” across the display.

The whole alarm shall be guaranteed for 6 years.

The alarm will be shipped in a sealed polythene sleeve within its outer packaging, to prevent any contamination during transportation, and shall include separate User & Installer manuals.

The alarm shall be installed in accordance with the manufacturer’s instructions, BS EN 50292, Part P of the Building Regulations and the latest IEE Regulations i.e. 17th edition [BS7671].

Solenoid Operated Gas Shut Off Valve

The valve shall be closed by power interruption in less than 1 second with automatic reset so that electrical power alone shall re-open the valve.  The valve shall be electrically connected to the Co Detector / Alarm.

Valves shall be manufactured to Class A in accordance with EN161 and DIN3391-3394 standards. Valves shall be protected to IP54.

Valves should be 240v AC

Valves shall be capable of either vertical or horizontal mounting.

SCHEDULE 7

OIL FIRED BOILERS

Prior to the supply and installation of any items detailed within this schedule within the scheme the Developer shall complete the schedule below detailing the systems provided to allow the Employers Agent to review their compliance with the performance specification.

|  | Performance Specified | Developers Proposal |
| --- | --- | --- |
| Boiler Manufacturer | - |  |
| Boiler Model | - |  |
| Boiler Type | Condensing External |  |
| Central Heating/Output Range kW | 18-25 |  |
| SED BUK Value % | 93.2% |  |
| Height (mm) | 950 |  |
| Width (mm) | 640 |  |
| Depth (mm) | 770 |  |
| Weight (kg) | 195 |  |
| Burner Manufacturer |  |  |
| Total Primary Water Capacity (litres) | 69 |  |
| Flue diameter (mm) | 125 |  |

The boiler shall be an external cabinet mounted condensing type manufactured and specified according to the boiler efficiency Directive 92/42/EEC.  The boiler shall be complete with the following:

- A 5-year guarantee on the primary heat exchanger

- A stainless steel condensing heat exchanger with a 10-year guarantee

- A minimum of 69 litres Primary Water Capacity

- Built-in frost protection

- Pre-heated thermal store

- Maximum hot water rise at optimum flow rate of 40oC

- A full range of spare parts required to service the boiler for at least 10 years

- Central Heating Flow and Return connections at 22mm

- Robustness through a 5mm mild steel inner primary heat exchanger surface and a 3mm outer shell.

The product must be available through mainline and independent merchants with a maximum 5 day lead time.

Technical assistance should be available from the manufacturer via the project manager, service manager, lead service engineer, local sales manager or divisional service manager.

The manufacturer or their local representative shall commission all boilers installed as part of these works.

The boiler installer shall be OFTEC registered for all points of the installation and shall demonstrate that they have completed at least a 1 day boiler course run by the boiler manufacturer applicable to each type of boiler being installed as part of the works.  This course should cover installation and commissioning of that particular boiler.

A 2 year parts and labour warranty shall be provided from the manufacturer, as well as a 10-year and 5-year anti-scale guarantee on the primary heat exchanger.

The manufacturer shall enter into on-site client support clinics with tenants to ensure that their new systems are fully understood and advise on how to achieve optimum performance.  Additional support in this area for the client staff should be provided upon request to include the organising of events and associated training.  Easy to read manuals must be provided.

Each boiler shall be supplied complete with a 100mm diameter balanced flue kit to meet all current building regulations in terms of discharge and shall be located in line with OFTEC requirements for spacing and location of flues.

SCHEDULE 8

ELECTRONIC TIME CONTROLLERS

All heating boilers are to be provided with electronic time controllers.

The controllers shall be manufactured by the boiler manufacturer and shall have a weather compensation function, with an external temperature sensor used to enable the controller to vary the boilers output based on outdoor temperature. Weather compensators shall be directly mounted to gas boilers.

The controller shall provide separate heating and hot water control and shall provide seven day time control.

The controller shall have a “holiday function” allowing normal heating and hot water times to be suspended for the duration of a holiday and resumed after.

A separate two channel time clock interlinked to the gas boiler shall be provided to allow for separate time and temperature control of two separate heating zones as shown on drawing M100.

The controller shall also be complete with an advance button and a +1 hour button to allow manual override on any channel.

Controllers shall have dimensions 158mm wide x 98mm high x 36mm deep.

Controller shall conform to the following:

- Electromagnetic compatibility Directive (2004/108/EC)

BS EN 60730-1:2000, BS EN 60730 - 2-7:1992

- Low Voltage Directive (2006/95/EC)

BS EN 60730-1:2000, BS EN 60730 - 2-7:1992

Where controllers are provided solenoid valves shall be provided by the same manufacturer to allow separate control/isolation of the each heating zone and primary hot water circuit.

Heating to each dwelling heating zone shall have a wall mounted room thermostat controller.  Final locations shall be agreed on site prior to commencement of installations.  Thermostats shall be of a lockable type and shall have red and green indicators.

System boilers must be fitted with integral diverter valves for use with this control configuration.

Heating controllers shall have an in built “Service Interval Timer” function such that if it is not reset during the boiler commissioning visit the clock shall shut down at the end of month 13.

SCHEDULE 9

PIPE IN PIPE PIPEWORK

All pipe connections from maniFolds to radiators and sanitary fittings shall be flexible plastic pipe in conduit manufactured to BS7291 – 1:2001 (class ‘S) and BS7291 – 3:2001.  All such connections must be single pipe runs with no pipe joints and/or connections below floors or screeds.

Pipework shall incorporate an oxygen diffusion barrier to protect the system from oxygen permeation.  The pipe shall have a barrier that means the oxygen diffusion requirements of DIN4726.

The pipe in conduit system to be used throughout shall in all cases allow each pipe to be withdrawn and replaced including through solid floors and walls.

Pipe in conduit shall be laid with the fewest possible bends and the largest possible bend radii.

In concrete floors/screeds conduits shall be secured to the reinforcing steel with metal or plastic ties at 400mm intervals.

In timber studs and joists conduits shall be secured using proprietary clips placed at 400mm intervals.

Where pipe bends, the conduit shall be supported using a pipe bend support or at either side of the bend using suitable clips.

Radiator connection guides shall be used in all cases to take pipes to finished floor level and connect to all radiators and all sanitary ware connections.  In timber/joisted floors where it is not possible to use a radiator connection guide a pipe bend support shall be used to bend the pipe through 90o out of the floor directly onto the radiator or sanitary appliance.  From this point white radiator connection guides shall be provided above floor to final connections.

Radiator connection guides shall have white polypropylene guides with RAL 9016 (white) powder coated aluminium to all radiators.

Radiator connection guides shall have white polypropylene guides with chromed aluminium to all sanitary appliances.

All pipes shall have supports/clips at no more than 150mm from connections, valves and other controls.

Hydraulic pressure testing shall be undertaken in accordance with BS6700:1997 before the system is taken into operation and both before and after floor screeds are poured.  The test pressure shall be 10bar.

SCHEDULE 10

RADIATORS

All radiators shall be panel radiator manufactured and tested to BS EN 442.  Each radiator shall carry the BS Kitemark certifying independent approval of heat output and verifying production under BS EN 9001. All radiators to comply with BS 3528 and Kitemarked.

Radiators shall have central connections to the underside of the radiator and equipped with an integrated valve arrangement. Each radiator shall be supplied with a fitted valve top and a thermostatic head fitted directly to the built in valve. Refer to drawing M100 for further details.

All radiators are to be at least 25mm below sill level with at least 100mm clearance from floor to under side of radiator.

All radiators shall be provided with a 10 year manufacturer’s guarantee against defects caused by faulty materials or manufacturer.

All radiators shall be complete with primer coat and epoxy polyester finish coat in white (RAL 9016) to all surfaces (front and rear) allowing the radiator to be fitted without further painting.

Radiators shall be installed mounted on concealed wall mounting brackets suitable for the size and weight of the particular radiator.

Radiator shall be capable of operation up to 100oC.

Radiators shall be capable of operation to 5.4bar and be tested to 7bar.

It should be noted that there may be occasional radiators that vary from the above however this shall only be where they are specifically noted on drawings.

SCHEDULE 11

RADIATOR VAVLES

Each radiator shall be fitted with a thermostatic radiator valve on the top of the radiator which is integral to the radiator body such that it is within Lifetime Homes requirements. The only exclusion to this is the radiator in the room where the room thermostat is fitted shall have a handwhell valve in place of the thermostatic radiator valve.

Where there are multiple radiators in the room, where the room thermostat is to be fitted then the closest radiator shall be complete with a handwhell valve and all others shall be complete with programmable radiator control valves.

All valve bodies shall be reversible and bi-directional and include a flow selectable feature to ensure no risk of water hammer.

All valves shall be manufactured in factories assessed and certified to ISO9001.

SCHEDULE 13

GAS BOILER FLUES

Each boiler shall be supplied complete with a matching flue.  The entire flue bit shall be supplied by the boiler manufacturer.  The boiler and flue shall be sized and installed to permit a 16m horizontal run inclined at 50mm per meter run from the appliance to allow condensate to drain back into the boiler.  Where applicable flues shall include a flue turret elbow, weather sealing plate and internal plate.

Where gas flumes are to be run in voids or above ceilings the Developer shall provide a 300mm x 300mm access hatch at each flue joint and/or fitting to allow full future inspection.

The Developer shall have the boiler manufacturer’s representative and commissioning engineer visit site prior to installation to confirm, in writing, that the boiler and matching flue to be installed are in line with both the manufacturer’s recommendations and Gas Safe Regulations.

SCHEDULE 15

HOT WATER CYLINDERS

Prior to the supply and installation of any items detailed below within this schedule within the scheme the Developer shall complete the schedule below detailing the systems provided to allow the Engineer to review their appliances with the performance specification.

|  | Performance Specified | Developers Proposal |
| --- | --- | --- |
| Cylinder Manufacturer |  |  |
| Cylinder Model |  |  |
| Nominal Capacity | 170 litres |  |
| Coil Capacity | 17kW |  |
| Cylinder Diameter | 579mm |  |
| Cylinder Height | 1384mm |  |
| Immersion Heaters | 3kW |  |
| Cylinder Heat Loss | 1.42kwHr/day |  |

Cylinders shall be duplex stainless steel tested to 12bar.  Each electrical immersion heaters shall be supplied with regulation thermostat and dual pole thermal cut-out.

Cylinder thermostats shall have ½” T & P relief valve and shall be complete with inverted control kit.

Cylinders shall have a 25 year tank guarantee on all electrical components.

Cylinder coils shall be manufactured to BS1566 and exceed a match CH&SS Best Practice for heat recovery.

No sacrificial anode shall be used / required to provide corrosion resistance.

Insulation shall be a 60mm thick void free layer of high performance polyurethane foam and shall have an outer casing.

The base of the cylinder shall be fully insulated.

Hot water cylinder blow off’s must be taken through a tundish and dry trap before being run in 32mm copper to the closest 100mm soil line.

SCHEDULE 16

FLOW REGULATION VALVES

All plumbing appliances shall be fitted complete with ¼ turn isolating valve at final connections and flow regulation isolating valves at all maniFold connections to allow all plumbing outlets to have their flow regulated.

Flow regulation ball valves shall be 15mm combination filtration, isolating and flow regulating devices for use an individual outlets to maintain the flow rate at a desired level.  The valve shall incorporate a flow regulator fitted downstream of the isolator and filter.

Valve bodies shall be cast DZR brass, caps shall be DZR brass, strainers stainless steel, balls chrome plated brass and seats PTFE.  Valves shall be WRAS approved.

Flow rates shall be set as follows:

| Wash hand basins 1.7l/m |  |
| --- | --- |
| Shower 6l/m |  |
| Kitchen Taps 2.5l/m |  |
| Baths 6l/m |  |
| Sinks 1.7 l/m |  |

SCHEDULE 17

SINKS

Sinks shall all be single bowl single drainer 1.2mm thick, grade 316 (1.4404 BS EN 10088) and BS 1244 Parts 1 and 2  stainless steel with brushed option finish.

The sink shall be 1000mm long x 500mm wide x 150mm bowl depth.

The unit shall be complete with two tap holes and a 38mm BSP vulcathene waste and plug drainer and bowl positions shall be as shown on the final agreed kitchen layouts.

The single inset sink and drainer shall be in heavy gauge stainless steel (Kitemarked to British Standards) to be designed with integral support to prevent sagging of sink unit as a consequence of improper use. Support rail to be provided to the underside of the sink drainer.

Sinks shall be complete with a lever action taps.  The sink shall be manufactured to BS1244 and Kitemarked to the British Standard.

The sink shall be compete with an earthing lug and shall have integral support to prevent sagging.

Valve bodies shall be cast DZR brass, caps shall be DZR brass, strainers stainless steel, balls chrome plated brass and seats PTFE.  Valves shall be WRAS approved.

SCHEDULE 18

WASH BASINS

Within main bathrooms / shower rooms a 650mm wide x 500mm deep white vitreous china wash basin and pedestal shall be provided.

Within the secondary shower rooms / bathrooms generally located on the ground floor of dwelling a 450mm wide x 360mm deep white vitreous china wash hand basin and pedestal shall be provided.

Wash basins shall have two tap holes complete with lever action taps (hot left and cold right when facing basin).

Each basin shall be complete with:

- Basin bolted to wall

- Pedestal bolted to floor

- Overflow

- 32 chrome plated waste outlet with plug, CP chain and stay.

- 32 white plastic bottle trap with 75mm deep water seal.

SCHEDULE 19

WC’S

All WC’s shall be white vitreous china close coupled suites comprising of the following:

- WC pan screwed to floor having horizontal outlet

- Close coupled screw to wall cistern

- 6 / 4 litres dual flush with lever action handle. Handle to be between the centreline and the side of the cistern furthest away from the adjacent wall.

- Outlet connector

- White heavy duty seat and cover

- Domex screws

SCHEDULE 20

BATHS

Baths shall be 1700mm x 700mm slip resistant with integral hand grips.

Baths shall be standard gauge (1.5mm) pressed steel white enamelled to BS1344 (0.3mm).

The bath shall have 2 tap holes and be complete with legs.

Baths shall be complete with low flow, 2 hole bath shower mixer set, rated at 6l.

The bath shower mixer shall be of brass / copper material.

The bath shower mixer hot and cold taps shall be lever action.

The bath mixer shall have a shower kit comprising chrome plated flexible hose, shower hose and wall fixing bracket. Flexible hoses shall be 800mm in length maximum.

Baths shall include side and end panels as supplied by the bath manufacturer.

Baths shall have overflows at heights to limit the bath water volume to 156litres.

All baths and panels to be white.

SCHEDULE 21

SHOWERS

Shower mixers shall be surface mounted with concealed 15mm hot and cold connections recessed into walls.  Valve bodies shall be DZR brass and chrome plated with zinc alloy and chrome plated individual temperature and flow control knobs.

Shower control inlets shall contain check valves and fitters, both housed within readily accessible cartridges for easy maintenance.

The shower outlets shall be a 15mm external union.

Standard connections are to be hot-left, cold-right, outlet-bottom when facing the control.

Showers shall be in compliance with BS7942, EN1111, EN1287 and be WRAS approved.

Showers shall have a top lever for control of temperature and a bottom lever for control of flow.

Temperature controls shall allow the user to select the required temperature within the range available.  An integral stop shall limit the maximum temperature to a present level of 43oC.

At a flow rate of 20 litres per minute the maximum pressure loss shall be 0.5bar and at 30 litres per minute shall be 1.5bar.

Showers shall be complete with a heavy duty shower kit comprising of the following:

- Robust grab rail

- 1.25m flexible hose

- Brass slide bar

- Clamp bracket assembly

- Hose retaining ring

- Adjustable spray handset )5 function)

- Soap dish

The shower and shower kit shall be suitable for high pressure operation.

Under this contract each shower shall include for a level dec shower unit.  Shower trays shall be as follows:

- 1300mm x 800mm

- Made from toughened GRP

- 22mm in depth

- Impervious to water

- Have top accessible gully 127mm deep with 75mm seal and horizontal outlet

The shower tray shall be trimable to up to 30mm.  Each shower tray shall be supplied with both a full length curtain (and pole) and a shower door enclosure.  Shower enclosures / doors shall be ‘L’ shaped with a pair of 400mm bi-Folding doors meeting on the corner.

Shower enclosures shall include for the following:

- 750mm high

- 180 o rise and fall hinges (10mm lift)

- 360o full length interesting hinges

- Powder coated aluminium frames

- Anti-shatter PETG panels

- Compensator adjustment up to 20mm to provide level installation

- Suitable for use with shower tray

Each shower shall be complete with a shower seat as follow

- CE approved (BS EN 12182:1999)

- Wall mounted seat with fine/coarse height adjustable support legs

- Folds upwards when not in use for greater useable shower area

- Removable ribbed grey soft pads for ease of cleaning

- Armrests swivel independently and offer lateral stability

- Facilitates cross transfer

- Easy to install with a weight capacity 190 kg / 30 stone

- Seat Width 460mm / Seat Depth 380mm / Depth from wall 550mm

- Height adjustable from 465 to 615mm (padded) / pad height 20mm

- Height of backrest from seat 450mm

- Padded.

SCHEDULE 22

SHOWERS FORMERS

Under this contract each shower and future shower shall include for a level dec shower unit.  Shower trays shall be as follows:

- 1300mm x 800mm

- Made from toughened GRP

- 22mm in depth

- Impervious to water

- Have top accessible gully 127mm deep with 75mm seal and horizontal outlet

Even when a shower is described as “Future” the tray / former shall be supplied and installed now.

The shower tray shall be trimable to up to 30mm.

Where the showers are for future use the gully shall be a 160 Dia. Nickel Bronze 'P' Trapped Access Cover Assembly, for use with flexible sheet floor covering (eg. vinyl) (2"socket outlet.), with 2" Socket BS 5255 dia. horizontal outlet. It shall be a compact, lightweight, ‘’trapped gully with solid cover (gasketed) for use in areas decked with sheet floor covering such as vinyl, up to 3.5mm thickness. The Gully shall also be available with a with peripheral slot drainage for future use.

SCHEDULE 23

THERMOSTATIC MIXING VALVES

All hot water connections to baths shall be fitted with thermostatic mixing valves with BuildCert TMV3 Thermostatic Mixing Valve Scheme approval to limit the temperature to 40oC.  A thermostatic mixing valve shall also be fitted to the main hot water flow from cylinder or combination boiler limiting the maximum flow temperature to 60oC. These valves shall be complete with non return valves.

SCHEDULE 24

SOILS AND WASTES

Separate waste and soil lines shall be run from each appliance to main vertical soil stacks.  Under no circumstances shall soils and waste lines be combined.

All soil stacks shall be run full bore to 300mm above roof exit level.  No air admittance valve shall be used.

Where soil and waste pipes pass through floor and fire walls including apartment walls they shall be fitted with fire collars intumescent fire sleeves to provide 1 hour fire rating.

Soils and wastes shall be installed to the following criteria:

| Appliance | Diameter DN | Min. trap seal depth mm | Max length (L) of pipe from trap outlet to stack m | Pipe gradient | Max. numbers of bends | Max. drop (H) m |
| --- | --- | --- | --- | --- | --- | --- |
| Washbasin, bidet (30mm diameter trap) | 30 | 75 | 3.0 | 1.8 Min | 2 | 3.0 |
| Washbasin, bidet (30mm diameter trap) | 40 | 75 | 3.0 | 1.8 Min | No Limit | 3.0 |
| Shower, bath | 40 | 50 | No Limit | 1.8 Min | No Limit | No Limit |
| Kitchen sink (40mm diameter trap) | 40 | 75 | No Limit | 1.8 Min | No Limit | No Limit |
| Household dishwasher or washing machine | 40 | 75 | No Limit | 1.8 Min | No Limit | No Limit |
| WC with outlet greater than 80mm | 100 | 50 | No Limit | 1.8 Min | No Limit | 1.5 |
| Bath drain, floor drain | 50 | 50 | No Limit | 1.8 Min | No Limit | No Limit |
| Floor drain | 70 | 50 | No Limit | 1.8 Min | No Limit | No Limit |

SCHEDULE 25

WHOLE HOUSE VENTILATION

Prior to the supply and installation of any items detailed within this schedule within the scheme the Developer shall complete the schedule below detailing the systems provided to allow the Engineer to review their compliance with the performance specification.

|  | Performance Specified | Developers Proposal |
| --- | --- | --- |
| Unit Manufacturer | - |  |
| Unit Model | - |  |
| Unit Volume | 56l/s @ 200Pa |  |
| Specific Fan Power | 0.40 w/l/s |  |
| Heat Recovery Efficiency | 91% |  |
| Weight | 10kg |  |
| Dimensions | 621mm W x 894mm H x 432mm D |  |

The data given above shall be as published in the Standard Assessment Procedure 2005 – Appendix Q as tested by BRE.

The unit shall be manufactured of impact resistant expanded polypropylene with an ABS plastic front panel and be complete with C2 synthetic filters.

The whole house ventilation unit shall come with a 5 year guarantee on all compartments.

The whole house ventilation unit shall be complete with the following

- G3 Grade Filter protection on fresh air inlet (from outside) and system extract (from dwelling). The Heat Exchanger & Filters shall be fully accessible for future reference.

- Provision of anti-vibration mounts to prevent vibration being transmitted to structural beams and condensate drain connection.

- The units shall use Low Energy, high efficiency EC motor with sealed for life bearings and backward curved centrifugal fans.

- The HRV unit shall function safely within the temperature range of -20 to +50 Degrees Celsius

- The Developer shall supply 2nr sets of additional filters per unit.

- The system shall have air-flow sensors on both supply and extract valves (to the dwelling), to ensure correct airflow is maintained at all times, even when the filters start to block.

- All duct connections shall be top entry.

The whole house ventilation system shall have the following controls:

- Set back and boost facilities on separate supply and extract fans

- PIR controls for each bathroom, shower room and wc to trigger automatic boost facility with over run timer set at 15 minutes.

- Separate Humidity stats which can be set to 60% RH and are left non adjustable at high level (300mm from ceiling) within all bathrooms and shower rooms / toilets.

- Kitchens shall be provided with a boost timer giving a range of boost times from 1/4hr to 2hrs. This unit shall have the facility to be instantly cancelled or reset and the 1/4hr LED shall flash warning of time out. The booster shall have LED’s indicating boost times of 2, 1, ½ and ¼ hours.

All boost inputs from remote devices shall be taken to the WHV unit by 240v live and earth cables.

All wiring and control switches etc shall be supplied under the electrical sub-contract however the MVHR unit shall be capable of accepting all signals detailed above and mechanical and electrical sub-Developers shall liaise fully to ensure that all the above requirements are met prior to ordering or installing any items.

Roofspace Ducting

Within roof spaces ALL ducting shall be insulated foam vapour resistant EPE to the following specification:

- Self Extinguishing: Class B1 DIN 4102

- Density: 50kg/m³

- Heat Transfer coefficient:0.040 W/m°K per DIN 52613 (by 0°C)

- Temperature range: -40°C to +60°C

Where ductwork changes to drop to below in houses it shall be in rigid plastic with 40mm thick mineral wool insulation to match the insulation properties detailed above within the actual roofspace.

It shall not be acceptable to use general roofspace mineral wool laid in roofspaces for fabric heat loss control to be used as the insulation for ventilation ducting.

Apartment Intake and Discharge Ducting

Within apartments intake ducting and discharge ducting to outside from the unit shall be vapour resistant EPE as above.

Ducting to Other Areas

Where ductwork runs in areas other than roofspaces it shall be rigid plastic ducting.

Bends shall be minimised to ensure adequate air flow and least resistance bends shall have a minimum Fold at least the same as the diameter of the ducting used.

All ducting shall be insulated with at least 25mm of insulating material with a thermal conductivity of 0.04W/mk and cold/supply air ducts hall be wrapped with a vapour barrier outside of the insulation.

Where ducts rise vertically they shall be fitted with condensation traps.

Duct Joints

Ducting joints shall be both screw fixed taped using silver foil type tape (not duct tape).

Final Connections

Where possible all final connections shall be rigid and short flexible final connections shall only be used where it is impossible to make a rigid connection. Where flexible ducting has to be used it shall be only in very short lengths to connect to units and diffusers (no more than 300mm).  Any flexible ducting shall be pulled taut to minimize resistance. Vents

General Requirements

Systems shall be supplied, installed and commissioned in line with the recommendations of Standard Assessment Procedure 2005 – Appendix Q MVHR Installation Guide.

Inlet and discharge ducts for the system shall be at least 3m apart and shall be a terminate in a 200mm x 200mm powder coated wall grille on the gable wall of houses and top floor apartments and in 400mm x 60mm powder coated grille.

All ducting joints shall be double sealed using proprietary sealant within joints and duct taped twice around the entire joint.

Condensate lines from all whole house ventilation units must be run internally via a dry trap to connect to the internal waste system of the dwelling. Under no circumstances shall external condensate discharges or lines be accepted.

All MVHR units must come with all ventilation connections top entry to the unit as this is required to ensure they fit into the confined space available in some instances and in order to ensure continuity across the scheme.

Duct routes are for pricing information only and indicative. The Developer must engage a whole house ventilation specialist who shall design and draw up all duct runs and submit 1:50 plans and proposals for agreement with the consulting engineer prior to fabrication. No extra costs shall be accepted for duct work route refinement to suit the constructed dwellings. Where timber framed dwellings are to be constructed the timber frame manufacturer and ventilation supplier shall liaise fully to ensure that all ducts required fit within the dwellings constructed. Joist and timber directions are shown on drawings and timber frame manufacturers must ensure that where these are altered the changes are suitable for accommodating alternative duct routes and these shall be allowed for on the plans provided to the consulting engineer.

Locations of main MVHR units shall be easily accessible for maintenance and flooring / boarding shall be provided in houses from the roofspace trap door to the unit. Where possible the MVHR unit shall be provided on the wall of the roofspace over the landings / bathrooms.

Maintenance

One month after handover the Developer shall return and replace all filters within ventilation systems and units.

One month before the end of the defects liability period the Developer shall return to site and replace all filters within ventilation systems and units.

Noise

The entire system shall be capable of providing an overall noise level of NR25 in bedrooms and NR30 in all other rooms when on boost. Where necessary and depending on the unit the Developer proposes to install attenuators shall be provided to ensure these noise levels are met.

Air Valves

All supply and extract air valves shall be 125mm and lockable to prevent tamper after commissioning, (these are to be locked at the end of commissioning).Supply valves shall be manufactured to have a predominant horizontal throw of air.

Air valves shall not be sited over areas where plans shown occupants are likely to be sedentary for prolonged periods of time.

Documentation to be handed over to the end user

The following information shall be provided where relevant:

- Design statement that sets out the key characteristics of the system provided along with specific, non technical information on how the system should be used

- Manufacturers contact detail

- Use of air inlets for background ventilation

- Location of and setting automatic controls

- Location and use of on/off and boosts settings

- Instructions on how cleaning and maintenance should be carried out including filters

- Location of filters

- Recalibration or checking of sensors and their location

The O&M manual should also contain relevant manufacturers literature supplied with the system or with individual components of the system.

The three part sheet detailed within the commissioning section below should be signed and completed for each dwelling and included in the O&M manual.

Competent Persons

All installation and commissioning should be undertaken and completed by a person who is registered on the “Competent Persons Register” for domestic whole house ventilation. This shall be deemed to be a BPEC Accredited Person. The Developer prior to commencement of works on site shall provide the registration card of the competent person the are engaging to undertake the works to demonstrate that the are competent to undertake the work associated with the domestic mechanical ventilation heat recovery system. No works shall be undertake by a person who is not suitably qualified.

Commissioning should be undertaken fully in line with HM Governments “Domestic Ventilation Compliance Guide”.

Checking design against measured air flow rates

The measured air flow rates should be recorded as part of the testing and commissioning procedures. The measured values should be set against design values. Compliance with the design will be met if the measured air flow rates for are equal to or greater than the design value. If any measured value is less than the design value adjustments shall be made to correct the system and all air flows re-measured until they all meet the design values.

Measurement of air flows should be performed using equipment that has been calibrated at a UKAS accredited calibration centre. Calibration should be performed annually for each air flow device to record final air flow rates.

To demonstrate compliance all three parts of the following checklist and test sheets shall be fully completed for each and every dwelling.

System Details and declarations

| - Installation Address Details |  |
| --- | --- |
| Dwelling number |  |
| Street |  |
| Locality |  |
| Town |  |
| County |  |
| Post Code |  |
| 1.2 Installation Details |  |
| Manufacturer |  |
| Model Number |  |
| Serial Number |  |
| Location of Fan Unit |  |

Installation Details

| 2.1 Installation Checklist – General |  | Tick as appropriate |  |
| --- | --- | --- | --- |
| Has the system been installed in accordance with manufacturers requirements ? |  | Yes | No |
| Have relevant system installation clauses been followed as detailed in DVCG Tables 1, 3, 5 and 7 as applicable |  | Yes | No |
| Type of ductwork installed (e.g. rigid, semi rigid) |  |  |  |
| If and deviation from Tables 1, 3, 5 and 7 these should be detailed here |  |  |  |
| Description of installed controls (e.g. timer, central control, humidistat, PIR etc) |  |  |  |
| Location of manual / override controls |  |  |  |

| 2.2 Installation Engineers Details |  |
| --- | --- |
| Name |  |
| Company |  |
| Address Line 1 |  |
| Address Line 2 |  |
| Telephone Number |  |
| Post Code |  |
| Signature |  |
| Competent Person Scheme Registration Number |  |
| Date of Installation |  |

Installation Details

| 2.3 Visual Inspections |  |  |
| --- | --- | --- |
| Total installed area of background ventilators in dwelling |  | mm |
| Total floor area of dwelling |  | m2 |
| Have all background ventilators been left in open position | Yes | No |
| Have the correct number and location of fans / terminals been provided | Yes | No |
| Is the installation complete with no obvious defects | Yes | No |
| Do all internal doors have sufficient undercut to allow air transfer between rooms (i.e. 10mm over and above final floor finish)? | Yes | No |
| Has all protection / packaging been removed (including from background ventilators) such that the system is functional? | Yes | No |
| Has the ductwork installation been installed in such a manner that air resistance and leakage is kept to a minimum ? | Yes | No |
| Are the correct number and size of background ventilators been provided | Yes | No |
| Has the entire system been installed such that there is sufficient access for routine maintenance and repair / replacement of components? | Yes | No |
| Have appropriate air terminal devices been installed to allow system balance | Yes | No |
| Has the heat recovery unit and all ductwork been effectively insulated where installed in unheated spaces? | Yes | No |
| Condensate connection is complete and drains to an appropriate location ? | Yes | No |
| Upon initial start up was any abnormal sound or vibration experienced or unusual smells detected? | Yes | No |

| 2.4 Inspectors Details |  |
| --- | --- |
| Name |  |
| Company |  |
| Address Line 1 |  |
| Address Line 2 |  |
| Telephone Number |  |
| Post Code |  |
| Signature |  |
| Competent Person Scheme Registration Number |  |
| Date of Inspection |  |

Air flow test and commissioning details

| 3.1 Test Engineers Details |  |
| --- | --- |
| Name |  |
| Company |  |
| Address Line 1 |  |
| Address Line 2 |  |
| Telephone Number |  |
| Post Code |  |
| Signature |  |
| Competent Person Scheme Registration Number |  |
| Date of Test |  |

| 3.2 Test Equipment |  |  |
| --- | --- | --- |
| Schedule of air flow measurement equipment used (model and serial) |  | Date of last UKAS calibration |
| 1. |  |  |
| 2. |  |  |
| 3. |  |  |

| 3.3 Air Flow Measurements (Extract) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Room Reference | Measured Air Flow High Rate l/s | Design High Rate l/s | Measured Air Flow Low Rate l/s | Design Low Rate l/s |
| Kitchen |  |  |  |  |
| Bathroom |  |  |  |  |
| GF WC |  |  |  |  |
| Utility |  |  |  |  |
| Other |  |  |  |  |
| Other |  |  |  |  |

| 3.4 Air Flow Measurements (Supply) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Room Reference | Measured Air Flow High Rate l/s | Design High Rate l/s | Measured Air Flow Low Rate l/s | Design Low Rate l/s |
| Living |  |  |  |  |
| Dining |  |  |  |  |
| Bedroom 1 |  |  |  |  |
| Bedroom 2 |  |  |  |  |
| Bedroom 3 |  |  |  |  |
| Bedroom 4 |  |  |  |  |
| Other |  |  |  |  |
| Other |  |  |  |  |

| 3.5 Commissioning |  |  |
| --- | --- | --- |
| Have controls been set up in accordance with manufacturers recommendations | Yes | No |
| Have all distribution grilles been locked to prevent unauthorised adjustment | Yes | No |

SCHEDULE 26

COOKER HOODS

All cooker locations shall be provided with re-circulating cooker hoods.  Kitchen cooker hoods shall be stainless steel chimney extractor hoods with an extending chimney to fit varying ceiling heights.  Cooker hoods shall have twin fans to provide three speeds of 340/420/460m3/hr.  A washable metal grease filter and charcoal filter shall be supplied as a part of the unit.

The unit shall be 600mm in width, include 2 x watt lamps, have top exhaust facility and operate at 230v/50Hz.

Hoods shall have washable grease filters.

Where recirculation hoods are provided there shall be ample ventilation grilles provided within them to provide adequate recirculation.

Ductwork shall be rigid throughout and in line with HM Government “Domestic Ventilation Compliance Guide”.

ELECTRICAL SERVICES INSTALLATION

SPECIFICATION

INDEX

### 1	Products, Materials and Works Standards

### 1	Requirement

2.1	Introduction

2.2	Scope of Work

2.3	Installation Regulations

2.4	Samples

2.5	Coordination and Integration

2.6	Inspection, testing, commissioning and setting to work

2.7	Operating Instructions and Documentations

2.8	As Installed Drawings

2.9	Personnel Instruction

2.10	Home User Guide

2.11	Servicing and Testing during the Defects period

2.12	System of Supply and Design Information

2.13	Earthing

2.14	System of Cabling and Wiring

2.15	Mains Supply

2.16	General Lighting Installation

2.17	External Lighting Installation

2.18	Street Lighting Installation

2.19	General Purpose Power Distribution

2.20	Fire and CO alarm Installation

2.21	Communal Fire Alarm Installation

2.22	TV Installation

2.23	Communal TV aerial installation

2.24	Door Entry System

2.25	Access Control System

2.26	Closed Circuit Television System

2.27	Warden Call

2.28	Telephone wiring

2.29	Lift Installation

2.30	Electrical Installations in Connection with Mechanical Services

2.31	Photovoltaic System

2.32	AOV smoke vent installation

### 3	Schedules

Schedule A – Schedule of Luminaires

Schedule B – Schedule of Equipment

Schedule C – Schedule of Drawings

##### SECTION ONE

PRODUCTS, MATERIALS & WORKS STANDARDS

SECTION ONE

PRODUCTS, MATERIALS AND WORKS STANDARDS

1.1	Requirement

The Electrical Services Installation is to be carried out by Developer in accordance with Performance Standards set in this specification.

##### SECTION TWO

PARTICULAR SPECIFICATION

FOR ELECTRICAL SERVICES DESIGN

SECTION TWO

PARTICULAR SPECIFICATION

2.1	INTRODUCTION

The requirement consists of the supply, erection, connection, testing and setting to work of the complete Electrical Services Installations, associated with the proposed works, to ensure a complete and compliant installation in all respects.

This Specification should be read in conjunction with the under noted documents:

- DFC Housing Association Guide

2.2	SCOPE OF WORK

The Developer shall deliver to site, install, test and commission all items necessary for the complete electrical installation of the following:

- Application to, and negotiation and liaison with NIE regarding new incoming supplies and metering to each dwelling, communal area and street lighting pillar, and any associated diversions of existing cables and equipment. The permanent electricity supply must be provided for commissioning of the lift installation to suit the proposed programme of work and commissioning.

- Application to, and negotiation and liaison with BT and Virgin Media regarding new incoming services to each dwelling and item of equipment requiring telephone connection, and any associated diversions of existing services. Live telephone service must be provided for commissioning of the lift installation, fire alarm and warden call system to suit the proposed programme of work and commissioning.

- Communal and sub main distribution and dwelling consumer unit installations

- Lighting installation

- External lighting installation

- Street Lighting installation in accordance with the stamped approved Roads Service drawing

- General power installation and final connection of associated equipment

- Communal fire alarm installation and mains powered detector installation in dwellings

- Television distribution system

- Door entry system

- Warden call installation

- Telephone wiring

- Lift installation

- Electrical Works associated with the mechanical installation

- All works associated with the installation of renewable technologies

- Earthing

- Testing and Commissioning installation

- Labelling and documentation

Under this sub-contract the Developer shall supply, deliver to site, off load, install, test, commission, and set to work, all items of materials and equipment necessary for the continuous operation of the works described throughout the specification and as indicated on the contract drawings.

The Developer will be responsible for arranging and managing the connection of all necessary utility services, and for completing and issuing to the Utility providers application forms and connection cards as and when required to suit the Contract Programme.

All utility services companies must be contacted prior to commencement on site to ensure that all existing services have been identified and are dealt with accordingly to suit the proposed programme of works.

2.3	INSTALLATION REGULATIONS

The whole of the installation shall be carried out in accordance with the current editions of:-

(i)	The IEE Wiring Regulations (BS7671)

(ii)	Building Regulations

(iii)	Health & Safety at Work regulations

(iv)	Construction Products Regulation

(v)	Any regulations issued by the Local Government Authorities in respect of installations in certain specified buildings

(vi)	British Standards

(vii)	HSE Guidance

(viii)	CIBSE Guidance

(ix)	The DFC Housing Association Guide

Design information and data used for the selection of cables, accessories, etc. shall be in accordance with the current edition of the IEE Regulations BS7671

2.4	SAMPLES / APPROVALS

Prior to the placing any orders the Developer shall engage in a two stage approval process for all items to be provided under this sub-contract. This shall comprise the following: -

- Completion of all forms contained within the appendices of this specification confirming both the product details and their compliance with all items relating to their selection

- Upon initial approval of any or all items set out within the schedules, the Employer may request that the Developer provides physical samples of any item prior to full approval to supply and install each item. Catalogues will not be acceptable for Employer approval. The Developer shall provide samples free of charge whether or not they are approved and/or installed as part of the works

Failure to comply with this instruction will result in the Developer replacing any and all items installed without approval and found not to be acceptable at his own expense.

The Developer shall also be liable for the cost of any incidental work involved in replacing the items.

2.5	CO-ORDINATION AND INTEGRATION

The Developer shall note the requirement that he must provide installation drawings. These shall:-

(i)	Show all services properly related to others within his own, and others’, contract, all such drawings being fully co-ordinated with other services and building elements.

(ii)	Allow adequate provision for maintenance.

(iii)	Show builders work details.

(iv)	That detail any specialist installations that require site co-ordination and builder’s attendances such as the lift and photovoltaics.

During the progress of the work the Developer shall continue to discuss routes of services and locations of plant and devices with other trades.  Possible clashes or inappropriate positioning related to door swings, fixtures etc shall immediately be reported to the Engineer. No additional cost will be entertained for additional works due to lack of co-ordination.

The Developer shall mark all services locations on walls prior to the commencement of installations to show the locations of all items and to demonstrate that they have been properly co-ordinated. Failure to not show the location of any item which causes a clash at a later date shall result in the sub-contractor relocating one or both items at no cost to the contract. No installations shall be commenced until both the Contract Administrator and Employer have approved all co-ordinated locations on site.

# 2.6	INSPECTION, TESTING, COMMISSIONING AND SETTING TO WORK

The complete electrical works shall be inspected and tested in accordance with the IEE Regulations, and shall be commissioned and set to work in accordance with manufacturer’s recommendations and CIBSE Guidance.

The Developer shall take all necessary records during the tests and on completion thereof shall provide in triplicate a test report and record, along with an Installation Certificate.  All instruments required for testing purposes, together with skilled supervision and adequate labour for carrying out the tests shall be provided by the Developer.

The Developer shall test and set to work the complete installation prior to the issue of the Certificate of Practical Completion.

Details of the tests form part of this Specification but the Engineer reserves the right to ask for further tests to be carried out should they prove to be necessary.

The Developer shall instruct the Employer's staff on the operation of the complete works, including all the various controls and equipment.  Where specialised equipment has been supplied the Developer shall arrange for the manufacturer's representative to demonstrate the operation of the equipment to the Employer's staff.

On the completion of each dwelling the Developer must provide a NICEIC Test and Inspection certificate.

2.7	OPERATING INSTRUCTIONS AND DOCUMENTATION

At the completion of the installation the Developer shall instruct and advise the Employer as to the proper operation and maintenance of plant.  The instructions shall be carried out during the commissioning period and the ‘Practical Completion Certificate’ will not be issued until all operating instructions are submitted to the Employer.

Operating instructions shall be provided in the form of bound documents to include all details of starting up and operation of items of equipment included in the contract together with specialist information for the operators reference.

This documentation shall be provided by the Developer in duplicate and be available for use during the commissioning of the plant at the commencement of the Defects Liability Period.  The following details shall be provided where applicable: -

(a)	Operating instructions

(b)	‘As Fitted’ drawings (in the form of AutoCAD disks)

(c) 	Manufacturers’ Drawings of Equipment

(d)	Sectional drawings where applicable

(e)	Schedule of accessories & equipment installed, manufacturer and type numbers

(f)	Spare parts list

(g)	Maintenance schedules of recommended frequency of inspection and overhaul in terms of time and running hours.

(h)	Test Certificates

(i)	Schedules of Commissioning Tests

(j)	Contact names, addresses, normal and emergency telephone and fax numbers for all suppliers and installers for each product or system installed

2.8	AS INSTALLED DRAWINGS

During the whole of the contract the Developer shall keep on site an up-to-date set of prints marked up with details necessary for the production of As Installed Drawings as described below. These prints shall be made available for inspection by the Contract Administrator at any time.

Before completion two paper prints of each As Installed Drawing shall be submitted for comment.

Time shall be allowed for comment in accordance with the contract conditions.

In addition time required for correcting any errors shall be allowed.

The final issue shall consist of two paper prints, of each drawing and also one set of computer software discs containing the drawing information in AutoCAD format.

2.9	PERSONNEL INSTRUCTION

The Developer shall include in his Tender Price for the attendances of all necessary persons to fully instruct Employer’s personnel in the operations of the installations.

2.10	HOME USER GUIDE

Information for the Home User Guide shall be prepared and presented in an A4 wallet / holder with the correct postal address and dwelling number. This information must be available at handover.

Information must be provided for each system ‘As Installed’ and should provide easy descriptions and instructions for use together with any necessary maintenance that may be required.

The systems will include the following:-

- Consumer Unit/ Distribution Equipment

- Accessory Specification

- White Goods

- Lighting Controls and Associated Luminaire details

- Fire Detection System

- Television Distribution System

- Door Entry  System

- Lift

  - SERVICING AND TESTING DURING THE DEFECTS PERIOD

The Developer shall correct all defects and provide all replacement parts if required at no cost to the Employer during the defects period.

Additionally during the defects period and at no cost to the Employer, the Developer shall carry out or arrange for his specialist sub-contractors to carry out routine inspection, testing and servicing of all systems and equipment in accordance with manufacturers’ recommendations and the requirements of the applicable British Standards.

During this period the electrical Developer shall submit to the Employer full reports including details of tests carried out and any faults found with the corrective action taken.

Defects correction and routine testing and servicing during the defects period shall be provided for all systems and equipment installed under the contract.

  - SYSTEM OF SUPPLY AND DESIGN INFORMATION

| Main Source of electricity supply | LT underground service cable to be provided by NIE all associated negotiations and costs to be included for as part of the project |
| --- | --- |
| Nominal voltage | 230 volts single phase supply for houses 400 volts three phase and neutral supply to the apartment block |
| Frequency | 50 Hertz |
| Phasing | Single phase for houses Three phase and neutral for apartments |
| Method of earthing | TN-C-S (to be confirmed by NIE) |
| Value of external earth full loop impedance (NIE value) | 0.8 ohms |
| Method and type of installation for main and sub-circuit wiring | LS0H twin and earth cables and high impact PVC conduit |
| Conduit system | Metric, high impact PVC |
| Mains Cabling | LS0H split concentric |
| Sub-Circuit Wiring | LS0H twin and earth |
| Protective Devices | RCBOs in line with requirements of BS7671 |

  - EARTHING

The Developer shall supply and install an earthing conductor between the NIE earthing terminal and the installation earthing terminal.

The Developer shall supply and install all necessary circuit protective conductors and main equipotential bonding conductors.

Main equipotential bonding conductors shall be connected to the following as near as practicable to the point of entry into the building and/or into each dwelling: -

Water service pipes

Gas service pipes

Other service pipes and ducting

Heating and ventilation systems

Exposed metallic structural parts of the building

Supplementary bonding conductors shall be supplied, installed and connected to all simultaneously accessible exposed conductive parts and extraneous conductive parts, including: -

wash hand basins

hot and cold pipework services

mechanical plant

ventilation ductwork

exposed metallic structural parts of the building

lighting switches, lighting luminaires, socket outlets, fused connection units etc

Every joint in metal conduit, trunking, tray, pipework or ductwork shall be electrically continuous.

The Developer shall include for earthing of all electrical equipment in accordance with the latest edition of the IEE Wiring Regulations (BS7671).  The Developer shall be responsible for earthing each item of electrical equipment or control gear, whether supplied under this sub-contract or provided under another contract.

Labels indelibly engraved with the lettering 'Safety Electrical Earth- Do Not Remove' in legible type lettering of not less that 4mm high shall be permanently attached to all earthing terminals.

The earth continuity conductor throughout the installation shall be in the form of a single core cable (or earth core of a multi-core) specifically installed as an earth continuity conductor.

Every cable supplied and installed as an earth continuity conductor (other than the earth core of a multi-core cable) shall be a single cable having a conductor composed of strands of high conductivity tinned copper wires insulated with PVC compound coloured green/yellow.  Earth continuity conductors which take the form of one core of a multi-core cable shall be of a size and type suitable to the cable of which it forms a part.

Every earth continuity conductor shall be terminated in approved type cable clamps, soldered sockets or crimping lugs and shall conform in all respects to the requirements of the IEE Wiring Regulations.

All circuit protective-bonding conductors shall be enclosed in HD PVC conduit.

The insulation is specified to provide a measure of protections against corrosion of the conductor, but additional protection against corrosion and/or mechanical damage shall be provided where this is considered necessary for the compliance with the IEE Wiring Regulations.

  - SYSTEM OF CABLING AND WIRING

    - General

The Developer shall employ the following types and methods of wiring, together with the materials and form of installation as specified hereafter and shall install all equipment, materials and accessories in strict accordance with the manufacturer's instructions insofar as it is applicable to the specified Electrical Installation.

The cable sizes, method of installation, together with the type and rating of the protective devices for the proposed installation shall be selected in accordance with the requirements of the latest edition of the IEE Wiring Regulations.

    - Conduit System

Generally, the conduit installation required for the proposed installation throughout the building shall be carried out, using high impact PVC. All conduit accessories, boxes, couplings, etc., shall be provided with a similar finish.

All ground floor and intermediate apartments shall be wired as a fully rewireable loop-in conduit system using high impact PVC conduit throughout.

The conduit system shall be arranged in a neat and orderly manner to suit the building structure and shall harmonise with the other services and fixtures involved. The conduit runs, where possible, shall follow the lines of the building structure.

    - Low Smoke Zero Halogen Cables

Generally the wiring for the proposed electrical installation shall be carried out in LS0H twin and earth cables having stranded copper conductors, which shall be clipped to the building structure and enclosed in HD PVC conduit were necessary

All LS0H cables shall be 600/1000 grade and be made by an approved manufacturer.

All cables except where otherwise specified shall be manufactured and tested in accordance with the relevant British Standard and such later amendments and additions to the relevant British Standard that have been issued at the date on which the cables are ordered.

In addition to all cables being manufactured to the relevant British Standard, cables shall be certified by the British Approvals Service for Electrical Cables (BASEC) or by the European Committee for Electro-technical Standardisation (CENELEC).

    - Fire Alarm System

The wiring for the proposed new fire detection/alarm system shall be carried out utilising fire resistant 2core twisted screened and earth 1.5mm² flame resisting cable complying with BS6387 Category CWZ, EN 50200 PH30 & PH60, BS 8434-1 30 minutes, BS EN 60332-1-2, BS EN 50266-2-4, BS EN 61034-2 and produce less than 0.5% acidic gases when tested in accordance with BS EN 50267-2-1.  Cables shall be clipped to the building structure or enclosed within HD PVC conduit as required.

  - MAINS SUPPLY

    - General

Within each dwelling and/or apartment building consumer units, switchgear and Northern Ireland Electricity metering facilities will be located as indicated on the tender drawings.

The responsibility for co-ordination with NIE for any necessary modifications shall be included as part of the contract.

In apartment buildings all switchgear and metering must be incorporated as a cubicle pattern switchboard supplied and installed to meet the space requirements of Northern Ireland Electricity and their supply equipment.

Switchboard drawings must be provided to both NIE and the Engineer for approval prior to manufacture.

  - GENERAL LIGHTING INSTALLATION

    - General

Under this section the Developer shall provide a complete lighting installation.

    - Luminaires

All luminaires shall be carefully installed in a manner appropriate to their nature and method of fixing. All supports required for the luminaires shall be supplied and installed under this section of the contract.  All luminaires shall be complete in all respects and it should be noted that all fluorescent and compact fluorescent lamps shall have identical colour temperature and colour rendition throughout the building and be supplied as part of the Contract.

It is the Developer’s responsibility to ensure that all requirements are satisfied.

    - Positioning of Luminaires

The exact positions shall be agreed on site to comply with layouts and the appropriate partition walls and building lines.

    - Bonding of Metalwork

Metalwork of lighting luminaires shall be earth bonded utilising 1.5mm² PVC earth cable as a part of the lighting cabling installation.

    - Lighting Switches

Lighting switches shall be 20 amp, rocker operated grid switches mounted in a flush metal clad box, and shall be generally at a height of 1050mm above F.F.L.

    - Accessories

All wiring and ceiling accessories shall be from one single manufacturer’s range.

They shall be manufactured to ISO 9002 certification and shall comply with all applicable British Standards.

They shall be finished white

They shall be made from high grade thermoset material with inherent antimicrobial properties.

    - Conduit, Trunking and Cables

Lighting luminaires shall be connected to the circuits utilising 1.5mm² LS0H twin and earth cables clipped to the building structure or enclosed in PVC conduit recessed in the fabric of the building.

    - Extract Fans

Where extract fans are to be supplied from local lighting circuits, the extract fans shall be supplied and installed under another contract and be complete with integral timer but shall be wired, connected and tested under this section of the contract.

    - Positioning

The final position for all items of equipment is to be marked out on site with the engineer and an Employer representative prior to any installation taking place.  Should services be installed prior to marking out, the Employer and engineer reserve the right to relocate any item of equipment at no additional cost to the contract.

    - Roofspace Lights

The Developer must ensure that lights are located in all accessible roofspaces to adequately illuminate walkways and accessible plant. Switches must be provided adjacent to the access hatch.

  - EXTERNAL LIGHTING INSTALLATION

    - General

The Developer shall provide a complete external lighting installation as detailed on the drawings.  The system shall be installed in accordance with the CIBSE lighting guide.

    - Street Lighting

Where the street lighting is to be adopted by Roads Service, the Developer must ensure that the installation is installed in complete compliance with the approved street lighting drawing.

    - Site Lighting

Site lighting shall be controlled by means of a photocell, time clock and hand-off-auto switch, and shall be fed from the landlord’s meter either within the apartment block or in the case of communal alleyways from a local meter cubicle.

    - Over Door Lighting

Over door lights shall be controlled by means of a photocell and switch located internally adjacent to the external door. A single photocell shall control both front and back door lights through a contactor.

    - Positioning

The final position for all items of equipment must be marked out on site with the engineer and an Employer representative prior to any installation taking place.  Should services be installed prior to marking out, the Employer and engineer reserve the right to relocate any item of equipment at no additional cost to the contract.

  - STREET LIGHTING INSTALLATION

2.18.1	Compliance

The street lighting scheme must be carried out in conformity with The Private Streets (Construction) (Amendment) Regulations (N.I.) 2001

The street lighting scheme shall comply with BS 5489 (BS EN 13201)

Street lighting columns must comply with BS EN 40-3-2:2000 (BS5649) and type test certificates as detailed in Appendix C of BS EN 40-3-2:2000 (BS5649) for each type of column to be used must be provided

All street lighting electrical works shall comply with the current BS 7671

Electrical equipment and accessories must comply with the relevant British Standard or acceptable alternative standard and must carry a suitable IP rating for use in exterior environmental conditions

2.18.2	Overhead line safety

The Developer must note specified minimum clearances between overhead lines and columns

2.18.3	DRD Roads Service Approved Drawing

The street lighting installation must be in strict compliance with the DRD Roads Service stamped approved drawing, and the contractor must ensure he is in possession of this drawing before commencing installation.

Any installation not in strict compliance this drawing must be altered by the Developer at his own cost. No re-siting of any street lighting equipment is permitted without formal approval.

2.18.4	NIE

The Developer shall apply directly to NIE for a supply connection to the new street lighting scheme

2.18.5	Earthing Arrangement

Until adoption by DRD Roads Service, the street lighting electricity supply is to be considered as a temporary construction supply. As such the installation is to be afforded additional protection as stated in clause 415.1.1 of BS7671, that is an earth electrode and an RCD with a rated residual operating current not exceeding 30mA and an operating time not exceeding 40ms at five times the rated operating current is to be provided and installed at the control pillar.

2.18.6	Control Pillar

Control pillars shall be constructed from 3 mm thick galvanised mild steel. Construction shall incorporate hinged fully weatherproof door (s) with stainless steel replaceable hinges and louvred vents protected by insect-proof perforated internal mesh baffle. Door locks shall be wedge-lock type featuring interlock plates and a removable brass bung shall protect key aperture by special key, which should be compatible with Lucy-type locks and bungs. Medium pillars to have twin locks and large pillars to have double doors and a removable centre pillar against which the doors close and lock with top and bottom locks. A facility shall be provided on the control pillar to enable the door to be securely locked by an operative while working on a system serviced from this pillar. This provision shall not protrude more than 25 mm beyond the surface of the pillar door and shall have no sharp edges and shall have a 15 mm diameter hole to facilitate the fitting of a padlock

Provision shall be made, on the rear of the pillar door for storage of A4 size documents. Brass Ml0 earth studding complete with M10 full nuts and whole plain washers in brass shall be provided on the sidewall level with the lower edge on the backboard

The lower portion of the pillars shall be fitted with removable 3 mm thick apron plate of painted galvanized steel. Plate to be retained by M8 bolts and washers, screwed into nut set, within main body of enclosure

The pillar shall be protected against corrosion so as to give a guaranteed life on site, in areas of mild environmental pollution, of 15 years. The protection system must meet the requirements of the Department of Transport Manual of Contract Documents Specification for Highway Works 1991 as detailed at Series 1900. Overall colouring to be Hollybush Green, BT4800-14C39. Control pillars shall be coated internally and externally with bitumen from the base up to bottom line of door. An equipment mounting backboard of 12.5-mm thick tanalised plywood shall be provided and shall be removable, fixed with 4 No screws nuts and nylon-shrouded washers

- Board Dimensions

Medium Pillar Backboard - Height 1,000 mm - Width 600 mm

Large Pillar Backboard - Height 1,000 mm - Width 1,400 mm

- Depth

Medium Pillar - Minimum 300 mm from backboard to door

Large Pillar - Minimum 300 mm from backboard to doors

Each pillar shall be supplied with a white heavy duty plastic label, firmly attached to the door (centrally, 150 mm from top) and bearing the inscription "DRD (NI) Roads Service" in black embossed lettering, 6 mm high. A unique pillar identification number in 75mm high yellow lettering on a black background shall be stencilled on each access door and on the pillar backboard

Pillars shall be erected on a cased concrete structure, the base will have 3 No slow bend 100mm ducts for small / medium pillars and up to 6 No slow bend 100mm ducts for large pillars. Left hand slow bend shall be for Supply Authority supply cable use only

Adequate space must be provided within the control pillar to accommodate the installation of the meter

The Supply Authority cut–out and meter shall be located to the left on backboard

A facility shall be provided on the pillar to enable the door to be securely locked this will be in addition to the wedge locks with bungs fitted

Locks and hinges shall be lubricated

Pillars shall be numbered as indicated on the plan of installation

The structural condition of the pillar cited both internally and externally shall be free from damage or corrosion to the protective coating

2.18.7	Photocells

Photo-cells must be of all electronic type with a switching ratio 1: 0.5 and a switch-on level of 35 lux

2.18.8	Cables

Underground cable shall be three Core XLPE/PVC/SWA/PVC Cable to BS5467. Core colours: Green/Yellow, (Earth) Blue, (Neutral) Brown (Live)

Cable should only be installed when both the cable and the ambient temperature is above zero degrees centigrade and has been for the previous 24hrs

Circuit cables shall be 600/1000v grade, which shall be marked on the sheath of the cable

Cable Joints are not permitted

Where cables have not been terminated, a pot-end shall be fitted to the cable end to prevent the ingress of moisture

2.18.9	Ducts

Ducting shall be provided for cable throughout the cable length. Longitudinal ducting shall be 32mm diameter 38mm external diameter flexible alkathene, orange in colour and made from Polythene or PVC and shall be smooth walled inner and outer faces of the non-ribbed variety. It shall be printed ‘Department for Regional Development - Street Lighting' in 6mm high blue lettering along its entire length

Where cable crosses the carriageway, 150mm twin wall uPVC duct shall be provided at a depth of 900mm from finished road level to extend 0.5m either side of the crossing

Marker tape shall be laid 225mm above the cable or duct and shall be 150mm wide, coloured yellow and printed along its entire length with the legend 'Caution - Street Lighting Cable Below'

Ducting shall not be kinked or damaged in any way

Footway duct shall only employ slow bends

Footway ducting should normally be located within 0.5m of the rear of the footway or as detailed on the plan of installation

2.18.10 Columns

Terminations and connections at each column base shall be made within a street lighting double pole cut out in accordance with the current edition BS 7671. Fuse carriers shall only be removable by use of a tool

Street lighting columns shall be ballasted with concrete and shall be aligned to the footpath or footway

Columns must be marked with a unique identification number as specified

Columns numbers shall be painted mid yellow on a matt black background. Self-adhesive PVC labels showing a single yellow digit on a black background to be manufactured from PVC material having a tensile strength of at least 20 N/mm2 and of overall thickness not less than 90 um. Adhesive material should provide an initial adhesion; measured on stainless steel, of at least 400 N/m. Label must be suitable for exposure to the elements and will be mounted in the vertical plane. Guaranteed life, both adhesive and legibility must be at least 7 years

Where columns are erected at the minimum agreed clearance from overhead power lines, the bracket arms and doors should be painted with red/white strips

Columns should be erected in a truly vertical manner in locations as indicated on the plan of the installation

The structural condition of the column both internally and externally shall be free from corrosion or damage to the protective coating

Column door locks & hinges shall be lubricated

Columns will be erected with column door positioned on the opposite side to oncoming traffic

Column doors should be correctly fitting

Column & bracket arm serial number tag shall be mounted within the base compartment

Columns should be numbered in accordance with plan of installation

Column numbering shall be No.1 to the end of street/road or an extension of an existing numbering system as per street lighting representative’s instructions (in the case of a small number of columns)

The Developer shall number all columns on the site

All lanterns and bracket arms shall be properly fitted and aligned at 90°to kerb

2.18.11 Inspection

During the construction period the Roads Service representative must be afforded access to the site to ensure that the works are being carried out in conformity with The Private Streets (Construction)(Amendment) Regulations (N.I.) 2001

It is the Developers responsibility to ensure that all materials meet the specification and are installed in accordance with the approved drawing

2.18.12 Completion

On completion the Developer must submit the following documentation: -

- Full details of all equipment used

- An NICEIC Electrical Installation Certificate

- A completed ‘Application for Transfer of Street Light Energy and Maintenance’.

- As built record drawings

  - GENERAL PURPOSE POWER DISTRIBUTION

    - General

Under this section the Developer shall provide a complete socket outlet and general-purpose power installation as detailed on the tender drawings.

    - Accessories

All outlets and associated conduit runs for all services shall be flush mounted

All DP switches and connection units must be suitably engraved in red lettering with details of the equipment they supply e.g. water heater, extract fan etc.

All socket outlet circuits shall be wired as 32 amp ring main circuits, RCBO-protected utilising 2.5mm² PVC cables in recessed high impact PVC conduit.

All wiring and ceiling accessories shall be from one single manufacturer’s range.

They shall be manufactured to ISO 9002 certification and shall comply with all applicable British Standards.

They shall be finished white

They shall be made from high grade thermoset material with inherent antimicrobial properties.

Socket outlets shall incorporate a 3-pin operated child resistant shutter system, which shall inhibit access to the electricity supply, unless all 3 pins of a standard British 13A plug are in position.

    - Mounting Heights

Mounting heights from finished floor level shall be taken as follows:-

Lighting Switches	1050mm to bottom of box

13 amp Sockets – General	  600mm to bottom of box

Fire Alarm Call Points	1050mm to bottom of box

Sockets etc. above Worktops	1050mm to bottom of box

Thermostats	1200mm to top of box

    - Positioning

The final position for all items of equipment must be marked out on site with the engineer and an Employer representative prior to any installation taking place.  Should services be installed prior to marking out, the Employer and engineer reserve the right to relocate any item of equipment at no additional cost to the contract.

No electrical switch or outlet shall be positioned within 350mm of an internal corner.

  - FIRE AND CO ALARM INSTALLATION

    - Scope of Works

The Developer shall supply and install a complete Fire and Carbon Monoxide alarm system as depicted on the tender drawings.

Generally, the installation shall be carried out in accordance with;

- Current IEE Wiring Regulations (BS7671)

- Current Northern Ireland Building Regulations

Additionally;

- Smoke/Heat alarms shall be interconnected and installed in accordance with BS5839-6:2013 and manufacturer’s instructions to Grade D, Category LD2.

- Carbon Monoxide alarms shall be installed in accordance with BS EN 50292:2002 and manufacturer’s instructions. CO alarms shall be interconnected to the Smoke/Heat alarms to increase audibility and operate such that if a CO alarm sounds, the Smoke/Heat alarms also sound.

- The Fire and CO alarm system shall incorporate a control switch to enable weekly testing and (in the event of an activation) identification of the device that caused the system to operate.

Requirements for inspection, testing, commissioning and setting to work, as installed drawings, personnel instruction, operating and maintenance manuals, and servicing during the defects period are detailed elsewhere in this specification.

    - Fire and Carbon Monoxide alarm installation in Individual Dwellings

All alarm devices shall be mains powered with sealed in rechargeable lithium cell backup supply capable of lasting 10 years+ and interconnected as detailed above.

All alarm devices shall have a built-in surface mounting plate with integral screwed connection terminal block and cable cover, connecting without the need for a flying lead and connector and shall incorporate an anti-tamper locking device to prevent unauthorised removal of the alarm without the use of a tool.

Mains powered Optical Smoke alarms shall be BSI Kitemarked to BS EN 14604:2005 and shall have an insect resistant fine mesh screen and a memory feature to indicate if the alarm has been activated in the previous 24 hours.

Mains powered Heat alarms shall be BSI Kitemarked to BS 5446-2:2003, Fixed Temperature 58oC +/-4oC, Class A1 devices and shall have a memory feature to indicate if the alarm has been activated in the previous 24 hours.

Mains powered Carbon Monoxide alarms shall be BSI Kitemarked to BS EN 50291:2001 and designed to have a working life of 10 years. They shall have a memory feature to indicate if CO has been detected during a period of absence and a replaceable sensor module to enable the sensor to be replaced after 5 years without the need for an electrician.

Mains powered alarm control switch shall incorporate Locate, Test and Silence functions and mains failure warning. All functions shall be operable from floor level.

Mains powered Relay module (1no.) shall be rated up to 240V AC / 5 Amps and operate on receipt of a signal from the interconnect line of a Smoke, Heat or CO alarm to shut down the mechanical plant.

    - Extent

Generally the installation will include the following: - Optical smoke alarms in the living room, hall and landings, Heat alarm in the kitchen and CO alarm in the room containing the heating appliance. Exact quantities must be taken from the drawings but the foregoing included as a minimum.

    - Fire shut-down

One of the detectors within the dwelling, typically that on the landing in a two storey dwelling, shall be supplied complete with a relay base from which the mechanical ventilation heat recovery system shall be supplied.  The base shall provide power to the MVHR system and act as a fire alarm interface to cut power and shutdown the MVHR system upon any activation of an alarm.

  - COMMUNAL FIRE ALARM INSTALLATION

    - General

### The Developer shall employ a fire alarm contractor to undertake the design, supply, installation, testing and commissioning of the fire detection and alarm system.

### The fire alarm contractor must be approved to BAFE SP203 or LPS1014 and their name must appear in the current list of firms engaged in the design, installation and commissioning of fire detection and alarm systems.

### The Fire Alarm Contractor shall also carry ISO 9001 quality accreditation.

### The Fire Alarm Contractor shall be qualified to design, install and certify fire alarm systems to BS 5839 part 1, and shall have third party accreditation of their competence with respect to BS 5839 part 1, latest edition.

### The Fire Alarm Contractor shall be trained and authorized by the manufacturer to calculate, design, install, test, commission and maintain the fire detection and alarm system, and shall be able to produce a certificate stating such upon request.

### The Fire Alarm Contractor shall supervise installation, software documentation, adjustment, preliminary testing, commissioning, setting in to use and certification of the system.

    - Scope

### This specification describes an addressable fire detection, alarm and signalling system.  The control panel shall be intelligent device addressable, analogue detecting, low voltage and modular, with digital communication techniques, in full compliance with all applicable codes and standards.  The features and capacities described in this specification are required as a minimum for this project and shall be furnished by the successful Fire Alarm Contractor.

### The system shall include all required hardware, interconnecting wiring and containment, and software to accomplish the requirements of this specification and the contract drawings, whether or not specifically itemized herein.

### Written agreement of design principles and proposed installation drawings shall be obtained by the Fire Alarm Contractor from the local building control department and Employer’s Insurance Company before commencement of the works.

    - Compliances

### The system shall be designed, supplied, installed and commissioned in accordance with the latest revisions of, and able to meet, the following standards: -

- BS 5839 part 1 Category L1: systems installed throughout all areas of the building.

- BS EN 54 and its associated relevant parts, to which all components and devices must have either LPCB or VdS certification.

- Compatibility shall be proven to EN 54 Part 13 - Compatibility assessment for system components, certified by either LPCB or VdS.

- BS 7273 part 4 - Actuation of release mechanisms for doors (Category A).

- The electrical installation shall be installed and tested in accordance with the latest edition of the IET Wiring Regulations.

- Part 3 of The Fire and Rescue Services (Northern Ireland) Order 2006 and The Fire Safety Regulations (Northern Ireland) 2010.

- It will be a requirement that the Fire Alarm Contractor will give attention to the requirements in BS 5839 part 1: section 3, regarding reduction of false alarms.  The manufacturer is to offer a false alarm statement with regards to compliance with a level 1 response (as defined in the CFOA policy).

    - System Description

Fire detection and alarm shall be provided by an analogue addressable system with a control panel, and a combination of smoke and heat detectors with integral sounder/strobes, manual call points and addressable interface relay units to mechanical plant, lifts, electrically-controlled doors and roller shutters etc. all as indicated on the drawings, and as required.

The Fire Alarm panel will be located in the entrance to the building.

All detection devices must incorporate a zone or loop isolator.  Zone isolators shall provide isolation of the positive and negative sides of the detection loop; in the event of any single short circuit no devices shall be isolated.

The fire alarm panel shall be linked via a ‘Firestu’ communicator to an Alarm Receiving Centre using Redcare remote monitoring.

The system shall comply with category L1

    - Open Protocol

All fire detection and alarm systems and devices must use standard equipment and be open protocols available freely from more than one source to ensure continuity of systems, efficient maintenance, control of software and engineering access.

    - Cause and effect matrix

The fire alarm specialist shall provide a cause and effect chart in discussion and agreement with the Contract Administrator

    - Detector suitability

Account must be taken of the location and relevant environmental factors when determining the type of detection device to be deployed in each area.

    - Sound levels

Account must be taken of all compartment doors, noisy environments and external areas when determining the number of sounders to be provided

    - Power Supply Units

A power supply unit and battery back-up shall be provided for each alarm panel and interface unit

A charger together with maintenance free sealed lead acid cells shall be supplied suitable for integral mounting within the processor unit, which should be BS EN54-4 compliant.

The batteries and charger shall be capable of providing standby power for a period of 24 hours plus a further 30 minutes in alarm load with all sounders operating continuously.

    - Modem Unit

The fire alarm specialist shall supply, erect and connect the required modem unit for signalling all fire alarm information, via a private telephone line, to a central alarm receiving station.

    - Ceilings, voids and ducts

Detection shall be provided in all voids of 800mm or more.

Void detection must be fully accessible and not obstructed for maintenance purposes. Access panels must be provide as necessary. Identification must be provided as specified below.

    - Installation of Detectors

All detectors (and bases) shall be installed in accordance with guidelines set out in BS 5839-12002, BS 7671 and the installation instructions provided by the manufacturer.

All detector bases shall be securely fixed to BESA boxes and allow for easy fitting and removal of detectors.

For detectors fitted to a false ceiling a suitable adaptor shall be used to allow the assembly and installation of the detector and base to be completed and tested prior to the installation of the ceiling tile.

Cable and wire entries to detector bases shall be fitted with grommets to prevent possible damage to the insulation.

Cable and wire strain relief clamps shall be provided at all entries to detector bases.

Cable entries of detector bases used in environments with abnormal atmospheric or operating conditions shall be appropriately sealed to prevent ingress of dust, water, moisture or other such contaminants. Use of the suitably I.P. rated back boxes, in such environments should be adopted.

    - Wiring

The detection and sounder circuits shall be wired using 1.5mm 2 core and earth screened low smoke zero halogen fire resistant cable and meeting the standards laid down in BS 7629. The automatic and manual devices together with addressable sounders and interface units shall be wired in a loop, starting and finishing at the control panel in accordance with the drawings.

    - Loop capacity

Loops must be designed so that the numbers of devices on the loop does not exceed 80% of its capacity thus allowing 20% spare capacity.

    - Labelling

All fire alarm devices shall be permanently labeled to denote the device zone and address number

    - Identification

Where remote or hidden detectors/devices are placed in voids, ducts or above ceilings, a suitable LED indicator is to be provided in a logical and adjacent position, clearly marked to specify the type of device, address number and location

    - Programming

The fire alarm specialist shall programme device addresses using unambiguous location descriptions

    - Commissioning

Upon completion of installation, the fire alarm specialist shall test, commission, set the system to work (including proving all functionality, programming, sound pressure levels, electrical tests and the connection to the Alarm Receiving Centre) and hand over the system to the customer.

The specialist shall record test results and shall provide a commissioning certificate.

    - Handover

At the time of hand over, the fire alarm specialist shall provide the customer with the following documentation:

1.	System description

2.	Operating and Maintenance instructions

3.	As-installed drawings

4.	Zone chart mounted adjacent to the control panel

5.	Design, installation, commissioning and verification certificates

6.	Declarations of conformity

7.	NICEIC installation certificate

8.	Log book

    - Training

The fire alarm specialist shall provide the customer with the training required by personnel to operate and test the fire detection and alarm system.

    - Maintenance

The Developer shall employ the fire alarm specialist to correct all defects, and provide routine servicing and maintenance in accordance with BS 5839 during the defects period.

  - TV INSTALLATION

    - Scope of Works

The Developer shall supply and install TV aerial outlets and coaxial cables as detailed on the drawings.

    - TV Installation in Individual Dwellings

Coaxial cables shall be installed from a central location i.e. the roof space in houses and first floor apartments or from a store in ground floor apartments to outlets located in the living room and bedrooms. Cables must be installed within pvc conduit, and have sufficient length left for future aerial connection by others.

The installation must be capable of supporting future Sky Plus HD Set top box installations, by installing co-axial cables from the central location to the living room outlet.  4no coaxial cables shall be provided from the central location to the living room for future sky, terrestrial aerial feed and aerial return, in addition to a cable from the central location to each bedroom.

All cables shall be manufactured to the relevant parts of Specification BS EN 50117. All cables must have passed the benchmarking approval test conducted by the Confederation of Aerial Industries Ltd. and have a certificate issued by the Confederation of Aerial Industries Ltd. that the cable meets with the benchmarking approvals.

All coaxial cable shall have a nominal characteristic of 75 ohms and will be suitable for the application concerned. The Developer should take into account the requirement for LS0H (Low Smoke Zero Halogen) insulation.

The cable must be earthed as necessary and at no point on the system must the loop impedance be greater than five ohms.

    - Mounting boxes

Flush metal boxes shall comply with BS4662 and have a minimum internal depth of 40 mm. All cable exits from the boxes shall be grommeted so as to prevent damage to the cable. Flush mounted boxes of insulating material may be used in hollow partition walls of plasterboard and similar material and shall have a minimum internal depth of 40 mm, comply with BS5773 and have mounting centres compliant with BS4662.

In all cases, care shall be taken to ensure that all cable bending radii are no smaller than those advised by the cable manufacturer.

    - Connectors

All accessories must conform to the requirements of BS EN 50083.

All passive accessories will be 75 ohms.

IEC connectors must always be crimped or screwed, using the correct tools.

Connectors must provide effective screening, and be suitable for use with the cable type.

    - Outlets

All socket outlets must be fully screened, flush mount type, from the same manufacturer and range to match all other accessories within the dwelling.

  - COMMUNAL TV AERIAL INSTALLATION

    - General

The Developer shall employ a specialist company to supply, install, test and commission the TV aerial and signal distribution system in apartment buildings.

The specialist shall be a member of a member of the Confederation of Aerial Industries and be a Sky Communal System approved installer, and have the relevant qualifications for Television Distribution Systems.

The specialist company shall be accredited by the equipment manufacturer and shall employ full time, a minimum of one technician certified by the manufacturer confirming that full training has taken place

    - Scope of Work

The specialist shall supply, install, test and commission a five cable Integrated Reception System, comprising four cables providing individual IF Polarities, and one cable providing terrestrial frequencies through a switching devicewith twin co-axial cables to the living room and main bedroom outlets as indicated on the drawings.

All installations shall be capable of supporting Sky Plus HD set-top box installations.

A loop shall be provided between the living room and main bedroom.

The systems shall comply with the current technical conditions of the Licensing Authorities.

    - Safety

Comply with: -

- All relevant Health and Safety legislation

- The Confederation of Aerial Industries (CAI) documents:

- General Statement on Health and Safety

- Code of Practice for the Installation of Terrestrial and Satellite TV Reception Systems

- Health and Safety in the Aerial & Satellite Industries

- Guidelines on Safe Operating Procedures for the Aerial and Satellite Industry

- BS EN 50083: Cable networks for television signals, sound signals and interactive services, particularly Part 1: Safety requirements

- BS 7671 (the IEE Wiring Regulations)

Ensure that earthing and bonding is rigorously carried out.

The system must be earthed, via a minimum 4mm2 earth cable, taking into account the CAI statement on Earth Bonding and the requirement to maintain no more than a 5 ohm loop resistance, to the building main earth terminal.

The aerial support structure must be bonded to the lightning protection system (LPS) or, if there is no LPS, to the building main earth terminal.

Incoming cables from antennas must be bonded across the outer sheath of all relevant co-axial cables prior to the input of the IF/RF amplifiers.

All co-axial outer connections must be permanently bonded to the building main earth terminal.

Drop Cables from Multiswitches to outlet plates must be bonded across the outer sheath of all drop cables.

All electrical and electronic devices must be bonded to each other by means of an earth tag.

Incoming and outgoing earth cables must be fixed in such a manner that should the device be disconnected from the system then the integrity of the earth is maintained. In general terms this means the earth cables being crimped together. Individual earth cables must not be wrapped around earth posts.

    - Standards

The systems must conform to the following standards and codes of practice:

- CENELEC BS EN 50083 all relevant parts.

- CENELEC BS EN 50117 for coaxial cables.

- CENELEC BS EN 60966 for connecting cables.

- BS 4662:1970 – Specification for boxes for the enclosure of Electrical Accessories

- BS 5773:1995 – Specification for general requirements for Electrical Accessories.

- The Confederation of Aerials Industries Codes of Practice for Television Aerials, and TV Systems.

- The requirements of the DTG R-Book 5 in respect of the system for the Digital Terrestrial services (except to the extent that technical differences apply, when this Specification will override DTG R-Book 5).

    - Approval of Developer’s proposals

System planning must be undertaken to avoid common analogue interference patterns.

A schematic drawing representing the proposed system in block diagram form, showing locations of equipment, types of cables and earthing arrangements must be submitted to the Engineer for approval.

    - Ease of access for installation and maintenance

All amplifiers and the aerial and dish arrays, and head end equipment must be easily accessible without cherry pickers, scafFolding etc.

    - Services

The services to be provided using the proposed system are as follows:

| Service | Programmes | Frequency |
| --- | --- | --- |
| Terrestrial Digital | Multiplex 1 | UHF |
|  | Multiplex 2 | UHF |
|  | Multiplex 3 | UHF |
|  | Multiplex 4 | UHF |
|  | Multiplex 5 | UHF |
|  | Multiplex 6 | UHF |
| Satellite Digital | All Horizontal and Vertical transmissions, both Low Band and High Band from the 28 degree east orbital position, in the transmission range from 10,700 MHz – 12,750 MHz. | IF |
| FM Radio | The national and local services, legally transmitted to the general area of the site concerned. | Band II |
| DAB | The Radio programmes provided by the DAB services. | Band III |

The Developer must perform a site test to determine that all the services listed above are available at the levels required for distribution (see below). If any service is, as a result of the site test, found not to be available this must be reported to the Engineer immediately so that an agreement may be made as to which services will be provided

    - Sky Plus HD

All installations shall be capable of supporting Sky Plus HD Set top box installations.

    - System Performance

It will be the responsibility of the Developer to familiarise himself with the site and local conditions prior to tendering. The Developer must satisfy himself that the services stated are available on each of the sites indicated, and that the quality of the signals will enable him to meet the relevant Specification requirements indicated. If any of the services are not available the Developer must notify the Engineer in writing.

Should the Developer believe that the proposed system, if supplied, will not meet the specified performance criteria this must be highlighted at the time of tender, together with alternative proposals.

    - Materials

All materials must be from an approved supplier and be new and previously unused. All goods and materials used in providing the system shall conform to EU and national standards, where such standards have been established, and to the Codes of practice issued by the relevant industry bodies.

All Equipment must be able to cope with the minimum and maximum signal levels, as listed hereafter for the given frequencies in use.

No departure from the specified and/or approved materials will be accepted.

    - Aerial systems

Assess aerial requirements by carrying out a signal strength survey.

Take into account the transmission arrangements in the area, and any new services being planned.

Select the appropriate aerial type, considering such factors as signal strengths, frequencies, polarisations, impedance matching, rejection of unwanted signals, appearance, and safety.

Only CAI/DTG benchmarked aerials may be used.

    - Siting

Assess aerial location by carrying out a site survey to identify possible sources of interference.

Aerials should be sited in the highest practicable position with a clear view in the direction of the relevant transmitter. This should only be compromised to reduce excessive ghosting on analogue signals.

Receiving aerials should be kept as far away as possible from any transmitting aerials in the vicinity, e.g. those for PMR and cellular telephone base stations, wireless broadband services, or amateur radio and CB.

Avoid sources of impulsive electrical interference such as heating and ventilation plant, and lift controls, etc. Aerials must not be sited where they look directly at such interference sources, and their downleads should be routed to avoid proximity with the associated power and control wiring.

    - Stability and wind loading

Comply with BS EN 50083-1.

For masts greater than 6m, a qualified structural engineer must be employed to guarantee the safety of both structure and building.

    - Combining aerials

A filter diplexer must be used where the outputs of VHF and UHF aerials are combined onto a single downlead.

    - UHF TV Aerial Systems

Ensure the aerial system is chosen for satisfactory reception of both analogue and digital TV services.

All UHF antennas must incorporate a Balun to ensure the matching of the dipole to the feeder cables.

    - Choice of Transmitter(s)

Take signals from more than one transmitter if necessary, depending upon the results of a signal strength survey.

Priority should be given to receiving the correct regional services, wherever practical.

    - Single aerial installations

In selecting a suitable aerial, only the types that have been approved under the CAI /DTG benchmarking scheme are to be used.

In addition, the following factors should be considered:

    - Aerial Group

Select the aerial group depending on transmitter frequencies in use, and future changes to digital frequencies as analogue transmitters are switched off.

    - Aerial Gain

Select the aerial gain depending upon the coverage area.

    - Aerial Directivity

Select aerial directivity depending upon the level and direction of interfering signals.

Rejection of an interfering digital signal should be sufficient to achieve at least 30dB level difference between the wanted and the interfering signals, in order to achieve a minimum decoding margin of 6dB.

Take account of interference that limits coverage during extreme weather conditions.

    - Cross-polar discrimination

Select the aerial to ensure adequate cross-polar discrimination and achieve levels of rejection similar to the levels required for interference.

    - Feeder pick-up rejection

Select the aerial to ensure adequate feeder pick-up rejection.

    - Impedance Match

Select the aerial to ensure adequate impedance match.

    - Multiple TV aerial installations

Run separate analogue and digital aerial downleads to the headend and use channelised headend equipment, or an application-specific combiner ahead of a wideband amplifier.

    - Satellite dishes

Satellite dishes must be of an adequate size for the system concerned and be able to produce a 15dB carrier to noise level at the installations site, for the given transponders being received.

    - Dish alignment

Dishes should be aligned for maximum signal strength and carrier to noise ratios. The LNB should be aligned so that the horizontal and vertical transponders appear equal and give maximum rejection of the opposite polarity.

    - Headend equipment /repeater amplifiers

All equipment should be powered at 230 volts.

Energy efficient amplifiers should be chosen to minimise total power consumption.

Reprogrammable profiling cluster filters and equalisers must be used, and these should not require special equipment or access codes to reprogram.

Launch amplifiers, repeater amplifiers, and multi-switches must have colour-coded inputs, input and interstage level controls and stepped gain outputs.

Only locally stocked and easily sourced equipment may be installed.

The equipment must be securely mounted and easily accessible for maintenance purposes in a dry secure location.

    - Cables and fixings

All cables shall be manufactured to the relevant parts of Specification BS EN 50117. All cables must have passed the benchmarking approval test conducted by the Confederation of Aerial Industries Ltd. and have a certificate issued by the Confederation of Aerial Industries Ltd. that the cable meets with the benchmarking approvals.

All coaxial cable shall have a nominal characteristic of 75 ohms and will be suitable for the application concerned. The Developer should take into account any requirements for special cable constructions such as LSZH (Low Smoke Zero Halogen)

The cable must be earthed as necessary and at no point on the system must the loop impedance be greater than five ohms.

Where applicable (in general terms this is where the cable needs protection from possible vandalism) external cables shall be protected by conduit, capping or trunking of a suitable size.

Internal cables, located in building risers, must be fixed to a cable tray or located within an enclosed conduit or trunking. All external surface routes must be approved with the Engineer before installation.

Where cables are run across a flat roof area, they should be installed on a suitable cable tray of galvanised material. The tray should be fixed, at not less than one metre spacing, to a heavy duty brick or concrete block, by means of a standard screw and plug fixing, two fixings to each brick or block. The brick or block should be laid on a non-penetrating membrane of rubber or on two layers of mineral roofing felt. The substance used should be cut to the size of the brick or block and loose laid on the existing roof surface. Care must be taken should any shingle be located on the roof that the placing of any Bricks or Blocks does not cause penetration of the existing roof surface. Alternatively, a proprietary support unit may be used in place of the brick or block, such unit to be approved by the Engineer, in writing prior to installation and installed to the manufacturer’s instructions.

Cable trays that are fixed vertically should be fixed using a method that locates the tray against a vertical surface, with a minimum spacing off of that surface of 12mm, at no more than one metre spacing so that the tray does not move in any plane.

All cable trays must be earthed in line with the earthing requirements of the current edition of the wiring regulations.

All cable installation routes must follow a ‘Tree & Bush’ installation format where the drop cable is routed from the wall socket, uninterrupted, to a switch position, which is located away from the Head-End, and the switches provide the facility to loop the five feeder cables through from one switch to the next.

Cable lengths from the multiswitch to the outlet should be kept to a minimum, and where possible no more than 30 metres.

Within the head-end and network, the connection of the coaxial cable will be via ‘F’ type and IEC connectors only. All ‘F’ connectors must be crimped and IEC connectors should be of a professional design and correctly made off. All connectors should be the correct size for the cable used.

All fly leads will be ‘Double Screened’ and comply with the relevant parts of BS EN 60966.  Fly leads should be of a length to achieve a neat and tidy installation.

    - Mounting boxes

Flush metal boxes shall comply with BS4662 and have a minimum internal depth of 40 mm. All cable exits from the boxes shall be grommeted so as to prevent damage to the cable. Flush mounted boxes of insulating material may be used in hollow partition walls of plasterboard and similar material and shall have a minimum internal depth of 40 mm, comply with BS5773 and have mounting centres compliant with BS4662.

Where surface mounted boxes are used, they shall be of moulded insulating material, have a minimum internal depth of 40 mm, comply with BS5773, have mounting centres compliant with BS4662 and be of a style and colour consistent with that of any electrical wiring accessories installed in the same dwelling.

In all cases, care shall be taken to ensure that all cable bending radii are no smaller than those advised by the cable manufacturer.

    - Connectors

All accessories must conform to the requirements of BS EN 50083.

All passive accessories will be 75 ohms. All satellite IF frequencies will be connected using ‘F’ type connectors.

IEC connectors must always be crimped or screwed, using the correct tools.

Connectors must provide effective screening, and be suitable for use with the cable type.

    - Outlets

All socket outlets must be fully screened, surface or flush mount type, and have a minimum of five connecting points. Individual sockets shall be provided for TV, Satellite1, Satellite 2 (Sky+), Audio (covering both FM and DAB frequencies), and loop to bedroom. Where required, sockets must be capable of passing the Digibox infra-red remote control signals.

Outlets must be from the same manufacturer and range to match all other accessories within the dwelling.

    - Measurements

Use accurate equipment designed for the particular service, as follows: -

- A portable meter suitable for roof work may be used and should be capable of measuring carrier to noise ratio and signal power level for all the types of services.

- A spectrum analyser capable of the following as a minimum:

  - Measurement in the range 5MHz to 2300MHz

  - Absolute level accuracy of not worse than ±3dB

  - Printer or memory function to enable records of measurements to be kept.

Use of a signal strength indicator is not acceptable.

Equipment must be accurate to within +/- 3dB

The following measurements are required:

- Signal level

- C/N ratio

- BER, CSI and MER

- Operating margin

    - Required signal levels delivered from the outlet plate

Service 		Minimum level 	Recommended level Maximum level

FM stereo radio 		54dBµV 		60dBµV*** 		74dBµV*

DAB 				30dBµV 		40dBµV*** 		70dBµV

Digital terrestrial television 	45dBµV** 		50dBµV 		65dBµV

Digital satellite television 	52dBµV 		60dBµV 		77dBµV

* Where successive FM channels are at an interval of 300KHz, do not exceed 66dBµV.

** This includes a margin to cover effects such as variations in propagation, due to the growth of foliage on trees, deterioration of the aerial system, etc. Care must also be taken that the analogue signals, usually at a significantly higher level, do not overload the digital receiver.

*** FM and DAB signals should be lower than analogue TV signals by at least 6dB. In addition, DAB signals should be lower than digital terrestrial signals by at least 6dB.

    - Required carrier to noise ratios delivered from the outlet plate

Service 			System 	Minimum C/N 		Noise bandwidth

FM radio 			Stereo 			45dB 			0.18MHz

DAB 				OFDM 			18dB			1.536MHz

Digital terrestrial television 	OFDM						7.6MHz

-16QAM		23dB

- 64QAM 		26dB

Digital satellite television 	QPSK 			12dB 			27MHz

Measurement of Carrier to Noise should be made against a 'noise floor' and not between transponders. The recommended frequencies to set the noise floor are 1970MHz. in the low band and 1070MHz. in the high band. Should a transponder signal be present at these frequencies than the 'noise floor' frequency should be adjusted to avoid conflict. The new frequency should be noted and advised on the completion certification.

    - Testing

Before the hand-over the system must be tested by the Developer to ensure that the system complies fully with the Specification, including electrical tests. The tests will include the maximum and minimum signals for each of the services, measured at the outlets as specified.  The Developer shall provide a printed record of all measurements, either in tabulated or spectrum form.

    - Commissioning

The Developer will supply a commissioning certificate, indicating signals at the inputs and output of the main equipment and levels received at the outlets. The Developer will demonstrate that the picture quality on all the services stated is to CCIR grade 4 on the analogue television channels and error free on the Digital channels.

The Developer will provide all certification forms in an agreed format.

    - Defects liability and maintenance

The Developer shall maintain the complete system to this Specification, without charge during the defects liability period.

The Developer will attend to reported faults within 24 hours or as otherwise agreed in writing by all parties concerned.

    - Training

One two hour training session on the system shall be allowed for within the tender.

    - Handover

At the time of hand over, the specialist shall provide the following documentation:

1.	System description

2.	Operating and Maintenance instructions

3.	As-installed drawings

4.		Commissioning certificate

  - AUDIO-VIDEO DOOR ENTRY SYSTEM

    - General

The Developer shall employ a specialist supplier/installer to supply, install, test and commission a complete digital audio-video door entry system as detailed on the tender drawings and in line with the requirements outlined hereafter.

The specialist company shall be registered to the ISO 9002 Quality Assurance standard.

The specialist company shall be accredited by the equipment manufacturer and shall employ full time, a minimum of one technician certified by the manufacturer confirming that full training has taken place.

    - System description

- The Digital Door Entry System shall be complete with:

- outdoor audio-only Vandal Resistant Entrance panel, c/w video interface card interfaced with a cctv camera adjacent to the entrance

- interface to permit emergency release of electrically-controlled doors from the warden call remote central station

- wall mounted apartment monitor stations with integral handset and microphone/speaker in each apartment.

- The system shall be complete with all necessary components and accessories as necessary for the satisfactory operation of the proposed system.

- System shall facilitate communication between Entrance Panels and monitors inside each apartment

- Connection of all internal monitors will be realized with 2 common wires, not polarized, all included (Call, Audio, Monochrome Video, Lock release and Monitor power supply)

- Connection of several different types of Audio/Video and Audio only units shall be made in the same way, so as to grant an easy and immediate replacement and/or upgrade

- Single way video distributors, individually provided together with each bracket shall be necessary and facilitate monitors connection.

- In case of need, system shall also permit the connection of monitors in the same riser with “Daisy Chain” mode, in/out from monitor to monitor, without the need of video distributors.

- System shall manage up to 240 users and up to 600mts distances with appropriate cables and power supplies.

- A visitor shall be able to call and communicate with any of the tenants in the building by entering the apartment’s number and pressing the relevant call push button.  System shall also allow the use of traditional button type panels, easily programmable without any additional wire.

- A buzzer shall then alert the called tenant and its monitor will switch on automatically.

- When the tenant picks up the receiver, an audio communication link shall be established between the calling entrance panel and the apartment.

- Tenant may allow entry to the visitor by pressing a dedicated key button on their respective monitor to open the electronic door.

- The system shall allow the manual self ignition of each monitor, without any negative side-effect (call from entrance panel must have priority)

- The system shall ensure “Secrecy of conversation” between visitors and tenants. It is not possible for any third party to listen to an existing communication.

- The system shall be able to facilitate an easy and quick self-programming of internal units by means of Dip-switch settings on monitors Bracket.

- Monitors bracket shall be complete with built-in digital decoder so as to avoid any use of additional Multi-way decoders in each floor

- The system shall integrate the “Bell System” without any additional buzzer or power supplies. Bell Button will be directly connected with 2 wires into the monitor’s bracket.

    - Entrance Panels

- The entrance panels shall be modular type, Vandal Resistant suitable for outdoor installations c/w video interface card interfaced with the cctv system to capture the picture from the cctv camera adjacent to the entrance

- The system shall permit the indifferent use of both digital and analogue push button type panels

- Entrance panels shall be installed at the entrance door of the buildings or in the lift lobbies or at common gates of all buildings, as indicated on systems configuration.

- Entrance panels shall facilitate any visitor to call and communicate with tenants.

- They shall be of aesthetic design with Double leaf 2.5mm thick stainless steel face plate and thick powder coated die-cast aluminium frames with special security resistant screws

- Entrance panels shall be complete with pre-amplified speaker unit with trimmers for microphone and loudspeaker adjustments

- Entrance panels shall provide beep sound for key pressed confirmation

- User friendly guided menu to help installer for any programming

- Entrance panels shall also provide audio confirmation for call affected

- Connection between main audio unit and push buttons will be “Plug and Play” type so facilitate the installation and reduce installation time

- Operating conditions will be -10ºc to 50ºc and 90% RH Humidity

    - Internal monitors

- Each unit shall be of attractive design suitable for wall mounting and constructed of high impact plastic

- Monitor shall be installed inside each apartment for tenants use

- Monitor shall be surface mounted type, plugged into dedicated connection bracket

- Fixing bracket shall have terminal board for wires connection and built in digital decoder

- Each monitor shall be connected with 2 wires only, “NOT Polarised”, by means of dedicated single way distributor

- Each Monitor shall be equipped with:

- Monochrome LCD Flat screen

- Audio handset with integral microphone, loudspeaker and flexible cord with plug

- 3 Buttons for lock release, self ignition / Free button

- Ring volume selector with Privacy/Do not disturb position with Red indicator

- External adjustment for Brightness

- Monitor shall provide different electronic chime for calls from main Entrance panels or Bell button

- Monitor shall be easily adapted for desk version with dedicated Desk base

- Each unit shall facilitate an easy and quick self-programming by means of Dip switches on monitors bracket

    - Video distributors

- Single way Video Distributors, individually provided together with each bracket, shall be necessary and facilitate monitors connection

- Video Distributor shall be of small dimensions in order to be placed in floors junction boxes or similar

- They shall be easy to be connected together in case of more apartments being distributed from the same floor

- The unit shall guarantee a perfect picture, avoiding any loss of video signal

    - Egress

All electrically-controlled doors shall be provided with a ‘green’ mushroom push-button switch engraved ‘push to exit’, and a green break glass unit to break the low-voltage supply to the magnetic door lock

    - Commissioning

Upon completion of installation, the specialist shall test, commission, set to work and hand over the system.

The specialist shall record test results and shall provide a commissioning certificate.

    - Training

One two hour training session on the system shall be allowed for within the tender.

    - Handover

At the time of hand over, the specialist shall provide the following documentation:

1.	System description

2.	Operating and Maintenance instructions

3.	As-installed drawings

4.	Commissioning certificate

    - Maintenance

The supplier/installer shall maintain the installation and pay all costs during the defects liability period.

Additionally, regular servicing and maintaining of the installation shall be carried out at 6 month intervals during the maintenance period. During this period the Equipment supplier shall submit to the Engineer a full report in duplicate including details of tests carried out and any faults found with the corrective action taken.

  - ACCESS CONTROL

    - General

Under this section of the specification the Developer shall employ a specialist sub-contractor to supply and installation of a complete access control system including all equipment and cabling to enable the system to function.

The specialist sub-contractor shall install the system to the standards required by the National Security Inspectorate (NSI) and be registered to ISO 9002 Quality Assurance standards.

Specialist Sub Contractor shall be asked to provide prior to installation at the handover stage their NACOSS Gold certification. Anything less than Gold Certification will not be accepted

Certificates shall be requested prior to the commencement of work.

The Specialist Sub-Contract Company shall be accredited by the equipment manufacturer and shall employ full time, a minimum of one technician certified by the Manufacturer confirming that full training has taken place.

Confirmation of the above shall be sought by the electrical Developer at tender stage.

    - Installation of Conduits

Conduits shall be continuous HD PVC installed in the methods as described under section 2.14 of this specification.  Terminations shall generally be of the BESA box pattern.

All cabling shall be installed within HD PVC conduit and galvanised trunking.

    - System of Cabling

All cabling shall be supplied and installed by the specialist Developer.  The electrical contractor shall provide all necessary containment required to provide a complete rewireable installation.

    - System Details

Operation

The system to be installed shall have the capability to control access doors with facility for future intruder detection devices and building management on a common LAN Network. Hardware for connection of the above shall share the same network.

The system shall carry out the following;

Add/Remove fobs or users from the system from a PC.  The PC shall be supplied and installed under this contract as a rack mounted unit provided in the comms cabinet and shall be of a suitable specification for running the access control software.

A shadow card option shall not be accepted.

The client should be able to interrogate the traffic going through the doors from a remote display.

Access equipment shall consist of a number of Proximity fob type readers.

The system shall consist of IP Network controllers.

The specialist contractor shall determine the need for any remote power supplies and shall allow for the cost of the same in his price to provide a reliable level of DC voltage to detectors. All costs for additional remote power supplies shall be included.

The power supply units shall provide stand-by battery capacity sufficient to continue to operate the system for a period of 24 hours. All costs for additional remote power supplies shall be included.

Programming Features:

- Various Memory Configuration options available (selectable by installer)

- 2000 user capacity expandable to 24, 500

- Expandable to 240 doors

- User name expandable to 240 doors

- Area settings expandable to 250

- Upload/Download capability for programming, control and monitoring.

- Programmable text descriptions for Inputs, Areas, Users, User Types, Time zones, Holidays, Groups, Doors, Area Lists, Door Lists, Telephone Numbers and Home auxillaries.

- Every text entry shall be individually programmable, placing no limit on the choice of words available.

Reporting Features:

- Multiple Reporting Formats, Contact ID, Securitel, IRfast and EarthNet.

- Multiple Client code reporting.

- Multiple Comms Tasks to allow variety of reporting options to operate simultaneously.

- Backup reporting available using any Dialler format

- Connection options for Printer, Computer, Monitor or External Modem.

- Automatic telephone line testing

- Password protected Remote Login feature to provide “Callback” option for added security.

Door Controllers

Intelligent Door Controllers, capable of continuing to operate in the event of loss of the LAN Network, shall be installed to cater for the doors.

These units shall have an integral power supply unit operating at 12v DC and shall be complete with the following features:

- Mother Board with built in circuitry to support 2 readers, 1 door

- Size in plastic cabinet: 232 x 320 x 80mm

- Up to two access readers per controller – Read in / Read out

- Access parameters configurable from software

- 50000 cardholders per controller.

- Max 200 controllers per data line

- Configurable Logical Input/Output Control

- Transaction Buffer:

- Maximum 2728 Events

- RS485 / RS232 Port or TCP/IP comms converter

- Connectors for supply to locks etc.

- Tamper Switch

- Comprehensive Status Indicators

- Integral Power Supply 12VDC

- Cabling between reader and controller – Beldon 9540

- RS485 data line CAT5 or Beldon 8723 max length 1000mtrs

Proximity Readers:

Readers shall be operated by fobs to the following specification

Carrier frequency - 125khz

Clock & data bit period

Operating voltage – 8-14vdc

Cable type Beldon 9540

Maximiun cable extension 100mtrs

Proximity fobs

2No Proximity fobs per flat will be provided with an additional 10No spare for client use.

Locking devices

A suitable motorised lock and automatic closing devices will be installed to the controlled doorways by others as part of the builders ironmongery package. The specialist must confirm lock compatibility prior to installation.

    - Log Book

A system log book shall be provided detailing all equipment and dates of maintenance. A sample shall be handed over for approval.

    - Testing, Commissioning and Maintenance

This Contract shall include for Testing and Commissioning of the complete access control system on completion of the works by the Developer. Commissioning and NSI Gold completion certificates shall be issued to the Employer.

Maintenance contract to be fully inclusive of parts, labour and callout within 4 hours for 1 year from the date of practical completion. Annual maintenance shall include quarterly visits to site to check and monitor the system is performing to an optimum level. Maintenance reports shall be issued on each visit and entries to the log book completed

  - CLOSED CIRCUIT TELEVISION SYSTEM

Not used

  - WARDEN CALL (Where Applicable)

    - General

The Developer shall employ a specialist supplier/installer to design, supply, install, test and commission a complete warden call system as detailed on the tender drawings and in line with the requirements outlined hereafter.

The purpose of the system shall be to facilitate remote release of the main entrance door and remote release of the key safe by Fold Telecare.

The specialist company shall be registered to the ISO 9002 Quality Assurance standard.

The specialist company shall be accredited by the equipment manufacturer and shall employ full time, a minimum of one technician certified by the manufacturer confirming that full training has taken place.

    - System description

This specification details the design, installation and operational performance of a communication system specifically designed for installation in accommodation occupied by elderly or infirm residents.  The system must be capable of providing emergency alarm signalling facilities and Telecare sensor monitoring.

There will be no local or remote scheme manager. The alarm signalling and communication features shall operate in remote off-site mode only, and all alarms will be reported using a PSTN link to a centralised and permanently manned facility (Alarm Receiving Centre ARC).

The system shall be linked by telephone to a remote Central Station Receiver and shall be fully approved for PSTN connection, complying fully with the requirements of BS 7369 for communication data protocol. The system shall be compatible with existing central station equipment manufactured by other leading companies.

The equipment shall be approved to meet European Standard EN55022 for Electromagnetic Compatibility and the Low Voltage Directive (LVD) and shall be certified and marked with the CE mark.  A copy of the Technical Construction File (TCF) relating to the standards shall be available for inspection at any time.

The system shall comply with the requirements of BS EN 50134.

The system shall have a Smart Technology option to perform electronic assistive technology functions. The system shall be capable of logging life-style activity monitoring in real time, storing the data and making it available to service providers.

In addition to the PSTN communication links described above the system shall have an Ethernet port to allow high-speed communication over ADSL broadband networks. The system will use standard browser interface software. The Ethernet communication port shall be used to access system operating data and assistive technology data.

The manufacturer shall undertake supply training and spare parts to any nominated company of an appropriate technical and commercial standing.

    - Installation

The system shall be installed in accordance with the current edition of the IEE Wiring Regulations, and all British Standards and Codes of Practice as applicable.

Full 'as fitted' drawings detailing all cable routes, cable sizes, joint box locations and cable colour codes will be supplied prior to final commissioning.

    - System cabling

All cables and cable containment shall be strictly in accordance with the current edition of the IEE Wiring Regulations.

Surface cables are not permitted.

    - Power supply

The power supply shall be an integral part of the central control unit.

The system shall operate from a 240 Volt 50 Hz mains supply but shall be capable of normal operation within +/- 10% of nominal.

The supply voltage to the system wiring shall not exceed 24 Volts DC.

The system shall be suitable for use on distribution networks protected by Residual Current Devices.

The system shall have an integral mains fail battery back-up facility which will run the system under normal load for up to eight hours. Should an installation require a battery back-up period in excess of eight hours, the system shall be capable of meeting this requirement by the addition of an external battery pack.

    - Central control unit

The central control unit shall be a single control unit housed in a metal enclosure and shall be wall mounted by pre-drilled fixing centres. The enclosure shall have adequate pre-drilled cable entries protected by grommets.

The central control unit shall provide the following facilities:

a) Extra low voltage power supply for the whole system, including standby battery. The power supply circuit shall include a low battery dropout feature to prevent permanent damage to the battery in the event of a prolonged mains failure.

A ‘mains failure’ warning shall be signalled within 5 minutes of a mains supply failure occurring.

A ‘mains restored’ warning shall be signalled when the mains supply is restored.

A ‘low battery’ warning shall be signalled prior to the battery dropout feature activating.

LED indicators shall clearly show that all power supply voltages are healthy.

b) Provision for connection of up to 256 dwellings each of which can have both warden call and access control facilities.

c) Monitoring of individual intercom units for fault conditions. Faults shall be signalled with the relevant intercom identity. Normal system operation shall continue in the event of an intercom fault or the removal of one or more intercoms from the system. It shall be possible to inspect the system memory and display all faults that exist. It shall be possible to mask faulty or removed intercom units to prevent continual fault signalling.

d) Audio amplifiers shall feature Digital Speech Technology (DSP) and have Automatic Gain Control (AGC) to ensure high quality speech and adequate sensitivity for the detection of speech through one closed door. It shall be possible to set the default volume level of individual intercom units to suit the user’s needs.

e) An RS232 output shall be available for connection to a local printer or computer.

f) Memory for the programming of digital intercom identities of up to three digits. Each digital identity shall be supplemented with a message indicating the location. Standard channel messages shall include FLAT, OFFICE, WARDEN, FRONT DOOR, CORRIDOR, COMMON ROOM, GUEST ROOM, BUNGALOW, TOILET, LIFT and SHOWER ROOM. There shall be provision for up to 80 other standard messages that can be allocated to specific channel identity numbers. There shall also be provision for the inclusion of site-specific customised messages.

Programming of all intercom data and system configuration options, including central station telephone numbers and site identification, shall be stored in NVRAM and shall be programmable on-site, without the need for special electronic equipment.

g) Call detection shall differentiate between an alarm call from the intercom unit and that from any other auxiliary trigger devices that may be connected to a particular intercom. The different types of calls shall be clearly signalled to the mobile master unit.

h) Alarm detection of one or more of the following auxiliary alarm devices: CEILING MOUNTED PULLCORD, SMOKE/HEAT DETECTOR, LOW TEMPERATURE DETECTOR, INDIVIDUAL RADIO TRIGGER, INTRUDER DETECTOR shall be possible. The channel from which the alarm was detected shall be signalled to the mobile master unit with a message clearly indicating the type of sensor.

i) Digital communicator to allow the system to communicate via the PSTN. The system shall be capable of signalling alarm calls in one of two modes;

1. If calls are signalled to a standard or mobile telephone a special key press sequence shall be required to confirm the authority of the recipient to answer the call. The identity of the calling channel shall be preceded by the site identity. Control of speech direction shall be automatic and controlled by the call recipient’s voice.

2. If calls are signalled to a remote central monitoring station a digital preamble shall identify the site and dwelling. Control of speech direction shall be by control tone from the central station.

The system shall be certified for connection to the PSTN network. The system shall be capable of DTMF dialling.

It shall be possible for the remote scheme manager or central monitoring station to call a resident even if the system is in the ONSITE mode (provided there is no system activity). An automatic warning tone shall be generated before a speech link is established.

The digital communicator shall monitor the telephone line for faults. Any fault detected shall be signalled to the mobile master unit if the system is in the onsite mode. A line fault shall prevent the system being switched to Local or Remote Offsite mode of operation. A BT line fault indicator shall be provided. This will have a strobe light to provide an onsite indication of a BT line fault.

There shall be provision for the storage in memory of at least four telephone numbers.

j) The mode of operation shall be selectable either locally or remotely. Local selection, by the onsite scheme manager, shall be by either a key-switch or using the cordless master unit. Remote selection shall be by a PSTN connection using special DTMF command codes. The local wall mounted keyswitch shall have LED indication to show the current operating mode of the system. Confirmation of the operating mode selected shall also be available using an enquiry code.

k) Provision shall be available for the connection of auxiliary alarm signalling devices. The outputs shall be programmable to indicate a variety of equipment conditions including BT line fault and alarm call not answered.

l) Programmable output signals shall be available for activation by both the local and remote scheme manager and by the remote central station. The outputs can be used to control external devices such as door locks, key safes, etc.

m) Where more than one scheme manager is on duty it shall be possible for scheme managers to contact each other using their mobile master units. Scheme managers shall also have direct access to external telephone lines to both make and receive normal telephone calls. It shall be possible for two scheme managers to talk to each other whilst a third is making an external call. If a scheme manager is making an external telephone call when an alarm occurs an audible signal shall inform the scheme manager.

n) When the system is operating in the ONSITE mode and an alarm call is not answered within a pre-set time the alarm call shall automatically be routed to either the LOCAL OFFSITE scheme manager or the central monitoring facility depending on the mode selected. The time delay shall be set to 5 minutes but shall be programmable to suit local conditions.

o) The system shall have an integral time clock. The time shall be set using the mobile or fixed master. A facility shall exist to check the current time and date. The time shall auto-adjust for BST/GMT twice per year. The time clock shall have it’s own back-up battery.

p) It shall be possible to allocate up to 2000 individual radio alarm devices to the system by individual allocation to specific intercoms. This process shall be carried out using the standard master unit and not a special programming tool.

q) Where individual pendant alarm transmitters are required on a site it shall be possible to connect up to 16 network receivers directly into the central control unit to ensure adequate coverage over the whole site. Individual pendant receivers shall be uniquely coded and shall be continuously polled by the central control unit to ensure system integrity.

r) The system shall facilitate the use of the warden call system and the access control system at the same time i.e. dual speech paths shall be employed.

s) When the system has been switched to a remote scheme manager, local offsite or central control, the access control system shall continue to operate normally for residents.

t) Where an Emergency Services panel is fitted all calls shall be routed in line with the selected system operating mode.

u) The central control shall have an Ethernet port to allow direct connection to a standard broadband communication network. The port shall support standard browser software to allow a variety of system functions to be accessed and to allow system activity data to be accessed.

v) The central controller shall log all system and alarm activity and store the data in a non-volatile memory. It shall be possible to download the stored data using either a local PC or, by using the Ethernet port and an Internet connection, to a remote PC. Access to the data shall be password protect. The system memory shall be capable of storing a minimum of 12 months data assuming a fully loaded system with an average of 8 sensors per intercom. An alarm message shall be generated when the memory is 90 % full.

w) It shall be possible to program Telecare sensors as either alarm sensors or activity sensors. The system shall be capable of sending either emails or text messages to care providers in the event that programmed activity patterns have been recognised. It shall be possible to tag any alarm or activity event to any email address or telephone number stored in the system memory.

x) It shall be possible to program up to three basic activity monitoring time periods into the system such that if no activity is detected from a particular intercom within the time period an alarm will be generated. It shall be possible to individually program each intercom for activity monitoring within the time periods.

y) The system shall have a Test Mode to allow any individual intercom to be tested without placing a full alarm call on the system. It shall be possible to select Test Mode which ever mode of operation the main system is operating in i.e. ONSITE, LOCAL OFFSITE or OFSITE. This mode of testing will ensure that genuine alarm calls from other intercoms are answered efficiently. When in Test Mode a VISUAL and AUDIBLE signal will confirm the successful operation of any of the wired or radio trigger devices allocated to the intercom. Test calls from each trigger device will be printed and stored in the system memory. If an intercom is accidentally left in Test Mode it will automatically revert to Normal Operation within 5 minutes of the last test being activated.

    - Apartment intercom unit

Not required

    - Radio device receivers

Not required

    - Door entry system

This system shall be interfaced to the door entry system to allow the remote opening of one or more entrance doors independent of each other. The door lock will release on receiving a signal from the remote call centre. The door open period shall be programmable.

    - Key Safe

The system shall include a key safe, and shall allow remote operation of the key safe to allow access to the master key to the flats.

A call button and speech unit is to be situated adjacent to the key safe.

    - Fire alarm interface

A speech module is to be fitted adjacent to and interfaced with the communal fire alarm panel. When the fire panel goes into alarm the speech unit must be activated, and communicate with Fold Telecare to give a warning that the main fire system is in alarm and establish two way speech with the speech unit.

    - Mains & telephone connection

All mains supply connections shall comply strictly with the current edition of the IEE Wiring Regulations.

The specialist shall liaise with Telecom Supplier to ensure that the ADSL telephone supply is terminated at a suitable position.

    - Commissioning

Upon completion of installation, the specialist shall test, commission, set to work and hand over the system.

The specialist shall record test results and shall provide a commissioning certificate.

    - Training

The specialist shall allow for two days training to be provided to the Employer

    - Handover

At the time of hand over, the specialist shall provide the following documentation:

1.	System description

2.	Operating and Maintenance instructions

3.	As-installed drawings

4.	Commissioning certificate

    - Maintenance

The supplier/installer shall maintain the installation and pay all costs during the defects liability period.

Additionally, regular servicing and maintaining of the installation shall be carried out at 3 month intervals during the maintenance period. During this period the Equipment supplier shall submit to the Engineer a full report in duplicate including details of tests carried out and any faults found with the corrective action taken.

  - TELEPHONE WIRING

    - Scope of Works

The Developer shall supply and install a complete telephone outlet system consisting of master and secondary outlets and 2-pair telephone wiring all as indicated on the drawings.

Within apartment buildings, the electrical Developer shall also supply and install multipair cable from each BT and Virgin Media network termination point to each master socket.

    - Cable containment

All wiring shall be contained within high impact pvc conduit recessed within the fabric of the dwelling.

Multipair cable shall be installed in galvanised steel trunking within risers and in ceiling voids.

    - Liaison with BT and Virgin Media

The Developer shall liaise with BT and Virgin Media regarding new incoming services to each dwelling.

Live telephone service must be provided for commissioning of the lift installation, fire alarm and warden call system to suit the proposed programme of work and commissioning.

  - LIFT INSTALLATION

    - Scope of work

The Developer shall employ a specialist lift installer to supply, deliver, erect, test and commission new passenger lifts as indicated on the drawings.

Each installation shall be as described in the equipment schedule hereafter.

The Developer shall also provide operation and maintenance manuals, record drawings and user training upon completion

    - Compliance

The workmanship, installation and testing of the lift installation shall in all respects conform to all relevant legislation and guidance, including the following:

- All relevant British Standards, including: -

- BS 2655, BS 5655, BS 8300, BS EN 12385, BS.EN 81, BS EN 12016

- BS 7671 Wiring Regulations

- All relevant legislation, including: -

- Building Regulations.

- Management of Health and Safety at Work Regulations

- Construction (Health, Safety and Welfare) Regulations

- Provision and Use of Work Equipment Regulations

- The Electricity Supply Regulations

- The Construction (Design and Management) Regulations.

- Electrical Equipment (Safety) Regulations

- Work Equipment Regulations

- Manual Handling Operations Regulations

- Workplace (Health Safety and Welfare) Regulations

- Personal Protective Equipment at Work Regulations

- Construction (Head protection) Regulations

- The Disabled Discrimination Act 1995 (1999)

- The requirements of the employer’s insurers.

- All relevant guidlines, including SAFed Guidelines

    - Electricity supply

Nominal voltage		400 volts three phase and neutral

Frequency			50 Hertz

Method of earthing 		TN-C-S

Protective Devices 		Fuses to BS88

    - Builders work and drawings

      - The builders work associated with the lift installation will be carried out by the Main Contractor.

      - The Lift installer shall provide detailed drawings, showing apertures, holes, chases, trenches, ducts and plinths as required for the installation and shall be responsible for the accuracy thereof.

      - The drawings shall be submitted to the Main Contractor for transmission to the Contract Administrator for approval

      - On approval of the drawings 3 copies shall be provided to the Main Contractor for distribution.

    - Materials and workmanship

      - All goods included in the works shall be new and comply with the current British and European Standards

      - The Lift installer must place an order for all materials required for the contract at such time to ensure delivery to site before such items are actually required to avoid any delay in the progress of the work.

    - Supervision of works

      - The Lift installer shall employ a competent representative or 'Foreman-in-Charge' to supervise and control the works on site with authority to discuss modification to the works as may be required from time to time, and on receipt of properly authorised site instructions, accept and execute such instruction on behalf of the Lift installer.

      - This representative and such additional site staff, as the Contract Administrator may deem necessary, shall be available on site during all working hours, unless previously agreed otherwise by the Contract Administrator.

    - Electrical installation

      - The electrical installation works to be carried out by the Lift installer shall commence at the TPN isolator

      - The electrical installation work shall conform in all respects with all relevant parts of BS7671

      - A fire signal shall be provided via a fire alarm interface. The lift installer shall wire and connect the fire signal to the lift controller.

    - Safety signs and warning notices

      - All signs and notices shall comply in all respects to BS EN 81.

    - Equipment to be provided

      - The following list of equipment is to be included in the sub-contract: -

      - Door release hooks/keys for opening landing doors.

      - Two sets of keys for control panels, etc.

      - Special tools for maintenance purposes.

    - Record drawings

      - The Lift installer shall supply completed "as fitted" drawings for the works.

      - The draft set of drawing shall be supplied to the Contract Administrator for approval 28 days before the practical completion, and on receipt of such approval the final 'as fitted' drawings shall be supplied prior to the date of Practical Completion.

    - Service and maintenance manuals

The Lift installer shall supply three properly hard bound 4 ring manuals with durable plastic covers and it shall contain:-

(a) Description of the installation, itemising all components of the plant installed. Information shall be adequate to provide all information required for future in-service tests.

(b) Description of how the plant operates, with full design details, together with a description of emergency action which should be taken in the event of a breakdown.

(c) Complete Schematic Line Diagrams indicating the main features of the plant, the interconnection between various items, drawing attention to the method of setting the controls, switchgear etc. The Contract Administrator shall be consulted before the diagrams are finalised

(d) Method of adjustment, typical fault finding routine and a complete set of wiring diagrams showing the various relay and semi-conductor modules and interconnection between these items. Wiring diagrams of all sub circuits and printed circuits shall also be included.

e) A description of the maintenance routine, oil and grease points and recommended lubricants.

(f) Service manuals for all specialised plant, giving all details listed above, including a list of spares.

(g) All the aforementioned burnt on to CD-ROM.

    - Inspection and testing

      - All tests are to be carried out in the presence of the Contract Administrator and a member of the Employer's Insurers in accordance with the Lifts Regulations 1997 and shall be to the satisfaction of all parties.

      - Seven days notice shall be given for the witness test to arrange the attendance of the Employers Insurers.

    - Maintenance

      - The Lift installer shall allow for routine inspection testing and maintenance of the lift installation during the Defects Liability Period

      - Maintenance visits shall be carried out at three-monthly intervals

      - Replacement parts shall be covered under warranty during the defects liability period

    - Tuition of staff

      - The Lift installer shall allow for instructing the Employers' staff in the operation of all safety measures required to be carried out in the event of any abnormal conditions, i.e. loss of power, over running etc.

      - It may not be possible to arrange such instruction until the building is occupied therefore due allowance shall be made for a subsequent visit after Practical Completion.

      - Arrangements will be made by the Contract Administrator for the attendance of the appropriate Employers' staff.

    - Equipment schedule

Description

Lift Type				Machine room-less passenger lift

Lift Drive				Gearless traction

Contract Load (Kgs)			8 Person – 630kgs

Speed (m/s.)				0.63 m/s

Entrances Served			See drawing

Floor Markings				G, 1, 2, 3 etc.

Entrance Type				Side Opening

Clear Entrance Width (mm)		900 mm

Clear Entrance Height (mm)		2000 mm

Shaft Width (mm)			Developers Design

Shaft Depth (mm)			Developers Design

Pit Depth (mm)				Developers Design

Headroom Height (mm)			Developers Design

Travel Height (mm)			Developers Design

Shaft

AC Gearless Machine	Provide, install, connect and test a gearless machine, incorporating Ascending Overspeed Protection in the form of 2 fully independent brakes each of which is separately able to stop and hold the car under emergency braking conditions

The machine will be located within the lift shaft

Guides & Fixings	Provide and install guides and fixings

Balance-weight	Provide and install buffer weight

Buffers	Provide and install buffers

Suspension Ropes	Provide and install suspension ropes

Overspeed Governor	Provide and install Overspeed governor & rope

Guarding & Protection	Provide and install pit ladder

Provide and install landing aprons & toe guards

Provide and install pit emergency stop switch

Landings

Architrave	Brushed stainless steel finish

Doors	Provide and install doors complete, including as required top railing, hanger, hanger rollers, landing lock, release mechanism and stainless steel door panels

Doors are to be two hour fire certified

Landing Door Finish	Brushed stainless steel

Landing Push Stations	Install new landing push stations fitted at every level to meet the requirements of EN81-70

Hall Lantern & Indicator	Provide and install hall lanterns and position indicators to meet the requirements of EN81-70

Service Control Panel	Install adjacent to the top floor entrance. Finished in aluminium

Lift Car

Car Interior Dimensions	1100mm wide x 1400mm deep x 2100mm high

Door Operator	Install door operating system

Car Interior	Standard range

Car Ceiling	Standard range

Car Flooring	Standard range

Car Door Finish	Brushed stainless steel

Car Door Protection	Full height infra-red door detectors

Car Operating Panel	Brushed stainless steel finish and an alphanumeric dot matrix LED indicator showing car position

Car push buttons to be tactile micro-movement with call registered indication

Lift Announcer	Audible messages within the car in compliance with EN81-70 regulations

Remote Monitoring	Provide hands free auto-dialler incorporated into lift car operating panel hands free communication in the event of an emergency

Car Top Control	Provide and install new car top control station to meet the requirements of EN81

Other	Provide: -

Brushed stainless steel handrails

Clear mirror to rear wall

Stainless steel skirting

Door open button

Alarm button

Emergency light unit

Overload indicator

Audible alarm with re-chargeable battery

  - ELECTRICAL INSTALLATIONS IN CONNECTION WITH MECHANICAL

SERVICES

    - General

The Developer shall provide a complete electrical installation in connection with the Mechanical Services Installation as specified hereafter.

    - Equipment

With the exception of the list below all equipment relating to the systems of the mechanical services installation shall be supplied by the Developer.  The various items shall either be both installed and electrically connected or be electrically connected only, as appropriate, as part of this sub-contract.

The Developer shall be responsible for the supply and installation of the following

- Immersion heater run back timer.

- Mechanical ventilation heat recovery boost run back timer.

- Mechanical ventilation heat recovery presence detectors.

- Mechanical ventilation heat recovery humidistats.

Prior to the connection of any equipment supplied under this contract the Developer shall obtain all relevant wiring details from the associated mechanical systems manufacturer.

    - Co-ordination

The Developer shall liaise with the Developer to co-ordinate services and to ensure accurate positioning of isolators, fused connection units.

    - Wiring

All power and control wiring associated with the Developers installation shall be undertaken as part of this sub-contract.

The Developer shall supply and install all necessary PVC conduit and wiring to the final components.

The Developer shall supply and install all isolators, fused connection units and flexible connections to individual items of mechanical equipment.

The Developer shall supply and install all conduits and back boxes for items such as internal and external sensors, thermostats, etc., in order that appearances can be similar to those of the electrical accessories.  The Developer shall ensure that all boxes are compatible with the mechanical items to be mounted thereon.

The Complete wiring installation shall be carried out in accordance with the relevant sections of this specification.

Alarm signals shall be provided from the fire alarm systems

    - General

The Developer shall be responsible for obtaining all specialist control manufacturers drawings prior to installation.

The installation shall be carried out in accordance with the controls specialist schematic drawings.

  - PHOTOVOLTAIC INSTALLATION

- INTRODUCTION

The Developer shall employ a specialist contractor who is: -

- a Microgeneration Certification Scheme certified installer, and

- a member of the Renewable Energy Consumer Code

- able to offer appropriate PI Insurance

- able to offer design warranty

All products used in the installation must be MCS registered.

This domestic sub-contract consists of the design (including structural design, gaining the approval of NIE, Planning Authority and Building Control, and the submission of installation drawings to the design team for comment), supply, erection, connection, testing, commissioning and setting to work of the complete photovoltaic (PV) array installation and all associated electrical works, to provide a complete and compliant installation in all respects,

The photovoltaic system is to be mounted on the roof and linked to the landlord’s mains electrical system via inverter units. The system is to be suitable for installation on the proposed roof, and is to be an ‘above-roof’ system (‘roof-integrated’ or ‘in-roof systems must not be proposed).

The system is to be rated at 8kWp.

- RELATED DOCUMENTS

This Specification must be read in conjunction with the under noted documents:

- Engineering Recommendation G83 (current edition) – Recommendations for the connection of small scale embedded generators (up to 16A per phase) in parallel with public low voltage distribution networks

- Engineering Recommendation G59 (current edition) – Recommendations for the connection of generating plant to the distribution systems of licensed distribution network operators.

- BS 7671 (current edition) - Requirements for electrical installations (all parts – but in particular Part 7-712 Requirements for special installations or locations – Solar photovoltaic (PV) power supply systems)

- BS EN 62446 (current edition) - Grid connected photovoltaic systems - Minimum requirements for system documentation, commissioning tests and inspection

- All other relevant British, IEC, TUV and UL Standards

- Building Regulations

- All other applicable legislation

- British Photovoltaic Association Codes of Practice

This specification is to be regarded as a general statement of requirements, and is in addition to any British Standard recommendation or requirement of Building Control.

The specialist Developer shall at all times adhere to the requirements of the above-noted documents.

3.	SCOPE OF WORK

The Works shall include the design, supply, install, test, commission and setting to work of the complete photovoltaic installation, including generation meter, and all labelling and documentation.

The following shall also be supplied and installed with the system: -

- local system information display unit

- weather station with data analyser (including irradiation intensity, module temperature, ambient temperature and wind speed)

- monitoring and data access via local PC and remotely via internet

The Developer shall provide line drawings, wiring diagrams and a list of materials proposed for use in the design and implementation of the system for comment prior to manufacture and installation.

The Developer shall include in his tender for all support frames and fixings to the roof structure, with panels arranged in banks.  The panels shall be set at the optimum angle commensurate with planning height restrictions to maximise the output from the PV arrays.

The Developer shall ensure that any and all associated builder’s work and attendance, electrical work and attendance and lightning protection specialist work and attendance is notified to the main and electrical contractors and is included within their tenders.

The Developer shall provide the complete electrical installation, including all cable containment, enclosures for PV equipment, provision of new switchgear or alteration to existing switchgear as required, installation of G59 protection and generation meter and installation of data cabling as required.

The Developer shall employ a lightning protection specialist to assess the requirement for lightning protection and ensure that for all necessary associated work and attendance is allowed for.

The Developer shall make application to NIE and shall liaise with NIE regarding connection to the NIE grid once all documentation is in place and the system has been certified as safe, operational and in compliance with standard codes of practice and regulations regarding installation and operation of grid connected photovoltaics.

The Developer shall provide all information as required by the local planning authority.

The Developer shall employ a professionally qualified structural engineer to provide a structural design certificate, and shall provide all information as required by the local Building Control department and shall gain building control approval to the complete photovoltaic installation.

4.	SITE EVALUATION

A site survey must be undertaken prior to tender submission to determine inclination, orientation and shading which will provide optimum system performance.

Performance shall be calculated using proprietary software, and the following information shall be submitted with the tender: -

- The electrical rating of the proposed PV array in kilowatts peak (kWp)

- The estimated annual electricity which will be generated in kWh/year

The sun path diagram and the information used to calculate the performance shall also be provided.

Developer is also required to visit each site to satisfy themselves as to its accessibility, local conditions, and the full extent and character of the Works, including the suitability of the site electrical installation, locations for the PV array and accommodation for the invertors. No claim on the grounds of want of knowledge in such respect of such matters shall be entertained.

5.	WARRANTIES AND PERFORMANCE

The installer must offer the following warranties: -

- 5 year performance warranty: 95% of rated kWp

- 12 year performance warranty: 90% of rated kWp

- 20 year performance warranty: 85% of rated kWp

- 25 year performance warranty: 80% of rated kWp

- 5 year manufacturer materials & workmanship warranty

- 5 year manufacturer warranty specifically for the inverter

A 20-year inverter warranty must also be provided.

6.	NIE APPROVAL

Installers are required to gain approval and inform NIE of the installation of a grid connected PV system in the following manner:

- Single installation covered by G83

- Notification using G83 commissioning form within 28 days following commissioning of the installation, to NIE designated contact details

- Multiple installations covered by G83 or installations in close geographical proximity to one another

- Application to connect submitted to NIE - using G83 multiple system application form

- Approval for connection to be received prior to installation.

- Notification within 28 days of commissioning using G83 commissioning form

- Larger installations covered by G59

- Application to connect submitted to NIE using G59 application form

- Approval for connection to be received prior to installation

- Commissioning to be performed to the requirements of NIE

- Notification within 28 days of commissioning using G59 commissioning form

7.	PLANNING PERMISSION

The relevant planning authority must be consulted to determine if planning permissions are required, and if so all information as required by the local planning authority n must be provided.

8.	BUILDING CONTROL APPROVAL

The PV installation must comply with all parts of the building regulations.

The Developer shall make all necessary submissions and provide supporting information, including structural design certificate, as required by Building Control and gain building control approval before commencing the works.

9.	BUILDER’S ATTENDANCE

The Developer shall ensure that any and all necessary builder’s attendances are notified prior to the submission of the tender for inclusion in the main contract tender price, including: -

- ScafFold

- Storage

- Lifting

- Openings

- Flashings

- Sealing

- Fixings and Supports

- Removal and re-installation of roof coverings, tiles or slates

10.	RENEWABLES OBLIGATION SCHEME

The Developer must provide 3 no. original copies of all drawings and MCS certificates, and must provide all necessary documentation and information as necessary and in a format suitable for submission with an application for support under the Renewables Obligation scheme.

11.	LIGHTNING PROTECTION

The Developer shall employ a lightning protection specialist to assess the requirement for lightning protection and ensure that all necessary associated work and attendance is allowed for.

12.	SUPERVISION

The Developer shall maintain full time qualified supervision on site to manage the work.

13.	SAFETY

Care shall be taken at all times to ensure that the PV modules are shielded from light until the commissioning stage.  The recommendations of pr EN50331-1 regarding safety requirements in PV installations shall be adhered at all times.

The design of the system must take account of safety under both normal and fault conditions.

In particular, risk assessments and method statements must take account of the following main safety issues: -

- The supply from PV modules cannot be switched off, so special precautions must be taken to ensure that live parts are either not accessible or cannot be touched during installation, use and maintenance.

- PV modules are current-limiting devices, which require a non-standard approach when designing fault protection systems, as fuses are not likely to operate under short-circuit conditions.

- PV systems include d.c. wiring, with which few electrical installers are familiar.

- The installation of PV systems presents a unique combination of hazards – due to risk of electric shock, falling and simultaneous manual handling difficulty. All of these hazards are encountered as a matter of course on a building site, but rarely all at once. While roofers may be accustomed to minimising risks of falling or injury due to manual handling problems, they may not be used to dealing with the risk of electric shock. Similarly, electricians would be familiar with electric shock hazards but not with handling large objects at heights.

Compliance with the CDM regulations is required.

14.	INVERTOR HOUSING

The Developer shall provide ventilated electrical enclosures as necessary to accommodate the invertors if no other suitable location is available.

15.	SYSTEM DESIGN

15.1	General

The system shall be designed to minimise electrical losses throughout by use of suitable low loss cabling and inverter unit.

15.2	Standard PV Modules

Modules must comply with the following international standards:

- IEC 61215 in the case of crystalline types

- IEC 61646 in the case of thin film types

- IEC 61730 - Photovoltaic (PV) module safety qualification

Modules must also carry a CE mark

Modules must be Class II

Modules must be certificated and listed on the MCS product database

15.3	Building Integrated Products / Modules

PV products shall be designed and constructed to meet the requirements within the relevant Building Regulations for the particular application that the PV product is intended. The PV installer must be able to demonstrate such compliance for all relevant projects in accordance with MCS012 or MCS017 (as relevant)

PV systems mounted above or integrated into a pitched roof shall utilise products that have been tested and approved to MCS012 (test procedures used to demonstrate the performance of solar systems under the action of wind loads, fire, rainfall and wind driven rain).

PV systems utilising bespoke building integrated PV modules must utilise products that have been tested and approved to MCS017 Product Certification Scheme Requirements: Bespoke Building Integrated Photovoltaic Products.

15.4	D.C. Voltage and Current Ratings (Minimum)

All d.c. components (cables, isolators / disconnectors, switches, connectors, etc.) must be rated for the maximum voltage and current of the array and of the individual modules.

Mono- and multi-crystalline silicon modules - all d.c. components must be rated, as a minimum, at:

- Voltage: Voc(stc) x 1.15

- Current: I sc(stc) x 1.25

All other module types - all d.c. components must be rated, as a minimum, from:

- Specific calculations of worst case Voc and I sc, calculated from manufacturer’s data for a temperature range of -15°C to 80°C and irradiance up to 1,250 W/m2

- A calculation of any increase in Voc or I sc over the initial period of operation. This increase is to be applied in addition to that calculated above.

15.5	PV String & Array Voltages

Double insulation (insulation comprising both basic & supplementary insulation) or reinforced insulation, appropriate barriers and separation of parts must be applied to all parts of the d.c. circuit to facilitate a level of protection equivalent to the protective measure “double or reinforced insulation” as defined in BS 7671- Section 412.

PV array open circuit voltage must not exceed 1000V

15.6	D.C. cable sizing

Cables must be sized in accordance with BS 7671 taking into account the multiplication factors in clause 17.3 above

Cables must be sized such that the overall voltage drop, at array maximum operating power (stc), between the array and the inverter is <3%.

15.7	D.C. Cable Type and Installation Method

To minimise the risk of faults, PV d.c. cable runs must be kept as short as practicable.

The cables used for wiring the d.c. section of a grid-connected PV system need to be selected to ensure that they can withstand the extremes of the environmental, voltage and current conditions, under which they may be expected to operate.

Cables must comply with the relevant IEC PV cable standard

Cables routed behind a PV array must be rated for a temperature range of at least of -15°C to 80°C.

Cables must be selected and installed so as to minimise the risk of earth faults and short-circuits. This can be achieved by reinforcing the protection of the wiring either through:

- Single conductor “double insulated” cable

- Single conductor cable suitably mechanically protected by conduit/trunking or a single core SWA cable

- Multi core Steel Wire Armoured SWA where suitable

External cables must be UV stable and water resistant. Where cables are likely to be subjected to external movement, i.e. those mounted immediately behind the array, they must be flexible (multi-stranded) to allow for thermal/wind movement of arrays/modules.

PV array cables must not be buried in walls or otherwise hidden in the building structure making mechanical damage difficult to detect

Where this cannot be avoided conductors must be suitably protected from mechanical damage, by means of metallic trunking or conduit or the use of steel wire armoured cable in accordance with BS 7671.

Exterior cables must be black in colour to assist in UV resistance.

Where long cable runs are necessary (e.g. over 20m), danger labels must be fixed along the length of the cable. Labelling must be provided every 5m on straight runs provided a clear view is possible between labels.

Where multiple PV sub-arrays and or string conductors enter a junction box they must be grouped or identified in pairs so that positive and negative conductors of the same circuit may easily be clearly distinguished from other pairs.

Junction boxes must be IP67 rated with low resistance connectors.

15.8	String Cables

For small systems where it is determined that string fuses are not required for module protection the string cables must be rated such that they may safely carry the maximum possible fault current.

For an array of N parallel connected strings, with each string formed of M series connected modules:

The string cables must be rated as a minimum as follows:

- Voltage > Voc(stc) x M x 1.15

- Current > I sc(stc) x (N-1) x 1.25

The cable Current Carrying Capacity (Iz) must be calculated according to the requirements of BS 7671 including factors taking into account installation conditions such as cable installation method, solar gains and grouping etc.

Where a system includes string fuses, the cable size may be reduced, but in all cases the Iz after de-rating factors have been applied must exceed the string fuse rating and must exceed the

I sc(stc) x 1.25.

15.9	Main d.c. Cable

For a system of N parallel connected strings, with each formed of M series connected modules:

The d.c. main cables must be rated as a minimum as follows:

- Voltage: Voc(stc) x M x 1.15

- Current: I sc(stc) x N x 1.25

The cable Current Carrying Capacity (Iz) must be calculated according to the requirements of BS 7671 including cable de-rating factors to take into account factors such as cable installation method and grouping

15.10	D.C. Plug and Socket Connectors

Plugs and socket connectors mated together in a PV system shall be of the same type from the same manufacturer and shall comply with the requirements of BS EN 50521. Different brands may only be interconnected where a test report has been provided confirming compatibility of the two types to the requirements of BS EN 50521.

Connectors used in a PV string circuit must comply with the minimum voltage and current ratings as detailed in string cable section above (section 24.8). Connectors used in a d.c. main cable circuit must comply with the minimum voltage and current ratings as detailed in the main d.c. cable section above (section 24.9)

Connectors must have a UV, IP and temperature rating suitable for their intended location and must be compatible with the cable to which they are connected.

Connectors readily accessible to ordinary persons shall be of the locking type, requiring a tool or two separate actions to separate and shall have sign attached that reads: ‘Do not disconnect d.c. plugs and sockets under load’

Cable connectors must not be used as the means for d.c. switching or isolation under load (see 24.16).

Plug and socket “Y” connectors may be used to replace a junction box. In this case “Y” connectors must be installed in accessible locations and their location noted on layout drawings

15.11	Other Inline Cable Junctions

In general cable junctions shall either be by an approved plug and socket connector or contained within a d.c. Junction Box (see below) and in-line cable junctions must be avoided.

15.12	PV Array d.c. Junction Box

The d.c. junction box must be labelled ‘PV array d.c. junction box. Danger contains live parts during daylight’.

All labels must be clear, legible, located so as to be easily visible, durably constructed and affixed to last lifetime of the installation.

The short-circuit protection afforded by the cable installation throughout the rest of the d.c. circuit needs to be maintained in the construction and makeup of the d.c. junction box.

Short-circuit protection shall be achieved by:

- Fabrication of the enclosure from non-conductive material

- Positive and negative busbars and terminals adequately separated and segregated within the enclosure and/or by a suitably sized insulating plate, or separate positive and negative junction boxes.

- Cable and terminal layout such that short-circuits during installation and subsequent maintenance are extremely unlikely

15.13	String Fuses

Selection of overcurrent protective measures must take account of the system design and the number of strings. In addition, the ability of a module to withstand reverse current must also be considered in compliance with IEC61730-2 Photovoltaic (PV) module safety qualification – Part 2: Requirements for Testing

String fuses are required where the maximum module reverse current is greater than the module maximum series fuse rating.

In order to provide full protection of all cables and modules string fuses are required in both the positive and negative legs of the string cabling.

For small systems where it is determined that fault currents do not present a risk to the modules, only the string cables & connectors need to be considered, and in this case oversizing string cables & connectors such that they may safely carry the maximum possible fault current without fire risk from overloaded cables is acceptable.

Where the inverter is of such a design that it has multiple MPPT inputs and the design does not allow fault currents to flow between these inputs, each MPPT input may be treated as a wholly separate sub-array for the purposes of deciding whether string fuses are required.

Fuses must not be mounted in such a position where their rating may be compromised by the build-up of heat from solar gains. The use of MCBs (miniature circuit breakers) is permissible provided they meet the string fuse criteria and are rated for use in an inductive circuit and will operate for currents flowing in either direction through the device. A system fitted with suitable removable string fuses provides a means to achieve the requirements for string isolation (section 24.17)

15.14	String Fuse Selection

The following requirements apply where the PV array provides the only source of fault current, such as in a typical grid connected system with no battery.

For a system of N parallel connected strings, with each formed of M series connected modules:

- String fuses must be provided for all arrays where: (N – 1) × Isc > module maximum series fuse rating

- Where fitted, fuses must be installed in both positive and negative string cables for all strings.

- The string fuse must be of a type gPV -according to IEC60269-6

- The string fuse must be rated for operation at Voc(stc) x M x 1.15

- The string fuse must be selected with an operating current In such that:

I n> 1.5 x Isc stc

In = 2.4 x Isc stc

In = Maximum series fuse value

15.15	Blocking Diodes

If incorporated, blocking diodes must have:

- A reverse voltage rating > 2 x maximum system voltage (as calculated in section 24.4)

- A current rating > 1.4 x Isc (where Isc is the relevant short circuit current for the string / subarray / array)

- Have adequate cooling (heatsinks) if required

15.16	D.C. Isolation and Switching

The following table describes the requirements for both isolation and switching in the D.C. side of the PV array circuit:

| D.C. Circuit | Switching | Isolation |
| --- | --- | --- |
| String | Not required | Readily accessible means of string isolation |
| Sub array | Optional | Readily accessible means of Sub Array isolation |
| Array | Readily accessible load break switch disconnector on d.c. side of inverter |  |

An additional d.c. isolating device must be installed at the point of cable entry into the building) for systems with long d.c. cable runs to provide a means of isolating the cable for safety reasons or maintenance works.

15.17	Isolation

Isolation shall be provided in both positive and negative cables and all isolation measures shall be readily accessible

String isolation may achieved by any suitable means such as appropriately located plug and socket connectors or removable string fuses.

Sub array isolation may be achieved by any suitable means such as a removable sub array fuse or by the use of a switch disconnector.

Array isolation shall be provided by the Array Switch Disconnector

15.18	Switch Disconnector – General Requirements

A switch disconnector must be installed on the d.c. side and shall have the following features: -

- The switch must isolate all live conductors (typically double pole to isolate PV array positive and negative conductors)

- The switch must be rated for d.c. operation at the system voltage maximum as calculated

- The switch must be rated for d.c. operation at the system current maximum as calculated

- The switch must be labelled as ‘PV array d.c. isolator’, with the ON and OFF positions clearly marked. Switch enclosures must also be labelled with ‘Danger - contains live parts during daylight’. All labels must be clear, easily visible, constructed and affixed to last and remain legible for as long as the enclosure.

15.19	Array Switch Disconnector

As noted in section 24.16, a readily accessible load break switch disconnector on d.c. side of inverter must be provided. This array switch disconnector shall be one of the following:

- A physically separate switch-disconnector mounted adjacent to the inverter; or

- A switch-disconnector that is mechanically connected to the inverter – that allows the inverter to be removed from the section containing the switch-disconnector without risk of electrical hazards; or

- A switch-disconnector integral to the inverter, if the inverter includes a means of isolation only operable when the switch-disconnector is in the open position (e.g. plugs only accessible once the switch disconnector handle is removed);

- A switch-disconnector integral to the inverter, if the inverter includes a means of isolation (e.g. plugs) which can only be operated with a tool and is labelled with a readily visible warning sign or text indicating ("Do not disconnect under load").

15.20	A.C. Module Systems switch disconnector

Where inverters are of the type that mounts directly onto or adjacent to PV modules, BS 7671 regulation 712.537.2.2.5 still requires the fitting of a switch disconnector.

15.21	Lightning Protection

If the building is fitted with a lightning protection system (LPS), the array frame must be connected to the LPS by a suitable sized conductor

Where an LPS is fitted, PV system components must be mounted away from lightning rods and associated conductors (see BS EN 62305). For example, an inverter must not be mounted on an inside wall that has a lightning protection system down conductor running just the other side of the brickwork on the outside of the building.

15.22	Earthing

The d.c. side of the installation must be constructed to meet the requirements of an installation using double or reinforced insulation, and therefore no connection to earth between the PV Modules or frame and main earthing terminal is required.

However, when the equipment or component is considered to be a class I appliance or accessory and is reliant on a connection with earth for safety using ‘automatic disconnection of supply’ (ADS) as the fault protective measure the metallic casings of fixtures and fittings shall be connected to the main earthing terminal via a circuit protective conductor (cpc).

Earthing of the inverter at the a.c. terminations is necessary where the inverter is a Class I piece of equipment and must be applied where necessary. Where class I inverters are used careful consideration must be given to the requirements for earthing.

15.23	Protective Equipotential Bonding

The d.c. side of the PV installation shall have double or reinforced insulation as the protective measure and therefore the component parts of the installation will be isolated and will not require protective equipotential bonding.

15.24	Determining an Extraneous-Conductive-Part

The frame of the array must be assessed as to whether it is likely to introduce a potential into the installation, by testing for insulation resistance between the frame and the main earth terminal. If the part is considered to be extraneous, protective equipotential bonding, as required by BS 7671, must be applied

15.25	System Earthing (d.c. Conductor Earthing)

It is preferable that there be no connection to earth of any of the current carrying d.c. conductors.

However, the manufacturer’s instructions for both the PV modules and the equipment to which the PV array is connected must be taken into account in determining the most appropriate earthing arrangement, whether: -

- No earth connection

- Hardwired connection of positive or negative conductor to earth

- Centre tapped array – with / without earth connection

- High impedance connection of positive or negative conductor to earth (for functional reasons)

Earthing of one of the live conductors of the d.c. side is permitted, if there is at least simple separation between the a.c. and the d.c. side. Where a functional earth is required, it is preferable that where possible this be done through high impedance (rather than directly).

If an earthed d.c. conductor is required, the manufacturer must confirm whether the inverter is suitable for earthing of a d.c. conductor, and this must be done in the inverter in accordance with guidance from the inverter manufacturer, and in accordance with IEC62109-2 (Safety of Power convertors for use in photovoltaic power systems – Part 2: Particular requirements for inverters).

15.26	Systems with High Impedance Connection to Earth

A high impedance connection to earth of one of the current carrying conductors may be permitted where the earth connection is required for functional reasons.

Where a functional earth is required, it is preferred practice that systems be functionally earthed through high impedance rather than a direct low impedance connection (where possible).

15.27	Systems with Direct Connection to Earth

Where there is a hardwired connection to earth, an earth fault interrupter and alarm system must be provided.

The nominal overcurrent rating of the interrupter shall be as follows: -

Array size Overcurrent rating: -

<3kWp =1A

3 – 100KWp =3A

>100kWp =5A

The earth fault alarm shall be of a form that ensures that the system operator becomes immediately aware of the fault, whether by visible or audible signal or another form of fault communication such as email, SMS or similar

Where the inverter is located in a remote location, the system must be configured so that a secondary alarm is triggered that will be immediately seen by the system operator. For systems in accordance with BS 7671 conductors used for earth fault detection must be cream in colour.

15.28	Surge Protection Measures

To protect the a.c. system, surge suppression devices must be fitted at the main incoming point of a.c. supply (at the consumer’s cutout). To protect the d.c. system, surge suppression devices must be fitted at the inverter end of the d.c. cabling and at the array. To protect specific equipment, surge suppression devices must be fitted as close as is practical to the device.

All d.c. cables must be installed to provide as short runs as possible and positive and negative cables of the same string or main d.c. supply must be installed together, avoiding the creation of loops in the system. This requirement includes any associated earth/bonding conductors.

Long cables (e.g. PV main d.c. cables over about 50 m) must be installed in earthed metal conduit or trunking, or be screened cables such as armoured.

15.29	A.C. Cabling

The PV system inverter(s) must be installed on a dedicated final circuit to the requirements of BS 7671 in which:

- No other current-using equipment is connected, and

- No provision is made for the connection of other current-using equipment, and

- No socket-outlets are permitted.

Where a single circuit feeds more than one inverter, the protective device for that circuit shall be less than the maximum MCB rating recommended by the inverter manufacturer(s). An inverter must not be connected by means of a plug with contacts which may be live when exposed and a.c. cables are to be selected and installed in accordance with BS 7671.

The a.c. cable connecting the inverter(s) to the consumer unit must be sized to achieve voltage drop of 1% or less.

15.30	RCD Protection

Where an electrical installation includes a PV power supply system that cannot prevent d.c. fault currents from entering the a.c. side of the installation, and where an RCD is needed to satisfy the general requirements of the electrical installation in accordance with BS 7671, then the selected RCD must be a Type B RCCB as defined in IEC 62423. Where any doubt exists about the capability of the inverter to prevent d.c. fault currents entering the a.c. side of the system then the manufacturer shall be consulted.

15.31	A.C. Isolation and Switching

To comply with the requirements of Engineering Recommendations G83 / G59: -

The PV system shall be connected to an isolation switch that fulfils the following conditions:

- Isolates line and neutral conductors

- Be securable in the OFF position

- Located in an accessible location

This switch shall clearly show the ON and OFF positions and be labelled as ‘PV system – main A.C. Isolator’

Isolation and Switching of the a.c. side of the installation shall also comply with the requirements of BS 7671. This must include the provision of an isolator adjacent to the inverter to disconnect the inverter from the source of supply (AC).

Note: At the point of installation of any a.c. switch-disconnector, the public supply must be considered the source and the PV installation the load.

15.32	Inverters

Inverters must carry a Type Test certificate to the requirements of Engineering Recommendation G83 or G59 (as applicable – see section 6).

The PV system must disconnect when the distribution system is not energised.

Inverter unit(s) shall be matched to the capacity of the arrays and shall be located in a suitable location (subject to wiring distance).  Inverters shall be complete with VDE 0126-1-1 disconnection function to ensure G59 compliance.

Noise generated by the DC Inverter unit shall not cause noise nuisance within the building.  Residual levels shall be no greater than NR 30 within all occupied spaces.

15.33	Inverter Sizing

Where a system features multiple strings/arrays with significantly different orientation or inclination, and where the variations in orientation or inclination are such that connecting the strings/arrays to a single MPPT input may significantly reduce the overall performance of the system. The strings or arrays must be connected to an inverter with a multiple MPPT function or separate inverters must be utilised.

The inverter must be selected to safely withstand the maximum array voltage and current (as highlighted in section 24.4). This must include any initial overvoltage period which is a feature of some module types. This must also include verifying that the inverter can safely withstand the array open circuit voltage maximum at -15°C.

Temperature range – An assessment must be made as to the temperature range acceptable and appropriate for the particular site and array mounting method

Power ratio – Inverters must be sized for 100% of array capacity.

Inverter ventilation – Inverter locations must be provided with sufficient ventilation, and manufacturer’s recommended clearance distances must also be observed. Inverter locations prone to high temperatures such as Plant rooms, Boiler rooms or roof spaces must be avoided.

A label “do not block ventilation” must be placed next to the inverter.

Inverters must also carry a sign ‘Inverter - isolate a.c. and d.c. before carrying out work’.

15.34	A.C. Cable Protection

Protection for the cable from the inverter(s) must be provided at the distribution board. This protective measure shall be selected and installed in accordance with the requirements of BS 7671.

15.35	Metering

Inverter output meter: Metering at the inverter output must be installed to display/record both energy delivered by the PV system (kWh), and instantaneous power output (kW).

An approved kWh meter as detailed in the “Metering Guidance” document issued by MCS, connected to measure generation, is required to facilitate payments of any financial incentives.

The meter must be located where the consumer can readily observe it.

The meter must be capable of remote reading via PC and/or via internet

Building Export meter: In order to enable payment on exported electricity, an approved kWh export meter with appropriate reading capabilities is required.

The appropriate Energy Supplier must be contacted to find out any particular requirements and to arrange for its fitting.

15.36	Weather station, Plant monitoring and Display unit

A weather station (including irradiation intensity, module temperature, ambient temperature and wind speed) with data analyser shall be supplied and installed

The facility shall be supplied and installed to allow monitoring and data access via local PC and remotely via internet

A display unit showing current PV output and total output shall be supplied and installed within the entrance lobby.  This display unit shall indicate the amount of electricity being generated by the PV devices in relation to building demand.

The device shall be easy to read and be provided with a large clear digital display and recessing bezel

16.	INSTALLATION

16.1	Ease of maintenance

All accessories and equipment shall be located so as to be easily accessible for future service and maintenance.

16.2	PV Specific Hazards

A method statement and risk assessment shall be provided for the installation of a PV system, and shall address the following: -

- Electricity at Work Regulations 1989.

- Detection of short circuit

- Protection from electric shock hazard (operator, owner, cleaner, service engineers, etc).

- Means of avoiding live working

- The combination of hazards due to risk of shock, falling, and simultaneous manual handling large objects at heights

16.3	Installation of d.c. circuits

16.3.1	Personnel

All persons working on the live d.c. cabling of a Photovoltaic (PV) system must be experienced / trained in working with such systems and fully acquainted with the voltages present on that system in particular.

16.3.2	Sequence of Works

All d.c. wiring must be completed prior to installing the PV array to allow effective electrical isolation of the d.c. system (via the d.c. switch-disconnector and PV module cable connectors) while the array is installed, and effective electrical isolation of the PV array while the inverter is installed.

It must never be necessary for an installer to work in any enclosure or situation featuring simultaneously accessible live PV string positive and negative parts.

Where it is not possible to pre-install a d.c. isolator cable ends/ connectors must be put temporarily into an isolation box and suitably labelled.

Cables are to be well supported, especially those cables exposed to the wind. Cables must be routed in prescribed zones or within mechanical protection, fully supported / cable tied (using UV stabilised ties) and they must also be protected from sharp edges.

16.3.3	Live Working

If it is unavoidable to work in any enclosure containing both positive and negative connections that are simultaneously live, work must be performed either by utilising insulating gloves & tools, insulating materials for shrouding purposes and appropriate personal protective equipment.

A temporary warning sign and barrier must be posted for any period while live PV array cables or other d.c. cables are being installed.

16.3.4	Array Mounting

The installer is responsible for designing the PV array mounting structure. The manufacturer’s instructions must be observed.

The system is to be an ‘above-roof’ system (‘roof-integrated’ or ‘in-roof systems must not be proposed).

The system shall be suitable for installing on a standing seam metal roof.

16.3.5	Load Calculations

The design and specification of the PV array mounting system must take into account the wind and snow loads to be expected.

Site specific calculations are required to ensure that the system proposed is sufficient to withstand the imposed loads.

For each site the imposed wind and snow loads must be derived using the procedures within Eurocode- 1 (BS EN 1991-1).

The pressure coefficients (Cp) used to calculate wind loads shall be derived as follows:

- For PV arrays that are mounted above, and parallel to, an inclined roof where there is a clear gap between the array and the roof - the pressure coefficients shall be taken from BRE digest 489 or from recognised test data commissioned for the specific purpose of determining the wind loads on solar systems.

- For flat roof systems - the pressure coefficients shall be taken from BRE digest 489 or from recognised test data commissioned for the specific purpose of determining the wind loads on solar systems.

- For roof integrated, nominally airtight systems - the pressure coefficients shall be taken from Eurocode-1.

- For roof integrated, air permeable “PV tile” type systems - the pressure coefficients shall be taken from BS5534 and treating the PV array as roof tiles. Edge Zone pressure coefficients shall be taken from BRE digest 489 and applied in calculations where some, or all, of the array lies in the “Edge Zone” as defined in BS EN 1991-1.

As described within Eurocode-1 tables A1.1 and A1.2, safety factors must be applied to the calculated loads. Taken in isolation, a safety factor of 1.5 must be applied to the derived wind and snow loads and a factor of 1.0 to the dead load (self-weight).

However, in normal use solar panels may be designated with a lower consequence of failure than for the supporting building structure, in accordance with Table B1 of EN 1990: 2002 + A1:2005 Consequence Class CC1. As a result the partial factor for design wind and snow loads may be multiplied by 0.9 (Factor KFI for Reliability Class RC1 from Table B3 of EN 1990: 2002 +A1 : 2005). Hence a safety factor of 1.35 must be applied to the derived wind and snow loads. Load calculations shall be undertaken by a suitably competent person.

16.3.6	Fixing Calculations

The PV array fixings (type and quantity) shall be checked to ensure that they can withstand the imposed (dead) load and wind uplift loads as calculated by ensuring that the imposed loads are within the range specified by the product manufacturer (and then installing according to the manufacturer’s instructions)

In all cases it is expected an appropriate safety factor to have been applied to the fixing withstand capacity

Fixing calculations shall be carried out by a suitably competent person.

16.3.7	Building Structure Calculations

The roof structure shall be checked to ensure it can withstand the imposed loads as calculated. This is to include a site inspection by a suitably competent person.

The specialist sub contractor shall ensure all necessary supporting structures and access facilities are in place before installation is commenced.

16.3.8	PV Roofing and Cladding Works

The PV systems must not adversely affect the weather tightness of the structure to which they are fitted. The system must be designed and installed to ensure this is maintained for the life of the system.

For integrated systems, the weather tightness of the PV system must be the same or better than the roof or cladding systems they are replacing and must not adversely affect the weather tightness of the surrounding covering.

For above roof PV systems, the array fixing brackets must not affect the weather tightness of the roof they are fitted to. For example, systems attached to tile roofs must be designed and installed such that the fixing brackets do not displace the tiles and cause gaps more than naturally occurs between the tiles. Fixing methods must not subject roof coverings to imposed loads which may degrade their primary purpose of maintaining weather-tightness.

Tiles or slates removed for fixing a mounting bracket must be re-attached to include a means of mechanical fixing.

Mounting systems relying on “through bolt” approach shall not be used.

The roof underlay must be inspected for damage during installation works. Any damage must be repaired or the underlay replaced as necessary.

Unless specifically designed to do so, systems must be kept away from the roof perimeter. For a domestic roof, a suitable minimum clearance zone is around 40-50cm.

Cable penetrations through the roof must not affect the weather tightness of the roof and must be durably sealed using a purpose-made product to accommodate the movement and temperatures expected,

Cable penetrations through underlay must be achieved using a purpose-made product

Thermal expansion shall be accommodated in the design of the module and mounting system

16.3.9	Pitched Roof System Requirements

PV systems mounted above or integrated into a pitched roof must utilise products that have been tested and approved to MCS012

In roof products (eg PV tiles) – All fixing and flashing components used to mount and make weather-tight the solar roofing product must be packaged and listed as part of a complete kit that includes the PV module. The MCS installer must ensure that the system is installed to comply with the manufacturer’s instructions.

In all cases it is expected that the manufacturers’ fixing instructions are followed with respect to wind loading and the installer must ensure that the design wind load is within the range as specified by the manufacturer; and/or for high wind sites, any required additional fixings are correctly installed. Where an installer has chosen to utilise a mounting assembly comprised of “universal” components, the installer must ensure that all components are suitable for the wind load imposed on that component.

16.3.10	Standing Seam and Other Metal Roofs

Where the PV array mounting system relies on securing the array to the metal roof cladding, the adequacy of the roof covering to transfer all additional loads back to the supporting structure must be verified. This must include consideration of all elements of the roof construction that could be affected by the additional loading. Calculations must include consideration of the array configuration (pitched or parallel to the roof) and the type, quantity and locations of PV array fixings.

Sitework must include verification to confirm that all the design requirements have been satisfied and that the roof covering has not been adversely affected by the installation work

17.	SIGNS AND LABELS

17.1	Safety information

Safety notices shall be provided where necessary and shall be to the same standards as equipment labels.  PV cabling shall be labelled using PVC labels affixed using cable ties at 500mm intervals throughout their length.

All components of the PV system must be labelled using engraved traffolyte labelled affixed with 2 corrosion resistant screws. All labels must be clear, easily visible, constructed and affixed to last and remain legible for the lifetime of the system.

Dual supply labelling must be provided at the service termination, meter position and all points of isolation between the PV system and supplier terminals to indicate the presence of on-site generation and indicating the position of the main a.c. switch disconnector.

17.2	Circuit diagram & system information

At the point of interconnection, a circuit diagram shall be installed, including the relationship between the inverter equipment and supply, a summary of the protection settings incorporated within the equipment, a contact telephone number for the supplier/installer/maintainer of the equipment, shutdown and start up procedures

17.3	Fire and Rescue Notification

To ensure the Fire and Rescue Service are aware that a PV system is installed on the roof, the following sign shall also be fitted: -

Location: next to the suppliers’ cut-out in the building

Size: This label shall measure at least 100mm x 100mm

Only required for PV systems fitted on roofs Solar PV on roof

18.	INSPECTION, TESTING AND COMMISSIONING

18.1	Inspection and Testing – a.c. Side

Inspection and testing of the completed system to the requirements of BS 7671 must be carried out and documented, and an NICEIC certificate and schedule of test results must be provided

18.2	Inspection and Testing – d.c. Side (PV Array)

The inspection and testing of the d.c. side of the PV system shall be in accordance with the requirements of BS 7671 and also BS EN 62446 Grid connected photovoltaic systems — Minimum requirements for system documentation, commissioning tests and inspection

The verification sequence contained within BS EN 62446 includes

• Inspection schedule

• Continuity test of protective earthing and/or equipotential bonding conductors (if fitted)

• Polarity test

• String open circuit voltage test

• String short circuit current test

• Functional tests

• Insulation resistance of the d.c. circuits

These tests shall be recorded on a PV array test report which shall be appended to the a.c. documents listed above.

18.3	Engineering Recommendation (ER) G83 and G59 Requirements

Depending on the size of the PV installation, the requirements of either Engineering Recommendation G83 or G59 are to be followed when commissioning a grid connected PV system.

Systems up to 6.5kW output per phase come under ER G83. These systems will not require any extra commissioning procedures (measures other than those described elsewhere in this document).

Systems over 21kW come under ER G59. These systems may require additional commissioning tests to verify the correct and safe operation of the grid interface protection circuits. Smaller systems using G59 type approved inverters may not require any additional tests.

Where separate protection relays are fitted (a “G59 relay”), on site testing of the relay and protection system is required. NIE needs to be consulted over the test procedure required and whether the tests need to be witnessed by an NIE representative.

Standard forms are provided by NIE to document the commissioning of a PV system.

19.	HANDOVER & DOCUMENTATION

The system user must be provided as a minimum with the information as described in of BS EN 62446 Grid connected photovoltaic systems — Minimum requirements for system documentation, commissioning tests and inspection. The following provides a summary of the information required:

- Basic system information (parts used, rated power, installation dates etc)

- System designer information

- System installer information

- Wiring diagram, to include information on:

- Module type & quantities

- String configurations

- Cable specifications – size and type

- Over-current protective device specifications (where fitted) - type and ratings.

- Array junction box locations (where applicable).

- d.c. isolator type, location and rating

- Array over-current protective devices (where applicable) – type, location and rating

- Details of all earth / bonding conductors – size and connection points

- Details of any connections to an existing Lightning Protection System (LPS).

- Details of any surge protection device installed (both on a.c. and d.c. lines) to include location, type and rating.

- AC isolator location, type and rating.

- AC overcurrent protective device location, type and rating

- Residual current device location, type and rating (where fitted).

- Module datasheets

- Inverter datasheets

- Mounting system datasheet

- Operation and maintenance information, to include:

  - Procedures for verifying correct system operation.

  - A checklist of what to do in case of a system failure.

  - Emergency shutdown / isolation procedures.

  - Maintenance and cleaning recommendations (if any).

  - Considerations for any future building works related to the PV array (e.g. roof works).

- Warranty documentation for PV modules and inverters - to include starting date of warranty and period of warranty.

- Documentation on any applicable workmanship or weather-tightness warranties.

- Test results and commissioning data

20.	Training

One two hour training session on the system shall be allowed for within the tender.

21.	Maintenance

The supplier/installer shall maintain the installation and pay all costs during the defects liability period.

Additionally, regular servicing and maintaining of the installation shall be carried out at 3 month intervals during the maintenance period. During this period the Equipment supplier shall submit to the Engineer a full report in duplicate including details of tests carried out and any faults found with the corrective action taken.

  - AOV SMOKE VENT INSTALLATION

    - General

The sub-contractor shall provide a complete smoke vent installation including all necessary equipment and controls to operate each window designated as an AOV (automatic opening vent)

    - Equipment

All necessary equipment to open and close each AOV window shall be included for as a part of the main contract but wired and connected as a part of this electrical contract.  For each AOV the sub-contractor shall wire and connect a control panel, actuator, breakglass, fire alarm interface and all necessary cabling. The actuator shall be surface mounted chain driven and capable of powering the weight of the window open and closed to allow a minimum open area of one square meter.

    - Operation

Upon activation of the fire alarm system a signal will be sent to each AOV control panel which shall drive the AOV window open to allow a minimum open area of one square meter.  Once the fire alarm is reset this AOV window shall automatically reset and close.

The AOV window shall be manually operable from both the breakglass and control panel.  Controls on the breakglass shall be enclosed behind a lockable door.  The breakglass shall indicate the status of the window it controls i.e. open / closed / fault.

    - Co-ordination

The Developer shall ensure the AOV system provided is suitable for use on the window in question and to co-ordinate position and installation of AOV controls and actuators to ensure a discrete installation is achieved

    - Wiring

All power and control wiring associated with the AOV smoke vent installation shall be undertaken as part of this sub-contract.

The Developer shall supply and install all necessary PVC conduit and wiring to the all components.

    - Alarm signals shall be provided from the fire alarm systems

##### SECTION 3

##### SCHEDULES

SCHEDULE A

SCHEDULE OF LUMINARIES

### SCHEDULE A

SCHEDULE OF LUMINAIRES

All luminaires to be supplied complete with lamps.  All lamps of the same type shall be the same colour temperature

| Ref | Description | Contractor’s Proposals |
| --- | --- | --- |
| A | Energy efficient pendent set for use with 18w 4pin compact fluorescent lamps with a 200mm long flex. Pendant to be complete with integral control gear | Manufacturer: Model no: |
| B | Circular 28w 2D type luminaire suitable for both ceiling and wall mounting providing both direct and indirect light through front and rear diffusers. To be constructed of vandal resistant polycarbonate body and fascia both finished in white. Main diffuser to be prismatic vandal resistant polycarbonate. Backlight diffuser to be clear vandal resistant polycarbonate. Luminaire to be fitted with high frequency gear and achieve a total light output of not less than 55 lamp lumens per circuit watt. Luminaire to be sealed to a minimum of IP44 | Manufacturer: Model no: Lumens per circuit watt: |
| C | Square 28w 2D type luminaire with grill suitable for external wall mounting. To be constructed of vandal resistant polycarbonate body and fascia (including grill) both finished in matt black. Main diffuser to be clear fresnel vandal resistant polycarbonate. Luminaire to be fitted with high frequency gear and achieve a total light output of not less than 55 lamp lumens per circuit watt. Luminaire to be sealed to a minimum of IP65 | Manufacturer: Model no: Lumens per circuit watt: |
| D | Square 28w 2D type luminaire suitable for external mounting. To be constructed of vandal resistant polycarbonate body and fascia both finished in matt black. Main diffuser to be clear fresnel vandal resistant polycarbonate. Luminaire to be fitted with high frequency gear and achieve a total light output of not less than 55 lamp lumens per circuit watt. Luminaire to be sealed to a minimum of IP65 | Manufacturer: Model no: Lumens per circuit watt: |
| E | Square 16w 2D type luminaire with prismatic diffuser suitable for both wall and ceiling mounting. To be constructed of vandal resistant polycarbonate body finished matt white. Main diffuser to be clear prismatic vandal resistant polycarbonate. Luminaire to be fitted with high frequency gear and achieve a total light output of not less than 55 lamp lumens per circuit watt. Luminaire to be sealed to a minimum of IP44 | Manufacturer: Model no: Lumens per circuit watt: |
| F | 2x35w T5 fluorescent luminaire with prismatic diffuser. To be constructed of vandal resistant polycarbonate. Diffuser to be prismatic vandal resistant polycarbonate. Luminaire to be fitted with high frequency gear and achieve an output of not less than 55 lamp lumens per circuit watt | Manufacturer: Model no: Lumens per circuit watt: |
| G | 20w 1700lm 4000k LED surface mounted circular luminaire finished white. Luminaire body to be cast aluminium and diffuser to be white opal polycarbonate. Luminaire light output ratio shall be rated at 100%. Luminaire shall achieve an output of not less than 85 luminaire lumens per circuit watt. LEDs shall be rated with a life expectancy of L80 50,000 hours and have a colour rendition of at least 80. Luminaire to be not more than 100mm deep and not more than 400mm in diameter. Each luminaire to be complete with an integral microwave based presence detector mounted behind the diffuser. Detector shall after a pre-set time of no movement dim lights to 20% and hold at this level until movement is detected or a further time period passes were lights will turn off. All parameters shall be fully programmable and 1no programmers shall be supplied as a part of the lighting installation. Luminaires denoted EMG to be complete with 3hr integral emergency batteries. | Manufacturer: Model no: Lumens per circuit watt: |
| H | 17w 1250lm 4000k LED surface mounted circular luminaire finished black. Luminaire body to be polycarbonate and diffuser to be opal polycarbonate. Luminaire light output ratio shall be rated at 100%. Luminaire shall achieve an output of not less than 70 luminaire lumens per circuit watt. LEDs shall be rated with a life expectancy of L70 50,000 hours and have a colour rendition of at least 80. Luminaire to be not more than 100mm deep and not more than 300mm in diameter. Luminaires denoted EMG to be complete with 3hr integral emergency batteries. Luminaire to sealed to a minimum of IP54 | Manufacturer: Model no: Lumens per circuit watt: |
| I | Not used |  |
| J | 12w maintained LED surface mounted exit box with acrylic blade type legend. Luminaire to be fitted with 3hr batteries for emergency operation. Luminaire to be fitted with down legend suitable for a 28m viewing distance | Manufacturer: Model no: |
| K | 6w non-maintained LED surface mounted emergency bulkhead. Luminaire to be fitted with 3hr batteries for emergency operation. Diffuser to be clear polycarbonate | Manufacturer: Model no: |
| L | 11w 1100lm 4000k LED wall mounted luminaire. Body to be in steel finished powder coated black and fitted with a clear prismatic polycarbonate diffuser. Luminaire shall be square with front face angled at 45°. Luminaire to have an impact rating of not less than IK15 and be sealed to IP65 | Manufacturer: Model no: Lumens per circuit watt: |
| M | Not used |  |
| N | 55w 6000lm 4000k LED post top luminaire. Body to be die cast aluminium finished powder coated and fitted with a clear polycarbonate diffuser. Luminaire to have an impact rating of not less than IK16 and be sealed to IP65. Post top luminaire to be installed on 76mm 4000mm tall root mounted tapered column. Column to be powder coated to match finish of luminaire | Manufacturer: Model no: Lumens per circuit watt: |
| SL1 | As per DOE stamped approved drawing WRTL Vectra 2650SNN/2D 50w SON-T+ fitted with electronic control gear with rear entry mounting mounted on Fabrikat 6m columns with 500mm outreach brackets and a K factor not more than 2 to BS5649. |  |

SCHEDULE B

## Schedule of equipment

ALPHA HOUSING ASSOCIATION

SCHEDULE B

## Schedule of Equipment

| Item | Description | Contractor’s proposals |
| --- | --- | --- |
| Cables | LS0H BASEC-certified | Manufacturer: |
| Consumer Units | BS compliant | Manufacturer: Range: |
| Wiring, telephone and ceiling accessories | BS compliant, with 15-year guarantee All accessories to be from one single manufacturer’s range, available through an extensive local distributor network. | Manufacturer: Range: |
| Mains Powered Detectors | Optical Smoke alarms shall be BSI Kitemarked to BS EN 14604:2005 Heat alarms shall be BSI Kitemarked to BS 5446-2:2003 Carbon Monoxide alarms shall be BSI Kitemarked to BS EN 50291:2001 All items to have sealed-in lithium rechargeable back-up batteries | Manufacturer: Model no: |
| Fire Alarm | BS 5839, L3 Specialist installer to be certified to NACOSS Fire Gold and BAFE SP203. | Specialist installer: Manufacturer: Model no: |
| Door entry | Specialist installer to be certified to ISO 9002 | Specialist installer: Manufacturer: Model no: |
| CCTV | Not used |  |
| Warden call | Tunstall (no other manufacturer acceptable in this instance) |  |
| Television Distribution | CAI-approved installer AND Sky communal systems approved installer | Specialist installer: Manufacturer: Model no: |
| Photovoltaics | BS compliant, MCS approved with 25 year guarantee Supplied and installed by an accredited member of the Microgeneration Certification Scheme who is certified to ISO 9001 and ISO 14001 | Specialist installer: Manufacturer: PV efficiency: |
| Lift | EN 81 | Specialist installer: |
| Lighting / Emergency Lighting | BSEN60598 / BS5266 | Refer to schedule A |
| AOV Smoke Vents |  |  |
| Hob | 4 zone, 600mm width, black glass finish with knob controls and residual heat indicator. | Manufacturer: Model no: |
| Oven | Energy A rated single fan oven, 600mm width, finished white with knob controls and side opening door. | Manufacturer: Model no: |
| Washing Machine | Energy A++ rated, 9kg capacity, 1400rpm spin, finished white with LCD interface. | Manufacturer: Model no: |
| Tumble Dryer | Energy A++ rated, 9kg capacity, 1400rpm spin, finished white with LCD interface. | Manufacturer: Model no: |
| Dish Washer | Energy A++ rated finished white with LCD interface. | Manufacturer: Model no: |
| Fridge Freezer | Energy A+ rated, 1750mm height, 600mm width, fridge volume 185lt, freezer volume 135lt, finished white with frost free operation and antibacterial protection. | Manufacturer: Model no: |